## All
Service Logs - Sep'2018 to Dec'2018
Ticket No | Date | Name of the Outlet | Code | Nature of Complaint | Breakdown / Preventive | Service Engineer | Rectified On | Interruption of Sales if any - Time Duration | Details of Work Done
CL1 | 2018-09-22 | Theni | A | Online UPS Installation Work | Preventive | Chandrasekar | 2018-09-22 | - | Supplied by vendor. Wiring work done by local electricians and Installation Completed by us
CL2 | 2018-09-23 | Vellakovil | D | Dispenser One Side Problem | Breakdown | Prabu | 2018-09-23 | - | Solenoid Valve Cleaned - Rectified
CL3 | 2018-09-23 | Ariyamangalam | D | Dispenser 1 B-Side Hose LPG Leakage | Breakdown | Nepolean | 2018-09-23 | - | New Hose Changed - Working Condition Normal
CL4 | 2018-09-23 | Velachery | R | Control Panel PLC Configuration & Testing | Preventive | Suneel | 2018-09-23 | - | Configured and Tested
CL5 | 2018-09-24 | Ariyamangalam | D | Dispenser Calibration | Preventive | Nepolean & Prakash | 2018-09-25 | - | Both the dispensers have calibrated and stamped by DIL
CL6 | 2018-09-24 | T.V.Kovil | A | Dispenser to office automation cable laying work | Preventive | Prabu | 2018-09-24 | - | Cable laying Completed
CL7 | 2018-09-24 | Cantonment | T | Decanting hose venting line leakage | Breakdown | Prabu | 2018-09-24 | - | One old Ball valve replaced - Leakage Arrested
CL8 | 2018-09-25 | Cantonment | T | Decanting liquid inlet ball valve leakage | Breakdown | Chandrasekar | 2018-09-25 | - | Replaced with old Ball Valve - Rectified
CL9 | 2018-09-26 | Karur | C | Rule 18 work | Certification | Nepolean | 2018-10-02 | - | Completed
CL10 | 2018-09-26 | Cantonment | D | Dispenser vapour line ROV ball valve leakage | Breakdown | Chandrasekar | 2018-09-26 | - | Leakage Arrested
CL11 | 2018-09-26 | Vellakovil | D | Dispenser one side low flow & Slow Delivery | Breakdown | Nepolean | 2018-09-26 | - | Solenoid Valve Cleaned - Rectified
CL12 | 2018-09-26 | Renganathan, Trichy | D | Nozzle lock complaint | Breakdown | Chandrasekar | 2018-09-26 | - | Rectified
CL13 | 2018-09-26 | Kangayam | C | Rule 18 work | Certification | Nepolean | 2018-09-26 | - | Completed
CL14 | 2018-09-27 | Dharapuram | C | Rule 18 work | Certification | Nepolean | 2018-09-27 | - | Completed
CL15 | 2018-09-27 | Dharapuram | T | Unloading side ROV with ball valve- Complaint | Breakdown | Nepolean | 2018-09-27 | - | New ROV with ball valve Changed - Rectified
CL16 | 2018-09-27 | Udumalpet | C | Rule 18 work | Certification | Nepolean | 2018-09-27 | - | Completed
CL17 | 2018-09-27 | Palladam | C | Rule 18 work | Certification | Nepolean | 2018-09-27 | - | Completed
CL18 | 2018-09-27 | Ariyamangalam | A | Automation Cable Laying Work | Preventive | Chandrasekar | 2018-09-27 | - | Laying work Completed
CL19 | 2018-09-27 | Mettupalayam | R | Control Panel Testing | Preventive | Prakash | 2018-09-27 | - | Control panel testing completed
CL20 | 2018-09-28 | Sulur | C | Rule 18 work | Certification | Nepolean | 2018-09-28 | - | Completed as per peso officers
CL21 | 2018-09-28 | Saravanampatty | C | Rule 18 work | Certification | Nepolean | 2018-09-28 | - | Completed as per peso officers
CL22 | 2018-09-28 | Cantonment | A | Automation Cable Laying Work | Preventive | Chandrasekar | 2018-09-28 | - | Laying work Completed
CL23 | 2018-09-28 | Avinashi | C | Rule 18 work | Certification | Nepolean | 2018-09-28 | - | Completed
CL24 | 2018-09-29 | Sulur | C | Stamping Work | Certification | Prakash | 2018-09-29 | - | Dispenser has calibrated and stamped by DIL
CL25 | 2018-09-29 | Bhavani | G | Site Inspection | New Project | Prakash | 2018-09-29 | - | Control panel testing completed
CL26 | 2018-09-29 | Chengalpattu | C | Batchen Dispenser Stamping Work | Certification | Suneel | 2018-09-29 | - | Dispenser has calibrated and stamped by DIL
CL27 | 2018-09-29 | Theni | D | Dispensing Motor Coil conducutor and servo stabilizer servo mode problem | Breakdown | Nepolean | 2018-09-29 | - | Replaced with old service motor
CL28 | 2018-09-30 | T.V.Kovil | D | Batchen Dispenser - not working | Breakdown | Prabu | 2018-09-29 | - | Cold Boot Restarted - Rectified - Testing 4.43L
CL29 | 2018-09-30 | Bhavani | G | Final Electrical & Mechanical Work | Preventive | Chandrasekar & Prabu | 2018-09-30 | - | Inspection Completed
CL30 | 2018-09-30 | Krishnagiri | D | Dispensor One Side Problem - Metering unit inside rod broken | Breakdown | Prabu | 2018-10-02 | - | Dispenser Metering Unit New One Changed
CL31 | 2018-09-30 | Ariyamangalam | A | Automation Work | Preventive | Prakash | 2018-09-30 | - | Going On
CL32 | 2018-09-30 | Tirunelveli | T | Tank Area ROV LPG Leakage | Breakdown | Nepolean | 2018-10-01 | - | Arrested
CL33 | 2018-10-01 | Velachery | D | Point Jumping Complaint | Breakdown | Ezhil | 2018-10-01 | - | Under Observation
CL34 | 2018-10-01 | Mettupalayam | C | CCOE Final Inspection | Certification | Chandrasekar | 2018-10-02 | - | Corrections made and work completed-As per PESO Officer's Instruction
CL35 | 2018-10-01 | Viruthunagar | R | ATG Relay box drive and Dispenser A side keypad and control panel Air Solenoid Coil - Problem | Breakdown | Nepolean | 2018-10-01 | - | Not Rectified-Waiting to avail required Spares
CL36 | 2018-10-01 | Dindigul | D | One side rate setting problem | Breakdown | Nepolean | 2018-10-01 | - | Rate Set - Rectified
CL37 | 2018-10-02 | Bhavani | C | CCOE Final Inspection | Certification | Prakash | 2018-10-02 | - | Corrections made and work completed
CL38 | 2018-10-02 | Mettupalayam | C | CCOE Final Inspection | Certification | Prakash | 2018-10-02 | - | Corrections made and work completed
CL39 | 2018-10-02 | Chengalpattu | C | Rule 18 work | Certification | Suneel | 2018-10-02 | - | Completed
CL40 | 2018-10-02 | Rasipuram | G | Site Visit | Preventive | Chandrasekar | 2018-10-02 | - | Completed-Site material requirement list noted
CL41 | 2018-10-02 | Theni | R | Motor and conductor complaint | Breakdown | Prakash | 2018-10-02 | 8 hours (9am to 5 pm) | Conductor replaced and motor winded - Rectified
CL42 | 2018-10-03 | Dindigul | D | Rate settings issue | Breakdown | Prakash | 2018-10-03 | - | Rate Set - Rectified
CL43 | 2018-10-03 | Viruthunagar | D | Dispenser keypad complaint | Breakdown | Karnan | 2018-10-03 | - | Dispenser A side New keypad changed
CL44 | 2018-10-03 | T.V.Kovil | D | Air compressor continues running air solenoid coil leaking problem | Breakdown | Prabu | 2018-10-03 | - | New solenoid coil changed - Air Leaking Arrested
CL45 | 2018-10-04 | T.V.Kovil | D | Batchan Dispenser Stopped dispensing due to Error | Breakdown | Prakash | 2018-10-04 | - | Rectified-Working Normally
CL46 | 2018-10-04 | Ariyamangalam | R | Turbo Complaint | Breakdown | Prakash | 2018-10-04 | 10 mins | Direct Connection given from Decanting MCB to Control panel - Rectified-(Work done by Prasath and Sankar-Electrician)
CL47 | 2018-10-04 | Velachery | C | Rule 18 work | Certification | Suneel | 2018-10-04 | - | Completed
CL48 | 2018-10-04 | Velachery | D | TRV threading damaged | Breakdown | Suneel | 2018-10-04 | - | Replaced the same by new one
CL49 | 2018-10-04 | Bhavani | D | Dispenser is now running in test mode. It is getting fused often might be due to issues in control panel wiring | Breakdown | Nepolean | 2018-10-04 | - | It will be under observation for the next two days.
CL50 | 2018-10-05 | Mettupalayam | G | Site Visit | Preventive | Prakash | 2018-10-05 | - | Mettupalayam unloading completed. Rochester is not working and dispenser is working normal.
CL51 | 2018-10-05 | Krishnagiri | D | Dispenser Calibation work | Preventive | Prabu | 2018-10-05 | - | Metering unit replaced and Both side of the dispenser functioning properly.
CL52 | 2018-10-05 | Bhavani | D | Yenen Dispenser Calibration Work | Preventive | Prabu | 2018-10-05 | - | Completed-Sales Started
CL53 | 2018-10-05 | Mettupalayam | C | Stamping Work | Certification | Chandrasekar | 2018-10-05 | - | Completed-Sales Started
CL54 | 2018-10-05 | Mettupalayam | R | OPW (ATG) installation work | Preventive | Chandrasekar | 2018-10-05 | - | Completed-Working Condition Normal
CL55 | 2018-10-05 | Ariyamangalam | D | N2 M/C air compressor not working | Breakdown | Nepolean | 2018-10-06 | - | contractor and cable checking
CL56 | 2018-10-06 | Bhavani | R | OPW (ATG) & FRL Unit - Unavailable | Breakdown | Prabu | 2018-10-06 | - | OPW (ATG) installation work & FRL unit work - Completed
CL57 | 2018-10-06 | Mettupalayam | G | Site Visit | Preventive | Chandrasekar | 2018-10-06 | - | Dispenser working condition is normal. Rochester gauge not working.
CL58 | 2018-10-06 | Ariyamangalam | R | Air compressor problem,input line Cable problem | Breakdown | Nepolean | 2018-10-06 | - | Spare Cable laying to run compressor - Temporarily rectified
CL59 | 2018-10-06 | Renganathan, Trichy | D | On /Off switch problem | Breakdown | Nepolean | 2018-10-06 | - | New Switch Replaced
CL60 | 2018-10-06 | Hosur | D | Point Jumping Complaint | Breakdown | Prabu | 2018-10-06 | - | New switch 1no's and new nozzle 2no's changed-Testing 1.94 L
CL61 | 2018-10-07 | Bhavani | R | Servo Stabilizer - Unavailable | Preventive | Prabu | 2018-10-07 | - | Control Panel Board Servo Voltage Stabilizer installation-Completed
CL62 | 2018-10-08 | Udumalpet | D | dispenser return line vapour Ball valve liquid leakage problem | Breakdown | Chandrasekar | 2018-10-08 | - | Bolt tightened and M seal Alardite Applied - Leakage Arrested
CL63 | 2018-10-08 | Bhavani | C | Dispenser Stamping Work | Certification | Prabu | 2018-10-08 | - | Completed
CL64 | 2018-10-08 | Mettupalayam | D | Dispenser sales stopped due to motor pressure not increasing | Breakdown | Chandrasekar | 2018-10-09 | - | love jaw couplings hotter pin and screw tightened and aligned - Rectified
CL65 | 2018-10-09 | Mettupalayam | T | Unloading process | Preventive | Chandrasekar | 2018-10-09 | - | Unloading Completed. Rochester Gauge is not working and ATG is working
CL66 | 2018-10-09 | Bhavani | G | Genset Power - Problem | Breakdown | Chandrasekar | 2018-10-10 | - | Genset Changed - cant rectify the problem
CL67 | 2018-10-10 | T.V.Kovil | D | Batchen Dispenser switch one side problem | Breakdown | Prabu | 2018-10-10 | - | New Switch Replaced - Rectified
CL68 | 2018-10-11 | Cantonment | D | Pump B & D Nozzle teeth changing | Preventive | Chandrasekar | 2018-10-11 | - | Replaced - Working condition Normal
CL69 | 2018-10-12 | Udumalpet | T | Tank area LPG leackage | Breakdown | Nepolean & Prabu | 2018-10-12 | - | Bypass vapour line 1.5 ball valve bottom gasket 2 nos replaced - Rectified
CL70 | 2018-10-13 | Ariyamangalam | D | B Side Nozzle Problem | Breakdown | Sheik | 2018-10-13 | - | Spare Nozzle Changed as per the instruction of Nepolean - Testing 1.22 Ltr
CL71 | 2018-10-13 | Dharapuram | D | Dispenser side ROV Problem | Breakdown | Prabu | 2018-10-13 | - | New ROV Changed
CL72 | 2018-10-13 | Vellakovil | D | One side LPG slow delivery problem | Breakdown | Nepolean | 2018-10-13 | - | Filter cleaned - Flow is normal
CL73 | 2018-10-14 | Cantonment | D | Pump C Nozzle Teeth changing | Preventive | Chandrasekar | 2018-10-13 | - | Replaced - Working condition Normal
CL74 | 2018-10-15 | T.V.Kovil | D | Yenen Dispenser not working | Breakdown | Prabu | 2018-10-15 | - | USB Cable Problem - Rectified - Testing 1.13 L
CL75 | 2018-10-15 | Vellakovil | T | LPG Slow delivery problem & Unloading side liquid line ROV lpg leakage | Breakdown | Nepolean | 2018-10-15 | - | High flow and low flow coils cleaned and DP valve Cleaned & for Leakage Center link is problem for that lathe work is processing
CL76 | 2018-10-16 | Avinashi | D | Metering unit LPG Leakage due to bearing and oil seal | Breakdown | Nepolean | 2018-10-16 | - | New bearing and oil seal changed and Metering unit working normally.
CL77 | 2018-10-18 | Avinashi | D | Metering unit LPG Leakage | Breakdown | Nepolean | 2018-10-16 | - | A Blue O Ring inside the metering unit is damged. Blue O ring is unavailable so LPG leakage couldn't Arrest. For temporary basis, Teflon tape applied and new bearing and white o ring changed. Leakage arrested but slow delivery complaint is occurred.
CL78 | 2018-10-20 | Tirunelveli | T | Unloading Problem | Breakdown | Prabu | 2018-10-20 | - | Unloading ROV to Solenoid Coil Pneumatic Air Hose Line Connection and Dispensing ROV 1 no changed. Unloading finished and working condition normal
CL79 | 2018-10-20 | Ariyamangalam | D | B Side Nozzle Teeth damaged & C Side Push Button problem | Breakdown | Nepolean | 2018-10-20 | - | B Side 2 new nozzles Changed and C Side On/off push button Changed - Working condition normal
CL80 | 2018-10-20 | T.V.Kovil | D | Dispenser not working | Breakdown | Prakash & Arulrayappan | 2018-10-20 | - | Connection lose conduct - Rectified. Discussion on shift closing
CL81 | 2018-10-21 | Saravanampatty | G | E.B power supply earthing problem | Breakdown | Nepolean & Prabu | 2018-10-21 | - | New Earth Connected - Temporarily rectified
CL82 | 2018-10-21 | Vellakovil | D | Dispenser Slow Delivery Problem | Breakdown | Prabu | 2018-10-22 | - | Solenoid Valve Cleaned both the side and Main filter is cleaned - Slow Delivery problem rectified & Inloading ROV Leakage arrested
CL83 | 2018-10-22 | Cantonment | T | Tank 2 unloading ROV air hose leakage problem | Breakdown | Chandrasekar | 2018-10-22 | - | New Hose Changed - Working Condition Normal - Leakage Arrested
CL84 | 2018-10-22 | T.V.Kovil | D | Yenen Dispenser not working | Breakdown | Prabu | 2018-10-23 | - | Problem found in Signal USP Cable. Dispenser one time totally off and USP Cable Properly connected - rectified the problem
CL85 | 2018-10-23 | Saravanampatty | G | Voltage Leakage problem | Breakdown | Nepolean | 2018-10-23 | - | problem found in Drive so drive is removed. And problem occurred in Fill point and office room emergency cable and earthi ng also
CL86 | 2018-10-23 | Avinashi | D | A Side metering unit O Ring problem | Breakdown | Nepolean | 2018-10-23 | - | New O Ring Changed and running normally. But metering unit stops its working suddenly. Hence confirmed that A side Metering unit is problem
CL87 | 2018-10-24 | Vellakovil | D | Dispenser Slow Delivery Problem | Breakdown | Chandrasekar | 2018-10-24 | - | New Filter changed and Solenoid Valve Cleaned - Rectified and calibration testing done
CL88 | 2018-10-24 | Velachery | D | Leakage in Unloading Pump Outlet & Dispenser C and D side Frequent Hanging while fuelling | Breakdown | Prakash | 2018-10-26 | - | Unloading Pump Outlet has been removed and Welded. Leak has not been able to arrest. Again it was dismantled, Pipe threaded and Inserted and then made welding on all the sides of pump. Leak got arrested. & Dispenser Hanging problem due to loose connection of internal wires which was distrupted while changing of fused light inside the Dispenser. Rectified and observed.
CL89 | 2018-10-25 | Ariyamangalam | D | Nozzle Testing | Preventive | Nepolean | 2018-10-25 | - | B Side one nozzle serviced and tested - Testing 4.53L
CL90 | 2018-10-26 | Rasipuram | D | Tank Nitrogen Testing | Preventive | Chandrasekar | 2018-10-26 | - | Testing Completed - No Leakage
CL91 | 2018-10-26 | T.V.Kovil | R | MOL problem (EB) - 2 times occurred | Breakdown | Nepolean | 2018-10-26 | - | Reset done - Running - Rectified
CL92 | 2018-10-30 | Thuraiyur | D | Dispenser One Side Problem | Breakdown | Prabu | 2018-10-30 | - | Dispenser breakaway one side problem. Solenoid valve to breakaway and breakaway to nozzle line one time LPG vent after line filling that time working is normal condition. Total testing 12.96
CL93 | 2018-10-30 | Vellakovil | D | LPG pipeline purged with N2 | Breakdown | Prakash & Chandrasekar | 2018-10-30 | - | Impurities removed and problem rectified. Dispenser is functioning normal.
CL94 | 2018-10-31 | Avinashi | D | Metering unit problem | Breakdown | Prakash & Chandrasekar | 2018-10-31 | - | New Metering unit replaced - Rectified
CL95 | 2018-10-31 | Cantonment | D | Dispenser B side nozzle teeth locked | Breakdown | Prabu | 2018-10-31 | - | Nozzle teeth assembly removed and refitted - locking problem rectified - Nozzle Working normally
CL96 | 2018-10-31 | Saravanampatty | G | Electrical Issues | Breakdown | Prakash & Chandrasekar | 2018-10-31 | - | Electrica issues Solved - Rectified
CL97 | 2018-11-01 | Avinashi | C | Stamping Work | Certification | Prakash & Chandrasekar | 2018-11-01 | - | Stamping Work Completed
CL98 | 2018-11-01 | Sulur | D | Nozzle & Control Panel Relay Complaint | Breakdown | Prakash & Chandrasekar | 2018-11-02 | - | Nozzle Lock complaint Rectified & Decanting Relay Replaced - Rectified
CL99 | 2018-11-02 | Palladam | G | New Dispenser pipeline and Electrical cable measuring work | New Project | Prakash & Chandrasekar | 2018-11-02 | - | Measuring work Completed
CL100 | 2018-11-02 | Velachery | D | Dispenser 2 - Hanged | Breakdown | Suneel | 2018-11-02 | - | Earthing connected from panel. It is working and under observation.
CL101 | 2018-11-03 | Dharapuram | G | Pump is not working with genset | Breakdown | Prakash & Chandrasekar | 2018-11-03 | - | Genset Wiring Checked and Rectified
CL102 | 2018-11-03 | Vellakovil | D | B Side Nozzle Teeth Complaint & Unloading Liquid ROV 2 nos Leakage | Breakdown | Prakash & Chandrasekar | 2018-11-03 | - | Nozzle teeth Serviced & ROV Tightened - Recfied
CL103 | 2018-11-09 | Velachery | D | Dispenser 2 flat cable changing | Preventive | Suneel | 2018-11-09 | - | Cable changing work completed and it is under observation.
CL104 | 2018-11-10 | Ariyamangalam | D | 4 No Spare Nozzle Service & Testing - D Side | Preventive | Nepolean | 2018-11-10 | - | Spare Nozzle 4 No Tested and Serviced. D Side Testing: 15.11 L
CL105 | 2018-11-11 | Tirunelveli | D | Power chord - motor line Diode solidring problem & B side liter Display cable one no problem | Breakdown | Nepolean | 2018-11-12 | - | Resoldering Work done & B side push button 1 no changed - Rectified
CL106 | 2018-11-12 | Viruthunagar | R | ATG Relay box - Drive - Complaint | Breakdown | Nepolean | 2018-11-12 | - | Drive - Power supply 12 v - Replaced with new one - Rectified
CL107 | 2018-11-12 | Cantonment | D | B & D Side Nozzle Servicing | Preventive | Chandrasekar | 2018-11-12 | - | Serviced - Working condition normal
CL108 | 2018-11-13 | Paramathi velur | T | Tank Installation | Preventive | Chandrasekar | 2018-11-13 | - | Tank installation and Hydro work completed - No Leakage.
CL109 | 2018-11-13 | Dindigul | T | Decanding line liquid ROV Lpg leakage problem | Breakdown | Nepolean | 2018-11-13 | - | Ball valve center ring side - metal washer new one no changed - Leakage arrested
CL110 | 2018-11-13 | Karur | D | Dispenser A side not working | Breakdown | Nepolean | 2018-11-13 | - | A Side DP Valve high flow & Low Flow solenoid coil cleaned & Dp valve bottom Butten and screw bottom Excess flow valve Block found - Block Released - Rectified
CL111 | 2018-11-13 | Rasipuram | C | Peso Inspection | Certification | Prakash | 2018-11-14 | - | N2 venting, pneumatic and electrical connection work in progress.Paver blocks inside the yard yet to complete, expecting them to complete it tomorrow. Due to this LPG decanting postponed. Decanting will be done after the paver blocks laid inside the yard.
CL112 | 2018-11-14 | Tirunelveli | D | Dispenser not working | Breakdown | Prabu | 2018-11-14 | - | Power chord changed but couldn't rectify the problem
CL113 | 2018-11-14 | Rasipuram | G | Decanting ,testing,and dispenser stamping | New Project | Prakash & Chandrasekar | 2018-11-14 | - | Completed Successfully
CL114 | 2018-11-15 | Ariyamangalam | D | A Side OPW nozzle locked | Breakdown | Nepolean | 2018-11-15 | - | New service nozzle one number replaced - Rectified & working condition normal
CL115 | 2018-11-16 | Cantonment | D | C Side keypad is not functioning | Breakdown | Nepolean | 2018-11-16 | - | New keypad replaced - Rectified
CL116 | 2018-11-16 | Tirunelveli | D | Dispenser Error & one side dispenser Litre Cable problem and another side Amount cable problem | Breakdown | Nepolean | 2018-11-19 | - | EPROM IC, Power Chord & Line filter changed & Motherboard checked -Rectified - online UPS, litre cable and amount cable required.
CL117 | 2018-11-17 | T.V.Kovil | D | B Side nozzle problem | Breakdown | Prabu | 2018-11-17 | - | Spare nozzle changed - Testing: 1.17 Ltrs
CL118 | 2018-11-17 | Rasipuram | R | Compressor overload relay is not working | Breakdown | Chandrasekar | 2018-11-17 | - | New Relay replaced & Electrical wiring work completed. Working condition normal.
CL119 | 2018-11-19 | Chengalpattu | R | Omntec ATG fuse blown up due to Lizard entry. | Breakdown | Suneel | 2018-11-19 | - | Rectified - Now working and sealed properly
CL120 | 2018-11-21 | Cantonment | D | Pump C & D nozzle hose sleeve changing | Preventive | Chandrasekar | 2018-11-21 | - | C pump testing - 1.03 Ltrs; D pump testing - 0.97 Ltrs
CL121 | 2018-11-21 | Mettupalayam | T | Above ground pump love jaw coupling problem & Decanting vapour ROV Leakage | Breakdown | Chandrasekar | 2018-11-22 | - | Love jaw couplings 1 no changed & hotter pin 1 no changed & dispensing and decanting vapour,liquid line insulation gas kit changed & Ball valve stem tightening- Rectified
CL122 | 2018-11-22 | T.V.Kovil | D | B Side nozzle and Spare nozzle serviced & testing | Preventive | Prabu | 2018-11-22 | - | Nozzle and Spare nozzle tested - B side Nozzle lifting trigger and lifting spring 1 no changed and nozzle teeth 4 no changed
CL123 | 2018-11-23 | Saravanampatty | T | Dispensing return line vapour ball valve gasket leakage & decanting ROV air line leakage | Breakdown | Chandrasekar | 2018-11-23 | - | Bolt tightened & new fittings and hose changed - working condition normal - Rectified
CL124 | 2018-11-23 | Chengalpattu | D | Batchen dispenser return signal problem | Breakdown | Suneel | Processing | - | Waiting for MX0 auxiliary contactor R1 Relay
CL125 | 2018-11-23 | Vellakovil | D | Rate Changing | Preventive | Chandrasekar | 2018-11-23 | - | Rate set & K factor changed - Rectified
CL126 | 2018-11-23 | Velachery | R | Compressor motor fan cottor pin broken | Breakdown | Suneel | 2018-11-23 | - | Replaced the cottor pin - Rectified
CL127 | 2018-11-24 | Velachery | D | Above ground motor spider replacement | Breakdown | Suneel | 2018-11-24 | - | Replaced
CL128 | 2018-11-24 | Ariyamangalam | D | Dispenser B side nozzle LPG Leakage- Nozzle teeth problem | Breakdown | Nepolean | 2018-11-24 | - | Service spare nozzle changed - Rectified
CL129 | 2018-11-25 | Chengalpattu | D | Batchen dispenser return signal problem | Breakdown | Suneel | 2018-11-25 | - | MX0 E22 auxiliary contactor R1 Relay changed - Rectified
CL130 | 2018-11-25 | Avinashi | T | Tank 2 unloading - Complaint | Breakdown | Nepolean | 2018-11-25 | - | Tank 2 unloading solenoid coil and R gate changed - Unloading working condition normal & FRL filter fitting one no changed and 4 nozzle serviced. Required materials noted.
CL131 | 2018-11-26 | Tirunelveli | D | Display card fitting work | Breakdown | Nepolean | 2018-11-27 | - | Fitting completed - Two side display condition and pump working condition normal - Rectfied
CL132 | 2018-11-27 | T.V.Kovil | D | A side nozzle hose damage | Breakdown | Prabu | 2018-11-27 | - | New sleeve changed - Rectified
CL133 | 2018-11-27 | Velachery | D | Nozzle C - Breakaway coupling Replacement | Breakdown | Suneel | 2018-11-27 | - | Replaced
CL134 | 2018-11-28 | Cantonment | D | C and D nozzle complaint - Leakage | Breakdown | Chandrasekar | 2018-11-28 | - | New nozzles4 no changed - Working condition normal & C.testing.1.05 litre D.testing.2.86 litre - Rectified
CL135 | 2018-11-28 | Ariyamangalam | R | Motor Over Loading (MOL) problem | Breakdown | Prabu | 2018-11-29 | - | Turbo Drive reset - Rectified
CL136 | 2018-11-29 | Ariyamangalam | D | D side 3 nozzles servicing and testing | Preventive | Nepolean | 2018-11-29 | - | Spare nozzles 4 no from our franchesees changed. Nozzle 4 nos and O ring 1 no changed. Testing - 5.87 Ltrs - Rectified
CL137 | 2018-11-30 | Cantonment | D | A & B pump new nozzles changing | Breakdown | Chandrasekar | 2018-11-30 | - | Changed - Working condition normal. A. Testing - 0.92 L & B. Testing - 0.86 L - Rectified
CL138 | 2018-12-01 | Velachery | D | D nozzle display board complaint | Breakdown | Suneel | 2018-12-01 | - | Repaired and under observation - Rectified
CL139 | 2018-12-03 | Paramathi velur | T | CP Work | New Project | Prabu | 2018-12-03 | - | Attended and completed
CL140 | 2018-12-03 | Vellakovil | D | Dispenser Complaint | Breakdown | Prabu | 2018-12-03 | - | Filter and Solenoid Valve Cleaned - Flow is normal - Rectified
CL141 | 2018-12-03 | Avinashi | T | Unloading process Tank2 not working - air hose damaged | Breakdown | Nepolean | 2018-12-03 | - | Tank 2 new one air line laying work done and ROV 2 nos fitted - Rectified
CL142 | 2018-12-03 | Rasipuram | T | Decanting pipe line leakage | Breakdown | Prabu | 2018-12-03 | - | Leakage Arrested - Rectified
CL143 | 2018-12-04 | Cantonment | T | Decanting liquid,vapour line ball valve leakage | Breakdown | Chandrasekar | 2018-12-04 | - | Stem tightening done - Leakage Arrested
CL144 | 2018-12-04 | Mettupalayam | T | Unloading process not working | Breakdown | Nepolean | 2018-12-05 | - | Excess flow valve block released - Rectified
CL145 | 2018-12-04 | T.V.Kovil | D | Dispenser B Side nozzle complaint | Breakdown | Prabu | 2018-12-04 | - | Spare nozzle changed - Testing 1.15 L Rectified
CL146 | 2018-12-06 | Ariyamangalam | D | Hosur Nozzles testing | Preventive | Nepolean | 2018-12-06 | - | 2 nozzles serviced and tested - 4 new nozzle teeth changed for a nozzle - d side testing: 8.62 L - completed
CL147 | 2018-12-07 | Thuraiyur | T | DPS line SS tube leakage and unloading liquid ROV open & close function problem | Breakdown | Prabu | 2018-12-07 | - | Leakage arrested & unloading liquid ROV Changed - Rectified
CL148 | 2018-12-07 | Dindigul | T | Unloading pump stuck - up | Breakdown | Chandrasekar | 2018-12-07 | - | Grease applied on both the sides and new 2 belts changed - Hence rectified
CL149 | 2018-12-08 | T.V.Kovil | D | A side dispenser nozzle problem | Breakdown | Prabu | 2018-12-08 | - | Nozzleteeth 4 nos changed and spare nozzle serviced - Rectified
CL150 | 2018-12-08 | Ariyamangalam | D | Dispenser1 Nozzle 4 no's servicing and testing | Preventive | Nepolean | 2018-12-08 | - | Serviced - Working condition normal D side testing - 9.06L
CL151 | 2018-12-10 | Vellakovil | D | Dispenser one side not working | Breakdown | Nepolean | 2018-12-10 | - | Two side High flow , Low flow and filter cleaned hence working condition normal - Rectified
CL152 | 2018-12-10 | Cantonment | D | Dispenser On/Off new switch two side changing | Preventive | Chandrasekar | 2018-12-10 | - | Changed - Working condition normal.
CL153 | 2018-12-12 | Cantonment | G | Genset servicing | Preventive | Balasundar | 2018-12-12 | - | Oil,oil filter,diesel filter changed at service hour-5825,next service hour-6225 - Attended
CL154 | 2018-12-12 | Velachery | C | Stamping Work | Certification | Venkatesh | 2018-12-12 | - | Stamping Work Completed
CL155 | 2018-12-14 | T.V.Kovil | R | DOL Starter Complaint | Breakdown | Prabu | 2018-12-14 | - | New 7.5HP DOL starter changed - Rectified
CL156 | 2018-12-15 | Ariyamangalam | R | servo stabilizer servo mode problem | Breakdown | Nepolean | 2018-12-18 | - | Sero mode problem rectified
CL157 | 2018-12-17 | Thuraiyur | D | Dispenser hose breakaway coupling LPG Leakage | Breakdown | Chandrasekar | 2018-12-17 | - | Dispenser hose breakaway coupling new 1 number changed - Leakage arrested - Rectified
CL158 | 2018-12-17 | Ariyamangalam | D | A side nozzle LPG Leakage problem | Breakdown | Nepolean | 2018-12-17 | - | New nozzle changed - Rectified
CL159 | 2018-12-17 | Theni | R | MOL Contactor Problem | Breakdown | Nepolean | 2018-12-18 | - | MOL relay auto manual position changed. EB room new emergency switch changed and Dispenser two side on/off switch loose connection serviced and Dispensing motor on condition 5.50. 5.74. 5.85 AMPS and voltage : 235. 237. 2.40 - Two nozzle working condition normal - Rectified
CL160 | 2018-12-18 | Dindigul | R | Servo Stabilizer - servo mode not functioning | Breakdown | Nepolean | 2018-12-18 | - | Working in By-Pass Mode
CL161 | 2018-12-20 | Vellakovil | D | Dispenser one side not working | Breakdown | Nepolean | 2018-12-20 | - | A side high flow and low flow valve cleaned - low flow coil Dust block released . New filter changed hence two side running condition normal - Rectified
CL162 | 2018-12-21 | Tirunelveli | D | Online UPSConnection & Dispenser Error | Breakdown | Nepolean | 2018-12-23 | - | Online UPS installation completed and dispenser error cleared Working condition normal - Ups input voltage : 239 and output voltage : 230v
CL163 | 2018-12-22 | Rasipuram | T | Online UPS Installation & Decanting mode power problem | Breakdown | Chandrasekar | 2018-12-23 | - | Online UPS installation completed and Power problem rectified. Decanting liquid hose adapter tightened. Working condition normal
CL164 | 2018-12-22 | T.V.Kovil | T | Unloading venting pipeline leakage | Breakdown | Prabu | 2018-12-26 | - | Y Strainer filter and Earth clamps cleaned - Leakage Arrested - Rectified
CL165 | 2018-12-24 | Cantonment | R | Air Compressor and Oil changing | Preventive | Chandrasekar | 2018-12-24 | - | Air compressor 2 nos and Oil changed - Working condition normal
CL166 | 2018-12-24 | T.V.Kovil | D | B side .Dispenser nozzle not working | Breakdown | Prabu | 2018-12-24 | - | Solenoid coil cleaned - Rectified
CL167 | 2018-12-26 | Ariyamangalam | D | On/Off push button switch not working | Breakdown | Nepolean | 2018-12-26 | - | New On / Off push button switch replaced - Rectified
CL168 | 2018-12-26 | Palladam | D | Additional Dispenser Installation | Preventive | Prakash, Chandrasekar & Vignesh | 2019-12-30 | 14 Hours (29-12-2018 10 am to 30-12-2018 12 am) | Additional Dispenser Installed
CL169 | 2018-12-27 | Theni | C | Stamping Work | Certification | Chandrasekar | 2018-12-28 | - | Stamping renewal completed, K factors changed, Both side dispenser ON/OFF switch problem rectified. A side nozzle 'O' - Ring adjusted with teflon tape to have proper grip. B side flow rate valve adjusted to ensure smooth flow
CL170 | 2018-12-27 | Ariyamangalam | T | Unloading side venting line (both liquid and vapour line) slow delivery & tanker earthing GI patta corroded | Breakdown | Nepolean | 2018-12-27 | - | High flow and low flow coils cleaned and Corrosion cleaned and paint applied - Rectified
CL171 | 2018-12-28 | Ariyamangalam | R | Compressor oil changing | Preventive | Nepolean | 2018-12-28 | - | Compressor oil changed
CL172 | 2019-01-04 | Salem | R | PLC and ROV work | Breakdown | Nepolean | 2019-01-04 | - | New ROV replaced & PLC malfunctioning due to servo stabilizer problem and absence of online UPS - Partially Rectified
CL173 | 2019-01-04 | Palladam | C | Stamping Work & Dispenser On/off switch complaint | Certification | Nepolean | 2019-01-05 | - | Stamping completed. A side On/off switch changed & B side nozzle teeth 4nos changed - Rectified - working conditiom normal
CL174 | 2019-01-05 | Vellakovil | D | One side meter unit top LPG leakage problem | Breakdown | Nepolean | 2019-01-06 | - | Seal kit complaint hence new seal kit and new bearing changed - Rectified - working conditiom normal
CL175 | 2019-01-06 | Theni | D | Dispenser Error 39 occurred | Breakdown | Chandrasekar | 2019-01-07 | - | New mother board replaced - Error 39 rectified and kept under observation

## Dropdown (hidden)
Ariyamangalam
Attur
Avinashi
Chengalpattu
Velachery
Mettupalayam
Saravanampatty
Sulur
Dharapuram
Dindigul
Bhavani
Hosur
Kangeyam
Karur
Aravakurichi
Krishnagiri
Paramathyvelur
Rasipuram
Palladam
Pudukkottai
Ramanathapuram
Salem
Theni
Thuraiyur
Tirunelveli
Cantonment
T.V.Kovil
Udumalpet
Vellakoil
Virudhunagar