## All
Service Logs - Jan' 2020 to Dec' 2020
ticket_no | date | name_of_the_outlet | code | nature_of_the_complaint | breakdown__ preventive | service_engineer | rectified_on | interruption_of_sales_if_any__time_duration | details_of_work_done
CL611 | 2020-01-01 | Ariyamangalam | D | A side nozzle leakage | Breakdown | Thirumalaisamy | 2020-01-01 | - | Nozzle Teeth 4 nos replaced - Rectified
CL612 | 2020-01-03 | Karur | G | Electrical cable laying work | Breakdown | Kathiresan | 2020-01-03 | - | ATG, HLA, Fill point emergency & Office room emergency new cable changed - Rectified
CL613 | 2020-01-03 | Tharamangalam | T | Cathodic Protection line connection | New Project | Prabu | 2020-01-03 | - | CP Connection completed
CL614 | 2020-01-04 | Hosur | D | Pump B nozzle complaint | Breakdown | Suresh | 2020-01-04 | - | Nozzle replaced - Rectified
CL615 | 2020-01-05 | Tirunelveli | D | Dispenser not working & Display cable damaged | Breakdown | Nepolean | 2020-01-06 | - | Dispenser fuse replaced & New display cable replaced - Rectified
CL616 | 2020-01-06 | Kodungaiyur | D | Dispensing ROV Leakage | Breakdown | Suneel Sagar | 2020-01-06 | - | Leakage arrested by servicing - Rectified
CL617 | 2020-01-06 | Tharamangalam | T | Tank flanges installation | New Project | Prabu | 2020-01-06 | - | Tank flanges installed - Attended
CL618 | 2020-01-07 | Tharamangalam | G | Mechanical & Pipeline work | New Project | Thirumalaisamy | 2020-01-12 | - | Pipeline welding work, pipeline hydro test completed & Rule 33 data collected - Attended
CL619 | 2020-01-07 | Kodumudi | R | Compressor NRV switch failure | Breakdown | Prabu | 2020-01-08 | - | NRV switch replaced by Compressor service people - Rectified
CL620 | 2020-01-07 | Manapparai | C | Tank purging, unloading, dispenser commissioning & Stamping | New Project | Prakash | 2020-01-09 | - | Commissioning & Stamping completed - Attended
CL621 | 2020-01-08 | Perundurai | G | Control panel electrical cable laying work | New Project | Prabu | 2020-01-10 | - | Electrical work completed - Attended
CL622 | 2020-01-10 | Ariyamangalam | D | Hosur nozzle servicing and testing | Preventive | Nepolean | 2020-01-10 | - | Nozzle serviced and tested - Testing 1.58L
CL623 | 2020-01-11 | Uthamapalayam | T | Tank installation | New Project | Nepolean | 2020-01-11 | - | Tank installation completed - Attended
CL624 | 2020-01-12 | Perundurai | T | N2 Test | New Project | Kathiresan & Prabu | 2020-01-12 | - | Nitrogen test completed - Attended
CL625 | 2020-01-12 | Manapparai | R | Stabilizer servo mode complaint | Breakdown | Chandrasekar | 2020-01-12 | - | Input power settings changed - Working fine - Rectified
CL626 | 2020-01-13 | Palladam | C | Dispenser stamping | Certification | Kathiresan & Prabu | 2020-01-13 | - | Dispenser stamping completed - Attended
CL627 | 2020-01-13 | Udumalpet | D | Dispenser one side not working | Breakdown | Kathiresan & Prabu | 2020-01-13 | 1 Hour | Metering unit bearing replaced - Testing: 100L - Rectified
CL628 | 2020-01-14 | Hosur | G | Yenen dispenser UPS battery complaint | Breakdown | Suresh | 2020-01-14 | - | New UPS battery replaced - Rectified
CL629 | 2020-01-15 | Kodungaiyur | T | Fill point ball valve leakage | Breakdown | Suneel Sagar | 2020-01-15 | - | Leakage arrested by gland packing seal changed & tightened- Rectified
CL630 | 2020-01-15 | Ariyamangalam | D | D side nozzle complaint & Nozzle servicing & testing | Breakdown | Nepolean | 2020-01-15 | - | Service nozzle replaced - Rectified D side nozzle serviced & tested - Testing 5.69L - Attended
CL631 | 2020-01-18 | Vellakovil | G | FRL unit leakage | Breakdown | Prabu | 2020-01-18 | - | Line is directed - Working fine - Rectified temporarily
CL632 | 2020-01-21 | Ariyamangalam | D | A side breakaway coupling LPG leakage | Breakdown | Nepolean | 2020-01-21 | - | New breakaway coupling changed - Rectified
CL633 | 2020-01-22 | Erode | R | Soft starter fixing | Preventive | Prabu | 2020-01-22 | - | Soft starter fixed - Working fine - Attended
CL634 | 2020-01-23 | Bhavani | D | Dispenser one side slow delivery | Breakdown | Prabu | 2020-01-23 | - | Excess flow valve center shaft broken - Line bypassed - To be replaced after receiving the material - Partially rectified
CL635 | 2020-01-25 | Rasipuram | R | Soft starter fixing | Preventive | Prabu | 2020-01-25 | - | Soft starter fixed - Working fine - Attended
CL636 | 2020-01-25 | Bhavani | D | Excess flow valve replacement | Preventive | Prabu | 2020-01-25 | - | Excess flow valve replaced - Attended
CL637 | 2020-01-26 | Cantonment | D | Batchen dispenser liquid ROV LPG leakage | Breakdown | Chandrasekar | 2020-01-26 | - | New ROV replaced - Rectified
CL638 | 2020-01-27 | Ariyamangalam | D | D side low flow slow delivery | Breakdown | Nepolean | 2020-01-27 | - | Filter cleaned - Working fine - Rectified
CL639 | 2020-01-28 | Attur | G | Compressor continuous running due to air leakage | Breakdown | Kathiresan | 2020-01-30 | - | Pressure switch replaced - Rectified
CL640 | 2020-01-29 | Bodi | T | Tank hydro test | New Project | Gowtham | 2020-01-30 | - | Tank hydro test and CP installation completed - Tested pressure - 28kg/sq.cm
CL641 | 2020-01-29 | Uthamapalayam | T | Tank hydro test | New Project | Gowtham | 2020-01-30 | - | Tank hydro test and CP installation completed - Tested pressure - 29kg/sq.cm
CL642 | 2020-01-30 | Pudukkottai | D | A side slow delivery | Breakdown | Chandrasekar & Thirumalaisamy | 2020-02-02 | - | Dispensing motor suction problem - Bypass valve cleaned and pressure adjusted - Inlet liquid line connected through emergency evacuation - Rectified
CL643 | 2020-01-30 | T.V.Kovil | D | Motherboard testing at A side | Preventive | Nepolean | 2020-01-30 | - | Motherboard tested - Testing: 13.31 L - Attended
CL644 | 2020-01-30 | Palladam | D | Dispenser not working | Breakdown | Prabu | 2020-01-31 | - | Control Panel wires reconnected - Working fine - Rectified
CL645 | 2020-01-31 | Tirunelveli | D | Yenen dispenser LPG slow delivery due to Turbo drive PLC problem | Breakdown | Nepolean | 2020-01-31 | - | Tank 2 - Turbo drive PLC card replaced - Working fine - Rectified
CL646 | 2020-01-31 | Udumalpet | D | Dispenser one side slow delivery | Breakdown | Prabu | 2020-01-31 | - | High flow low flow valve cleaned - Flow adjusted - Rectified
CL647 | 2020-01-31 | Vadivelan Nagar | A | Automation installation | New Project | Prakash & Prasath | 2020-02-02 | - | Installation completed and Automation is online - Attended
CL648 | 2020-02-02 | Chengalpattu | D | Batchen dispenser mother board replacement | Preventive | Prakash | 2020-02-02 | - | Motherboard replaced - Working fine and under observation - Attended
CL649 | 2020-02-03 | Karur | T | Unloading point leakage & Program On/Off switch complaint | Breakdown | Kathiresan | 2020-02-03 | - | Program key replaced Ballvalve leakage arrested applying teflon tape - Rectified
CL650 | 2020-02-03 | Cantonment | D | Batchen dispenser liquid ROV & Decanting vapour line ball valve with ROV complaint | Breakdown | Chandrasekar | 2020-02-03 | - | Liquid line ROV & Vapour line ballvalve with ROV replaced - Rectified
CL651 | 2020-02-03 | Ariyamangalam | D | D side meterring unit complaint | Breakdown | Nepolean | 2020-02-03 | - | Bearing and oil seal kit changed - Working fine -Testing -12.39L - Rectified
CL652 | 2020-02-04 | Dindigul | D | Nozzle 5m hose LPG leakage | Breakdown | Chandrasekar | 2020-02-04 | - | New 5m hose replaced - Testing 0.83 L - Rectified
CL653 | 2020-02-05 | Tharamangalam | G | GI flat welding, Electrical wire and pneumatic hose line laying | New Project | Prabu | 2020-02-05 | - | Welding and wire laying completed - Attended
CL654 | 2020-02-06 | Perambalur | G | Site measurement | New Project | Prakash, Kathiresan & Gowtham | 2020-02-06 | - | Site measurement completed - Attended
CL655 | 2020-02-06 | Virudhachalam | T | Tank installation | New Project | Prakash, Kathiresan & Gowtham | 2020-02-06 | - | Tank installation completed - Attended
CL656 | 2020-02-08 | Ariyamangalam | D | B side nozzle lock spring complaint | Breakdown | Nepolean | 2020-02-08 | - | New lock spring changed - Rectified
CL657 | 2020-02-09 | Kodumudi | C | Calibration | Certification | Suneel Sagar & Prakash | 2020-02-09 | - | Calibration completed - Testing : 467.76- Attended
CL658 | 2020-02-09 | Theni | T | Dispensing mode complaint and MNX 18 contactor complaint | Breakdown | Nepolean | 2020-02-10 | - | Control panel relay complaint - New 24 DC relay replaced - Rectified
CL659 | 2020-02-11 | Dharapuram | D | B side dispenser not working due to pulsar unit complaint | Breakdown | Nepolean | 2020-02-10 | - | New pulsar unit replaced - Rectified
CL660 | 2020-02-11 | Erode | T | Unloading hose leakage at both side | Breakdown | Prabu | 2020-02-11 | - | Both side adapter refitted - Leakage arrested - Rectified
CL661 | 2020-02-11 | Bodi | G | Trench, dispensing and unloading foundation marking | New Project | Prakash, Arjith & Gowtham | 2020-02-11 | - | Markings completed
CL662 | 2020-02-11 | Uthamapalayam | G | Trench, dispensing and unloading foundation marking | New Project | Prakash, Arjith & Gowtham | 2020-02-11 | - | Markings completed
CL663 | 2020-02-12 | Coimbatore | G | Control panel testing | Preventive | Prakash & Kathiresan | 2020-02-13 | - | Testing & Reprogramming completed - Attended
CL664 | 2020-02-12 | Ariyamangalam | D | D side china nozzle servicing and testing from Virudhunagar | Preventive | Nepolean | 2020-02-12 | - | Nozzle serviced and tested - Testing 1.62L
CL665 | 2020-02-12 | Chengalpattu | D | Batchen dispenser flat cable complaint | Breakdown | Suneel Sagar | 2020-02-12 | - | Flat cable replaced - Rectified
CL666 | 2020-02-14 | Cantonment | R | Control panel surge protector B phase burned | Breakdown | Chandrasekar | 2020-02-14 | - | New surge protector replaced - Rectified
CL667 | 2020-02-14 | Ariyamangalam | D | B side batchen dispenser on/off switch complaint | Breakdown | Nepolean | 2020-02-14 | - | New on/off switch replaced - Rectified
CL668 | 2020-02-14 | Salem | T | Tank area excess flow valve blocked | Breakdown | Prakash, Nepolean & Prabu | 2020-02-22 | 14-02-2020 (5 pm) to 20-02-2020 (5 am) | Above ground dispensing pump welded and tested - Suction is good - Testing : 26L - Rectified
CL669 | 2020-02-15 | Udumalpet | D | Dispenser one side not working - Metering unit leakage | Breakdown | Chandrasekar & Prabu | 2020-02-15 | - | Bearing and oil seal kit changed - Working fine -Testing -71.20L - Rectified
CL670 | 2020-02-15 | Paramathivelur | A | Automation installation | New Project | Madhavan & Kathiresan | 2020-02-15 | - | Automation brought online with mobile billing - Rectified
CL671 | 2020-02-15 | Vellakovil | C | Dispenser Calibration | Certification | Prabu & Kathiresan | 2020-02-15 | - | Dispenser calibration completed - Attended
CL672 | 2020-02-19 | Avinashi | T | Tank 2 - not dispensing | Breakdown | Chandrasekar & Gowtham | 2020-02-19 | - | Air line complaint - Pneumatic hose replaced - Rectified
CL673 | 2020-02-20 | Chengalpattu | D | Dispenser restart compliant & Error 39 | Breakdown | Suneel Sagar | 2020-02-22 | - | EPROM & Communication cable changed - Motherboard reset done - EPROM U13 IC replaced - Totalizer reset done - Working fine - Rectified
CL674 | 2020-02-21 | Ariyamangalam | D | A side nozzle leakage | Breakdown | Nepolean | 2020-02-21 | - | New Nozzle replaced - Working fine - Rectified
CL675 | 2020-02-22 | Virudhachalam | T | Tank hydro test | New Project | Thirumalaisamy & Gowtham | 2020-02-22 | - | Hydro test completed - Attended
CL676 | 2020-02-22 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2020-02-22 | - | Nozzle serviced and tested - Testing: 3.60L - Attended
CL677 | 2020-02-23 | Paramathivelur | G | Online UPS not working | Breakdown | Kathiresan | 2020-02-23 | - | Dust formation and switch not working properly - Cleaned and serviced - Rectified
CL678 | 2020-02-24 | Uthamasolapuram | T | Tank installation | New Project | Prabu & Gowtham | 2020-02-24 | - | Tank installation completed - Attended
CL679 | 2020-02-24 | Tharamangalam | G | Electrical work | New Project | Prabu & Gowtham | 2020-02-25 | - | Electrical cable work completed - Attended
CL680 | 2020-02-26 | Pudukkottai | G | Preventive maintenance & Online UPS servicing | Preventive | Chandrasekar & Thirumalaisamy | 2020-02-26 | - | Online UPS servicing completed & Preventive maintenance done and found satisfactory
CL681 | 2020-02-26 | Thuraiyur | T | Unloading point vapour line leakage | Breakdown | Kathiresan | 2020-02-26 | - | 40 NB ROV - Air leakage - New ROV replaced - Rectified
CL682 | 2020-02-26 | Velachery | D | D side solenoid leakage | Breakdown | Suneel Sagar | 2020-02-26 | - | Leakage arrested by applying teflon and anabond - Rectified
CL683 | 2020-02-27 | Tharamangalam | G | Electrical line completion and fittings work | New Project | Prabu | 2020-02-27 | - | Electrical line termination completed and fittings work completed
CL684 | 2020-02-28 | T.V.Kovil | D | B side on/off switch complaint and Nozzle leakage | Breakdown | Kathiresan | 2020-02-28 | - | Nozzle teeth 4 nos replaced & On/Off switch changed - Rectified
CL685 | 2020-02-28 | Udumalpet | D | Additional dispenser pipeline welding hydrotest and Installation | New Project | Prakash & Kathiresan | 2020-03-01 | 10.30pm to 4 am | Installation completed - Internal calibration done - Attended
CL686 | 2020-02-28 | Dindigul | D | Dispensing complaint | Breakdown | Nepolean | 2020-02-29 | 3 Hours | Control panel MOL Relay and contactor changed - Dispenser fuse changed - Rectfied
CL687 | 2020-02-29 | Chengalpattu | T | Equalization line SS connector leakage | Breakdown | Suneel Sagar | 2020-02-29 | - | Leakage arrested by applying teflon - Rectified
CL688 | 2020-02-29 | Karur | D | One side nozzle not working | Breakdown | Nepolean | 2020-02-29 | - | Excess flow valve blocks removed - Solenoid coil and DP valve cleaned - Working fine - Rectified
CL689 | 2020-03-02 | Kodungaiyur | G | Preventive Maintenance | Preventive | Suneel Sagar | 2020-03-02 | - | A side nozzle hammers replaced - B side Hose retraction rope fixed properly and surge protector relay - 1 no replaced - Attended
CL690 | 2020-03-02 | Udumalpet | C | Batchen & Yenen dispensers calibration and stamping | Certification | Prabu | 2020-03-03 | - | Both dispensers stamping and stamping completed - Testing: 258.99L - Attended
CL691 | 2020-03-03 | Bodi | G | Site Visit | Preventive | Prakash, Thirumalaisamy & Karthik (Canopy) | 2020-03-03 | - | Mechanical work started - Site visit completed
CL692 | 2020-03-03 | Uthamapalayam | G | Site Visit | Preventive | Prakash, Thirumalaisamy & Karthik (Canopy) | 2020-03-03 | - | Trench and canopy foundation marked - Site visit completed
CL693 | 2020-03-03 | Palladam | T | Ballvalve ROV Leakage | Breakdown | Prabu | 2020-03-03 | - | ROV set replaced - Leakage arrested - Rectified
CL694 | 2020-03-05 | Ariyamangalam | D | Dispenser nozzle NRV O ring complaint | Breakdown | Nepolean | 2020-03-05 | - | Service nozzle replaced - Testing: 3.20L -Rectified
CL695 | 2020-03-06 | Aravakurichi | A | Automation installation | New Project | Prakash, Kathiresan, Chandrasekar & Vignesh | 2020-03-06 | - | Installation completed and Automation is online - Attended
CL696 | 2020-03-06 | Namakkal 1 | A | Automation installation | New Project | Prakash, Kathiresan, Chandrasekar & Vignesh | 2020-03-06 | - | Installation completed and Automation is online - Attended
CL697 | 2020-03-06 | Ariyamangalam | D | D side Karur nozzle servicing & testing work | Preventive | Nepolean | 2020-03-06 | - | Nozzle tested and serviced - Testing : 3.16L - Attended
CL698 | 2020-03-07 | Aravakurichi | D | Dispenser working in Genset mode but not in EB mode | Breakdown | Kathiresan | 2020-03-08 | - | 63A changeover fuse replaced - Working fine - Rectified
CL699 | 2020-03-08 | Dindigul | D | Dispenser not working | Breakdown | Kathiresan | 2020-03-08 | - | Online and Offline UPS dust formation and switch not working properly - Cleaned - Working fine - Rectified
CL700 | 2020-03-11 | Perundurai | G | Commissioning and dispenser stamping | New Project | Prakash | 2020-03-11 | - | Commissioning & Stamping completed - Attended
CL701 | 2020-03-11 | Tirunelveli | D | Yenen dispenser not working and Batchen dispenser metering unit complaint | Breakdown | Nepolean | 2020-03-11 | - | Yenen dispenser R2 Relay changed and Batchen dispenser metering unit bearing and seal kit changed - Working fine - Rectified
CL702 | 2020-03-12 | Cantonment | G | Online UPS battery error | Breakdown | Prasath | 2020-03-12 | 9.45am to 10.20 am | Battery leg replaced - Working fine - Rectified
CL703 | 2020-03-12 | Tirunelveli | C | Dispenser Stamping | Certification | Kathiresan & Nepolean | 2020-03-12 | - | Stamping completed - Testing : 814.41 Ltrs - Attended
CL704 | 2020-03-12 | Hosur | D | A side dispenser hose leakage | Breakdown | Suresh | 2020-03-12 | - | Hose replaced - Working fine - Testing : 0.93 Ltrs Rectified
CL705 | 2020-03-12 | Ariyamangalam | D | D side nozzle leakage | Breakdown | Thirumalaisamy | 2020-03-12 | - | Nozzle replaced - Testing : 0.87 Ltrs - Rectified
CL706 | 2020-03-13 | Mettupalayam | D | Run mode not working | Breakdown | Prabu | 2020-03-13 | - | Dispenser input line adjusted - Working fine - Rectified
CL707 | 2020-03-13 | Mulanur | T | Tank installation | New Project | Thirumalaisamy | 2020-03-13 | - | Tank installation completed - Attended
CL708 | 2020-03-13 | Cantonment | D | C side nozzle lock complaint | Breakdown | Chandrasekar | 2020-03-13 | - | Spare nozzle replaced - Testing : 0.97 Ltrs - Rectified
CL709 | 2020-03-13 | Namakkal 1 | D | Dispenser one side not working | Breakdown | Chandrasekar | 2020-03-13 | - | Keypad replaced - Testing: 26.41 Ltrs - Rectified
CL710 | 2020-03-14 | Perundurai | A | Automation installation | New Project | Madhavan & Prabu | 2020-03-14 | - | Automation brought online with mobile billing - Rectified
CL711 | 2020-03-15 | Thuraiyur | T | EB room to Tank area air leakage due to pneumatic hose exploded | Breakdown | Kathiresan & Thirumalaisamy | 2020-03-15 | - | New pneumatic line 100 feet replaced - Rectified
CL712 | 2020-03-15 | Bodi | G | Pipeline hydro test | New Project | Gowtham | 2020-03-15 | - | Hydro test completed - Attended
CL713 | 2020-03-16 | Karur | C | Stamping work | Certification | Chandrasekar & Kathiresan | 2020-03-16 | - | Stamping completed - Testing : A side - 249.32 Ltrs - B side -251.14 Ltrs - Attended
CL714 | 2020-03-16 | Uthamasolapuram | T | Tank hydro test | New Project | Prabu | 2020-03-16 | - | Hydro test completed - Attended
CL715 | 2020-03-16 | Kodungaiyur | D | Motherboard replacement | Preventive | Thirumalaisamy | 2020-03-16 | - | Motherboard replaced - Working fine and under observation - Attended
CL716 | 2020-03-17 | Renganathan Bunk | D | Nozzle Leakage | Breakdown | Nepolean | 2020-03-17 | - | Nozzle Teeth 4 nos replaced - Rectified
CL717 | 2020-03-17 | Cantonment | D | C side nozzle servicing | Breakdown | Chandrasekar | 2020-03-17 | - | Nozzle serviced - Testing: 1.94 Ltrs - Rectified
CL718 | 2020-03-18 | Uthamasolapuram | T | CP Installation | New Project | Prabu | 2020-03-18 | - | CP installation and trench foundation mrakings completed - Attended
CL719 | 2020-03-18 | Attur | C | Dispenser stamping | Certification | Prabu | 2020-03-18 | - | Dispenser stamping completed - Testing A side 100.29lit; B side 125.83lit - Attended
CL720 | 2020-03-18 | Kodungaiyur | A | Automation installation | New Project | Madhavan | 2020-03-18 | - | Automation brought online with mobile billing - Rectified
CL721 | 2020-03-18 | Cantonment | D | D side nozzle complaint | Breakdown | Nepolean | 2020-03-18 | - | Service nozzle changed - Testing: 0.87 Ltrs - Rectified
CL722 | 2020-03-19 | Krishnagiri | A | Automation installation | New Project | Madhavan, Kathiresan & Vignesh | 2020-03-20 | - | Automation brought online with mobile billing - Rectified
CL723 | 2020-03-19 | Perundurai | G | Compressor not working | Breakdown | Prabu | 2020-03-18 | Half an hour | DOL starter wiring reconnected - Rectified
CL724 | 2020-03-19 | Ariyamangalam | D | D side nozzle servicing and testing | Preventive | Nepolean | 2020-03-19 | - | Nozzle serviced - Testing: 4.50 Ltrs - Rectified
CL725 | 2020-03-20 | Salem | C | Dispenser stamping | Certification | Prabu | 2020-03-20 | - | Dispenser stamping completed - Attended
CL726 | 2020-03-20 | Tharamangalam | A | Automation cable laying | New Project | Madhavan, Kathiresan & Vignesh | 2020-03-21 | - | Cable laid - Attended
CL727 | 2020-03-20 | Chengalpattu | D | Batchen dispenser solenoid complaint and switch problem | Breakdown | Suneel Sagar | 2020-03-20 | - | Solenoid assembly cleaned and switch replaced - Working fine - Rectified
CL728 | 2020-03-21 | Cantonment | D | C nozzle hard to lock | Breakdown | Gowtham | 2020-03-21 | - | Nozzle replaced - Testing - 0.97 Ltrs - Rectified
CL729 | 2020-03-21 | Uthamapalayam | G | Pipeline work | New Project | Chandrasekar | 2020-03-21 | - | Tank pipeline completed - Dispenser bed pipeline and Trench civil work is going on - Attended
CL730 | 2020-03-23 | Ariyamangalam | T | Compressor pressure switch complaint | Breakdown | Nepolean | 2020-03-23 | - | Serviced temporatily - Pressure switch has to be replaced after the lockdown period
CL731 | 2020-03-23 | Vadivelan Nagar | D | A side display card problem | Breakdown | Suneel Sagar | 2020-03-23 | - | Display card replaced - Rectified
CL732 | 2020-03-24 | Hosur | D | A side Nozzle problem | Breakdown | Suresh | 2020-03-24 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL733 | 2020-03-30 | Cantonment | A | Testing for automation- Roll back of the financial year | Preventive | Madhavan | 2020-03-30 | - | A nozzle testing - 6.6 ltrs D nozzle testing - 2.2 ltrs - Testing done
CL734 | 2020-03-30 | Ariyamangalam | A | Testing for automation- Roll back of the financial year | Preventive | Madhavan | 2020-03-31 | - | B nozzle testing - 4.4 ltrs D nozzle testing - 2.2 ltrs - Testing done
CL735 | 2020-03-30 | T.V.Kovil | A | Testing for automation- Roll back of the financial year | Preventive | Madhavan | 2020-03-31 | - | A nozzle testing - 4.4ltr C nozzle testing - 4.4ltrs - Testing done
CL736 | 2020-03-30 | Hosur | A | Testing for automation- Roll back of the financial year | Preventive | Madhavan | 2020-03-31 | - | B nozzle testing - 4.38ltrs - Testing done
CL737 | 2020-03-31 | T.V.Kovil | G | Oil dispenser air lock | Breakdown | Kathiresan | 2020-03-31 | - | Air lock released - Rectified
CL738 | 2020-04-04 | T.V.Kovil | A | Testing for automation application check up | New Project | Madhavan | 2020-04-04 | - | C nozzle testing - 1 Ltrs - Testing done
CL739 | 2020-04-05 | T.V.Kovil | A | Testing for automation application check up | New Project | Madhavan | 2020-04-05 | - | C nozzle : 5 liters D nozzle : 15 liter - Testing done
CL740 | 2020-04-12 | T.V.Kovil | A | Testing for automation mobile application upgrade | New Project | Madhavan | 2020-12-04 | - | A nozzle testing - 5.38 litres C nozzle testing - 21.74 litres D nozzle testing - 5 litres - Testing done
CL741 | 2020-05-06 | Ariyamangalam | G | Air machine mouth complaint | Breakdown | Nepolean | 2020-05-06 | - | Old mouth is replaced - Working fine - Rectified
CL742 | 2020-05-08 | Thuraiyur | D | Dispenser not working | Breakdown | Prabu | 2020-05-08 | - | Motherboard cable replaced nozzle lifting rod adjusted - Working fine - Testing - 19.58 Ltrs - Rectified
CL743 | 2020-05-09 | Yasodhai | G | Compressor air problem | Breakdown | Nepolean | 2020-05-09 | - | Tank 1 dispensing air line replaced newly - Working fine - Rectified
CL744 | 2020-05-09 | Thuraiyur | D | Dispensing Run Mode problem test mode working | Breakdown | Prabu | 2020-05-09 | - | R2 Relay changed - Working fine - Testing 3.36 Ltrs - Rectified
CL745 | 2020-05-09 | Erode | A | Automation - Mobile preset - application upgrade | New Project | Madhavan | 2020-05-09 | - | Upgraded - A nozzle testing - 18 ltrs - Attended
CL746 | 2020-05-16 | Ariyamangalam | G | Generator self motor complaint | Breakdown | Nepolean | 2020-05-16 | - | A serviced motor replaced - Working fine - Rectified
CL747 | 2020-05-18 | Bhavani | G | Generator Mode and UPS Noise complaint | Breakdown | Prabu | 2020-05-18 | - | UPS serviced - Rectified
CL748 | 2020-05-18 | Chengalpattu | D | Dispenser B side solenoid On/Off switch problem | Breakdown | Suneel Sagar | 2020-05-18 | - | Loose contact adjusted - Working fine - Rectified
CL749 | 2020-05-18 | Paramathivelur | A | Automation - Mobile preset - application upgrade | New Project | Madhavan | 2020-05-18 | - | Upgraded - Attended
CL750 | 2020-05-19 | T.V.Kovil | D | A side nozzle leakage | Breakdown | Kathiresan | 2020-05-19 | - | A side nozzle hammer teeth replaced and C side spare nozzle changed - Rectified
CL751 | 2020-05-19 | Velachery | G | Online UPS battery problem | Breakdown | Suneel Sagar | 2020-05-19 | - | 3 nos Battery and 1 Hooter replaced - Rectified
CL752 | 2020-05-20 | Kangeyam | D | Dispenser not working | Breakdown | Prabu & Thirumalaisamy | 2020-05-20 | - | Dispenser power cable adjusted and input supply connected with UPS - Rectified
CL753 | 2020-05-20 | Yasodhai | G | Air line complaint | Breakdown | Nepolean | 2020-05-20 | - | New air line laid - Working normally - Rectified
CL754 | 2020-05-20 | Vellakovil | G | Air Leakage | Breakdown | Prabu & Thirumalaisamy | 2020-05-20 | - | Dispensing and decanting side unloading coil replaced - Working fine - Rectified
CL755 | 2020-05-20 | Ariyamangalam | D | Error 23 occurred on C side | Breakdown | Nepolean | 2020-05-20 | - | Reset done - Rectified
CL756 | 2020-05-21 | Thuraiyur | C | Stamping work | Certification | Kathiresan | 2020-05-21 | - | Stamping done - Attended
CL757 | 2020-05-21 | Dindigul | R | Control Panel MOL relay problem | Preventive | Nepolean | 2020-05-21 | - | Conductor and relay replaced - Working fine - Rectified
CL758 | 2020-05-21 | Attur | T | Decanting pump leakage | Breakdown | Prakash & Kathiresan | 2020-05-23 | - | Decanting pump replaced and Rov serviced - Working fine - Rectified
CL759 | 2020-05-22 | Pudukkottai | d | Dispenser B side display problem | Breakdown | Chandrasekar | 2020-05-22 | - | Display card replaced - Rectified
CL760 | 2020-05-22 | Virudhunagar | C | Stamping work | Certification | Venkatesh | 2020-05-22 | - | Stamping done - Attended
CL761 | 2020-05-22 | Kangeyam | D | Dispenser and its display not working | Breakdown | Prabu | 2020-05-22 | - | Reset done - Rectified
CL762 | 2020-05-23 | Erode | T | ATG not working | Breakdown | Prabu | 2020-05-23 | - | 3V battery 1 no replaced and reprogramming - Rectified
CL763 | 2020-05-24 | Namakkal 1 | A | Automation - Mobile preset - application upgrade | New Project | Madhavan & Thirumalaisamy | 2020-05-24 | - | Upgraded - Attended
CL764 | 2020-05-25 | Perundurai | A | Automation - Mobile preset - application upgrade | New Project | Madhavan & Prabu | 2020-05-25 | - | Upgraded and RS485 to USB converter changed - Attended
CL765 | 2020-05-26 | Bhavani | D | One side nozzle leakage | Breakdown | Prabu | 2020-05-26 | - | A side nozzle serviced and b side nozzle replaced - Rectified
CL766 | 2020-05-26 | Bhavani | A | Automation - Mobile preset - application upgrade | New Project | Madhavan & Prabu | 2020-05-26 | - | Upgraded - Attended
CL767 | 2020-05-27 | Aravakurichi | A | Automation - Mobile preset - application upgrade | New Project | Madhavan & Thirumalaisamy | 2020-05-27 | - | Upgraded - Attended
CL768 | 2020-05-28 | Palladam | D | Dispenser not working | Breakdown | Prabu | 2020-05-28 | - | Dispenser side air hose replaced - Nozzles serviced - Rectified
CL769 | 2020-05-29 | Uthamapalayam | G | Welding work | New Project | Gowtham | 2020-06-02 | - | Welding work completed - Rectified
CL770 | 2020-05-29 | Cantonment | D | C nozzle leakage | Breakdown | Chandrasekar | 2020-05-29 | - | Serviced and working fine - Testing 0.97 Ltrs - Rectified
CL771 | 2020-05-29 | Cantonment | G | Oil pump leakage | Breakdown | Prakash | 2020-05-30 | 18 hours | New pump changed - Oil testing :6.100 Ltrs - Rectified
CL772 | 2020-05-30 | Rasipuram | A | Automation - Mobile preset - application upgrade | New Project | Madhavan & Prabu | 2020-05-30 | - | Upgraded - Attended
CL773 | 2020-05-30 | Vadivelan Nagar | D | B and C side keypad not working | Breakdown | Suneel sagar | 2021-05-30 | - | Keypad replaced - Rectified
CL774 | 2020-05-30 | Rasipuram | G | Unloading MCB not working | Breakdown | Prabu | 2020-05-30 | - | New MCB replaced - Working fine - Rectified
CL775 | 2020-05-31 | Vellakovil | D | Cutoff is improper | Breakdown | Prabu | 2020-06-02 | - | High flow low flow valve cleaned - Nozzle serviced - Metering unit filter cleaned - Testing - 8.85 Ltrs - Rectified
CL776 | 2020-05-31 | Krishnagiri | A | Automation - Mobile preset - application upgrade | New Project | Madhavan | 2020-05-31 | - | Upgraded - Attended
CL777 | 2020-06-02 | Bodi | G | Site Visit | New Project | Prakash & Kathiresan | 2020-06-02 | - | Site visit completed - Attended
CL778 | 2020-06-02 | Uthamapalayam | G | Site Visit | New Project | Prakash & Kathiresan | 2020-06-02 | - | Site visit completed - Attended
CL779 | 2020-06-02 | Chengalpattu | C | Stamping work | Certification | Suneel Sagar | 2020-06-02 | - | Stamping Completed - Attended
CL780 | 2020-06-03 | Cantonment | C | Calibration | Certification | Nepolean | 2020-06-03 | - | Calibration completed - Testing : 1716.36 - Attended
CL781 | 2020-06-04 | Kodungaiyur | D | Nozzle not working properly | Breakdown | Suneel Sagar | 2020-06-04 | - | Unloading solenoid, Nozzle teeth replaced and PM done - Rectified
CL782 | 2020-06-04 | Avinashi | C | Stamping work | Certification | Nepolean | 2020-06-04 | - | Stamping Completed - Attended
CL783 | 2020-06-04 | Velachery | D | Fill point indicator communication error | Breakdown | Suneel Sagar | 2020-06-04 | - | Repaired 9Pin DB connector - Rectified
CL784 | 2020-06-06 | Kodumudi | D | Dispenser error | Breakdown | Prabu | 2020-06-06 | - | Dispenser cables adjusted and liquid line flow adjusted - Rectified
CL785 | 2020-06-06 | Cantonment | C | Stamping work | Certification | Nepolean | 2020-06-06 | - | Stamping Completed - Attended
CL786 | 2020-06-08 | Mulanur | T | Tank hydro test | New Project | Thirumalaisamy | 2020-06-08 | - | Hydro test completed - Attended
CL787 | 2020-06-09 | Thuraiyur | T | Control panel MNx 16 contactor and MOL relay problem - Line directed | Preventive | Nepolean | 2020-06-10 | - | MNx 16 contactor and MOL relay replaced - Working fine - Rectified
CL788 | 2020-06-10 | Bodi | G | Electrical work | New Project | Gowtham | 2020-06-10 | - | Bodi site electrical work partially completed due to civil work pending. Control panel and tank area wiring termination completed.
CL789 | 2020-06-12 | Tharamangalam | G | N2 Test | New Project | Prabu | 2020-06-12 | - | Nitrogen test completed - Attended
CL790 | 2020-06-12 | Cantonment | D | C side nozzle complaint | Breakdown | Chandrasekar | 2020-06-12 | - | New Nozzle replaced - Working fine - Testing 0.97Ltrs - Rectified
CL791 | 2020-06-13 | Uthamasolapuram | G | Welding & Mechanical work | New Project | Thirumalaisamy | 2020-06-20 | - | Welding mechanical and hydro test completed - Attended
CL792 | 2020-06-15 | Udumalpet | D | Dispenser hose leakage & ATG sound problem | Breakdown | Prabu | 2020-06-15 |  | Dispenser hose replaced - ATG sound acknowledged - Rectified
CL793 | 2020-06-15 | Pudukkottai | G | N2 machine installation | New Project | Chandrasekar & Kathiresan | 2020-06-15 | - | N2 machine installation and genset silencer alteration completed - Rectified
CL794 | 2020-06-17 | Vellakovil | D | Dispenser one side problem & Unloading solenoid coil air leakage | Breakdown | Prabu | 2020-06-17 | - | Metering unit filter block, High flow & Low flow coil cleaned - Solenoid coil 3 nos replaced and unloading liquid hose 1 no replaced - Rectified
CL795 | 2020-06-17 | Ariyamangalam | D | D side nozzle teeth problem | Breakdown | Nepolean | 2020-06-17 | - | Nozzle teeth 4 nos replaced - Working fine - Testing 3.92 Ltrs - Rectified
CL796 | 2020-06-17 | T.V.Kovil | G | Imax modem complaint | Breakdown | Sathish | 2020-06-17 | - | D link modem replaced - Rectified
CL797 | 2020-06-18 | Kumbakonam | T | Tank installation | New Project | Nepolean & Kathiresan | 2020-06-18 | - | Tank installation completed - Attended
CL798 | 2020-06-20 | Bodi | G | Electrical cable termination, earth flat termination, Online UPS & servo stabilizer connection | New Project | Gowtham | 2020-06-20 | - | Cable termination done - Online UPS and Servo Stabilizer connection done - Attended
CL799 | 2020-06-20 | Uthamapalayam | G | Electrical cable termination, earth flat termination, Online UPS & servo stabilizer connection | New Project | Gowtham | 2020-06-20 | - | Cable termination done - Online UPS and Servo Stabilizer connection done - Attended
CL800 | 2020-06-21 | Attur | T | Unloading pump bypass valve pipeline alteration work | Breakdown | Prakash | 2020-06-21 | - | Alteration work completed - Attended
CL801 | 2020-06-23 | T.V.Kovil | G | N2 machine problem | Breakdown | Kathiresan | 23-06-2020 | - | Solenoid coil and air sensor serviced - Working fine - Rectified
CL802 | 2020-06-23 | Cantonment | D | Dispenser offline UPS battery problem | Preventive | Chandrasekar | 23-06-2020 | - | Offline UPS battery newly changed - Attended
CL803 | 2020-06-24 | Dharmapuri | G | Site marking | New Project | Prakash & Kathiresan | 24-06-2020 | - | testing & Reprogramming completed - Attended
CL804 | 2020-06-24 | Ariyamangalam | G | Compressor pressure switch complaint | Breakdown | Nepolean | 2020-08-12 | - | New compressor pressure switch changed - Working fine - Rectified
CL805 | 2020-06-30 | T.V.Kovil | D | A side nozzle complaint | Breakdown | Sathish | 2020-06-30 | - | Serviced nozzle replaced - Testing - 3.79Ltrs - Rectified
CL806 | 2020-07-01 | Aravakurichi | T | Unloading liquid and vapour ball valve leakage | Breakdown | Thirumalaisamy | 2020-07-01 | - | Leakage arrested by applying teflon and tightened - Rectified
CL807 | 2020-07-06 | Krishnagiri | D | Keypad not working | Breakdown | Nepolean | 2020-07-06 | - | Reset done - Rectified
CL808 | 2020-07-07 | Ariyamangalam | G | Compressor oil changing | Preventive | Nepolean | 2020-07-07 | - | Oil changed - Attended
CL809 | 2020-07-08 | Thuraiyur | T | By pass valve pipe line welding alterations | Preventive | Chandrasekar & Kathiresan | 2020-07-08 | - | Welding alteration work completed - Attended
CL810 | 2020-07-08 | Perundurai | T | ROV leakage and unloading training | Breakdown | Prabu | 2020-07-08 | - | ROV adjusted and leakage arrested and unloading training completed - Rectified
CL811 | 2020-07-09 | Dindigul | T | By pass valve pipe line welding alterations | Preventive | Chandrasekar & Kathiresan | 2020-07-09 | - | Welding alteration work completed - Attended
CL812 | 2020-07-10 | Karur | D | Nozzle complaint | Breakdown | Thirumalaisamy | 2020-07-10 | - | A side service nozzle changed and B side nozzle teeth changed - Emergency push button needs to be changed - Testing A side - 0.82 Ltrs - Rectified
CL813 | 2020-07-10 | Bhavani | T | Unloading liquid hose leakage and compressor running continuously | Breakdown | Prabu | 2020-07-10 | - | Hose adapter refitted applying teflon to arrest leakage - EB room to tank area air hose replaced - Rectified
CL814 | 2020-07-10 | Tirunelveli | T | By pass valve pipe line welding alterations | Preventive | Chandrasekar & Kathiresan | 2020-07-10 | - | Welding alteration work completed - Attended
CL815 | 2020-07-11 | Thuraiyur | D | Dispenser run mode not working | Breakdown | Nepolean | 2020-07-11 | - | R1 relay changed - Run mode working - Kept under observation - Rectified
CL816 | 2020-07-13 | Namakkal 2 | T | Tank installation | New Project | Chandrasekar & Kathiresan | 2020-07-13 | - | Tank installation and concrete work completed - Attended
CL817 | 2020-07-14 | Thuraiyur | R | Relay fitting work | Breakdown | Nepolean | 2020-07-14 | - | R1 and R2 relay changed - Working fine - Rectified
CL818 | 2020-07-14 | Dharmapuri | T | Tank installation | New Project | Chandrasekar & Kathiresan | 2020-07-14 | - | Tank installation and concrete work completed - Attended
CL819 | 2020-07-15 | Sulur | T | Tank area air leakage & EB - Earth to neutral problem | Breakdown | Prabu | 2020-07-15 | - | EB room to tank area air hose replaced - EB Chagned to 3 phase - Working fine - Rectified
CL820 | 2020-07-15 | Ariyamangalam | D | B side nozzle complaint | Breakdown | Nepolean | 2020-07-15 | - | Service nozzle replaced - Working fine - Testing - 1.26 Ltrs - Rectified
CL821 | 2020-07-17 | Ariyamangalam | D | D side nozzle servicing and testing | Preventive | Nepolean | 2020-07-17 | - | Nozzle serviced and tested - Testing : 3.30 Ltrs - Attended
CL822 | 2020-07-18 | T.V.Kovil | D | Dispenser error 11 and error 23 | Breakdown | Kathiresan | 2020-07-18 | - | Wire connection adjusted - Working fine - Rectified
CL823 | 2020-07-18 | T.V.Kovil | D | B side nozzle leakage | Breakdown | Sathish | 2020-07-18 | - | Nozzle teeth changed - Working fine - Testing: 2.21 Ltrs - Rectified
CL824 | 2020-07-18 | Uthamasolapuram | G | Electrical cable laying work | New Project | Thirumalaisamy | 2020-07-20 | - | Electrical cable laying completed - Pneumatic hose laying - Tank area body earthing completed - Earth flat welding completed - Attended
CL825 | 2020-07-20 | Ariyamangalam | D | B side nozzle lock spring problem | Breakdown | Nepolean | 2020-07-20 | - | Nozzle lock spring changed - B side Testing : 1.23 Ltrs - Rectified
CL826 | 2020-07-22 | Namakkal 2 | T | Tank hydro test | New Project | Thirumalaisamy | 2020-07-22 | - | Hydro test completed - Attended
CL827 | 2020-07-22 | Dharmapuri | T | Tank hydro test | New Project | Thirumalaisamy | 2020-07-22 | - | Hydro test completed - Attended
CL828 | 2020-07-23 | Aravakurichi | C | Stamping work | Certification | Nepolean & Gowtham | 2020-07-23 | - | Stamping work completed - Attended
CL829 | 2020-07-23 | Vellakovil | C | Stamping work | Certification | Nepolean & Gowtham | 2020-07-23 | - | Stamping work completed - Attended
CL830 | 2020-07-23 | Kangeyam | C | Stamping work | Certification | Nepolean & Gowtham | 2020-07-23 | - | Stamping work completed - Attended
CL831 | 2020-07-23 | Dharapuram | C | Stamping work | Certification | Nepolean & Gowtham | 2020-07-23 | - | Stamping work completed - Attended
CL832 | 2020-07-25 | Kumbakonam | T | Tank hydro test | New Project | Chandrasekar & Kathiresan | 2020-07-25 | - | Hydro test completed - Attended
CL833 | 2020-07-28 | Thuraiyur | R | PLC Relay continuous beeping | Breakdown | Nepolean | 2020-07-28 | - | EB pole 3 phase line wire damaged- Wire corrected - Rectified
CL834 | 2020-07-29 | Namakkal 2 | T | CP Installation | New Project | Nepolean & Gowtham | 2020-07-30 | - | CP installation completed - Range: 1.38 DCV - Attended
CL835 | 2020-07-29 | Bodi | C | Third party inspection | New Project | Nepolean & Gowtham | 2020-07-29 | - | Inspection completed - Attended
CL836 | 2020-07-29 | Uthamapalayam | C | Third party inspection | New Project | Nepolean & Gowtham | 2020-07-29 | - | Inspection completed - Attended
CL837 | 2020-07-30 | Dharmapuri | T | CP Installation | New Project | Nepolean | 2020-07-30 | - | CP installation completed - Range: 1.52 DCV - Attended
CL838 | 2020-07-30 | Namakkal 1 | G | Air compressor LPG line fitting complaint | Breakdown | Nepolean | 2020-07-30 | - | Air compressor LPG line fitting 1 no changed - Rectified
CL839 | 2020-08-01 | Sulur | D | Dispenser automatic cutoff | Breakdown | Prabu | 2020-08-01 | - | UPS Line corrected - Rectified
CL840 | 2020-08-01 | Palladam | D | Dispenser breakaway leakage | Breakdown | Prabu | 2020-08-01 | - | New breakaway changed - Rectified
CL841 | 2020-08-03 | Virudhachalam | G | Rule 33 data collection and Earth installation | New Project | Chandrasekar & Kathiresan | 2020-08-03 | - | Rule 33 data collected - 2 nos earth installed - attended
CL842 | 2020-08-04 | Manapparai | T | Dispenser pump spider problem | Breakdown | Chandrasekar | 2020-08-04 | - | New spider replaced - PMR completed - Rectified
CL843 | 2020-08-04 | Krishnagiri | T | Decanting process not working | Breakdown | Nepolean | 2020-08-04 | - | EB line phase corrected - Rectified
CL844 | 2020-08-04 | T.V.Kovil | D | Batchen dispenser B side nozzle leakage | Breakdown | Kathiresan | 2020-08-04 | - | Spare nozzle replaced - Testing : 1.18 Ltrs - Rectified
CL845 | 2020-08-05 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2020-08-05 | - | Nozzle serviced and tested - Testing: 3.48 Ltrs - Attended
CL846 | 2020-08-06 | Virudhachalam | T | Hydro test and welding | New Project | Chandrasekar | 2020-08-06 | - | Hydro test and welding completed - Pressure - 48kg/sq.cm - Attended
CL847 | 2020-08-07 | Vadivelan Nagar | G | Offline UPS installation | Preventive | Suneel sagar | 2020-08-07 | - | UPS installed and both dispensers connected - Under observation - Attended
CL848 | 2020-08-10 | Kumbakonam | G | Trench, Dispenser & Decanting pump bed, Genset bed marking | New Project | Krishna bhalaji | 2020-08-10 | - | Markings completed - Attended
CL849 | 2020-08-12 | Kumbakonam | T | CP Installation | New Project | Nepolean & Gowtham | 2020-08-12 | - | CP Installation completed - Attended
CL850 | 2020-08-12 | Namakkal 2 | G | Dispenser, trench, decanding pump and dispensing pump bed marking | New Project | Prakash | 2020-08-12 | - | Site marking completed - Attended
CL851 | 2020-08-12 | Dharmapuri | G | Dispenser, trench, decanding pump and dispensing pump bed marking | New Project | Prakash | 2020-08-12 | - | Site marking completed - Attended
CL852 | 2020-08-12 | Vadivelan Nagar | T | Dispensing pump spider complaint | Breakdown | Suneel Sagar | 2020-08-12 | - | Spider replaced - Rectified
CL853 | 2020-08-13 | Avinashi | C | Rule 18 work | Certification | Chandrasekar, Kathiresan & Gowtham | 2020-08-13 | - | Rule 18 work completed - Tank 2 connected with HLA - Attended
CL854 | 2020-08-13 | Mettupalayam | C | Rule 18 work and unloading liquid hose changing | Certification | Chandrasekar, Kathiresan & Gowtham | 2020-08-13 | - | Rule 18 work completed - Unloading liquid hose changed - Attended
CL855 | 2020-08-14 | Saravanampatty | C | Rule 18 work & Earth regeneration | Certification | Chandrasekar | 2020-08-14 | - | Rule 18 work completed & Earth Regenerated - Attended
CL856 | 2020-08-14 | Mettupalayam | R | Control panel soft starter installation & Earth regeneration | Preventive | Chandrasekar | 2020-08-14 | - | Control panel soft starter installed and air pressure switch connected & Earth Regenerated - Rectified
CL857 | 2020-08-14 | Sulur | C | Rule 18 work & Earth regeneration | Certification | Chandrasekar | 2020-08-14 | - | Rule 18 work completed & Earth Regenerated - Attended
CL858 | 2020-08-15 | Palladam | C | Rule 18 work & Earth regeneration | Certification | Chandrasekar | 2020-08-15 | - | Rule 18 work completed & Earth Regenerated - Attended
CL859 | 2020-08-15 | Udumalpet | C | Rule 18 work | Certification | Chandrasekar | 2020-08-15 | - | Rule 18 Work completed - Attended
CL860 | 2020-08-17 | Mulanur | T | Tank hydro test & Pipe welding | New Project | Thirumalaisamy | 2020-08-15 | - | Hydro test and welding completed - Pressure - 48kg/sq.cm - Attended
CL861 | 2020-08-17 | Ariyamangalam | D | B side nozzle leakage | Breakdown | Nepolean | 2020-08-17 | - | Serviced nozzle replaced - Working fine - Testing: 2.04 Ltrs - Rectified
CL862 | 2020-08-18 | Krishnagiri | D | Dispensing mode complaint | Breakdown | Nepolean | 2020-08-18 | - | Reboot done - Working fine - Rectified
CL863 | 2020-08-19 | Mulanur | C | Rule 33 data collection | New Project | Thirumalaisamy | 2020-08-19 | - | Data collected - Attended
CL864 | 2020-08-19 | Cantonment | G | Air machine nozzle complaint | Breakdown | Chandrasekar | 2020-08-19 | - | Air machine nozzle replaced - Rectified
CL865 | 2020-08-20 | T.V.Kovil | D | Dispenser C side and D side nozzle complaint | Breakdown | Kathiresan | 2020-08-20 | - | Nozzle teeth both side replaced - Working fine - Rectified
CL866 | 2020-08-22 | Bodi | G | Site Visit | New Project | Prakash & Chandrasekar | 2020-08-22 | - | Site visit completed - Attended
CL867 | 2020-08-22 | Uthamapalayam | G | Site Visit | New Project | Prakash & Chandrasekar | 2020-08-22 | - | Site visit completed - Attended
CL868 | 2020-08-25 | Cantonment | A | Credit sale activation and testing | New Project | Madhavan | 2020-08-25 | - | Credit sale activated and tested and integrated with shift closing - Attended
CL869 | 2020-08-25 | T.V.Kovil | C | Stamping work | Certification | Nepolean | 2020-08-25 | - | Stamping Completed - Attended
CL870 | 2020-08-27 | Tharamangalam | G | Site commissioning, Automation Installation & Pump opening | New Project | Prakash, Chandrasekar & Madhavan | 2020-08-27 | - | Commissioned, Pump opened and sales started with Automation mobile billing - Completed
CL871 | 2020-08-27 | Dharmapuri | G | Trench pit, dispenser, decanting pump bed and culvert chamber marking | New Project | Krishna bhalaji | 2020-08-27 | - | Markings completed - Attended
CL872 | 2020-08-27 | Tharamangalam | C | Stamping work | New Project | Krishna bhalaji | 2020-08-27 | - | Stamping Completed - Attended
CL873 | 2020-08-28 | Tharamangalam | G | On job training about 1) Customer service 2) Safety precautions while fueling 3) About LPG 4) Usage of safety equipments 5) How to prevent and handle emergency situations | Preventive | Krishna bhalaji | 2020-08-28 | - | Training completed - Attended
CL874 | 2020-08-28 | Velachery | G | Preventive Maintenance | Preventive | Suneel Sagar | 2020-08-28 | - | Preventive Maintenance completed
CL875 | 2020-08-28 | Vadivelan Nagar | G | Preventive Maintenance | Preventive | Suneel Sagar | 2020-08-28 | - | Preventive Maintenance completed
CL876 | 2020-08-28 | Tharamangalam | G | Genset commissioning & Testing | New Project | Prakash | 2020-08-28 | - | Commissioned and tested - Attended
CL877 | 2020-08-30 | T.V.Kovil | A | Credit sale activation and testing | New Project | Madhavan | 2020-08-30 | - | Credit sale activated and tested and integrated with shift closing - Attended
CL878 | 2020-09-01 | Udumalpet | D | Dispenser A side metering unit leakage | Breakdown | Prabu | 2020-09-01 | - | Bearing and Seal kit changed - Metering unit small LPG Hose replaced - Rectified
CL879 | 2020-09-01 | Ariyamangalam | C | Calibration | Certification | Nepolean | 2020-09-01 | - | Calibration done - Attended
CL880 | 2020-09-02 | Bodi | A | Automation cable laying & Camera connection | New Project | Prasath, Chandrasekar & Gowtham | 2020-09-03 | - | Cable laying, camera connection & Yard light fitting completed
CL881 | 2020-09-02 | Uthamapalayam | A | Automation cable laying & Camera connection | New Project | Prasath, Chandrasekar & Gowtham | 2020-09-03 | - | Cable laying, camera connection & Yard light fitting completed
CL882 | 2020-09-02 | Ariyamangalam | G | Genset self motor problem | Breakdown | Nepolean | 2020-09-02 | - | Self motor changed - Rectified
CL883 | 2020-09-03 | Ariyamangalam | C | Stamping work | Certification | Nepolean | 2020-09-03 | - | Stamping Completed - Attended
CL884 | 2020-09-04 | Virudhachalam | G | UPVC measurement & Electrical work | New Project | Prakash & Kathiresan | 2020-09-04 | - | UPVC Measurement done and electrical work instructions given - Attended
CL885 | 2020-09-04 | Dharmapuri | T | Tank cleaning & Mechanical work | New Project | Thirumalaisamy | 2020-09-04 | - | Tank cleaning completed and mechanical work going on - Attended
CL886 | 2020-09-04 | Vadivelan Nagar | T | Dispensing liquid ROV ball valve stem broken due to ball valve stuck up | Breakdown | Suneel Sagar | 2020-09-07 | - | Dispensing liquid ROV Ballvalve replaced - Working fine - Rectified
CL887 | 2020-09-05 | Thuraiyur | R | PLC problem | Breakdown | Nepolean | 2020-09-05 | - | PLC directed - Working temporarily - Under observation - Rectified
CL888 | 2020-09-06 | Attur | D | Metering unit leakage | Breakdown | Prakash & Kathiresan | 2020-09-06 | - | A side - Metering unit - Bearing and Seal kit replaced - Rectified
CL889 | 2020-09-07 | Ariyamangalam | D | A side nozzle leakage | Breakdown | Nepolean | 2020-09-07 | - | OPW Service nozzle replaced - Working fine - Testing : 1.12 Ltrs - Rectified
CL890 | 2020-09-08 | Saravanampatty | C | Stamping work | Certification | Chandrasekar & Kathiresan | 2020-09-08 | - | Stamping Completed - Attended
CL891 | 2020-09-08 | Sulur | C | Stamping work | Certification | Chandrasekar & Kathiresan | 2020-09-08 | - | Stamping Completed - Attended
CL892 | 2020-09-08 | Kangeyam | D | Dispenser not working | Breakdown | Prabu | 2020-09-08 | 5 Hours | Parameters changed - Working fine - Rectified
CL893 | 2020-09-08 | Rasipuram | T | Dispensing motor love jaw coupling complaint | Breakdown | Chandrasekar & Kathiresan | 2020-09-09 | - | Spider replaced - Rule 18 Work completed - Earth regenerated - Rectified
CL894 | 2020-09-08 | Cantonment | R | Offline UPS improper working | Breakdown | Gowtham & Chandrasekar | 2020-09-08 | - | New offline UPS replaced - Working fine - Rectified
CL895 | 2020-09-08 | Kodungaiyur | G | Preventive Maintenance | Preventive | Suneel sagar | 2020-09-08 | - | Preventive Maintenance completed
CL896 | 2020-09-09 | Namakkal 1 | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-09 | - | Rule 18 Work completed - Earth regenerated - Attended
CL897 | 2020-09-09 | Paramathivelur | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-09 | - | Rule 18 Work completed - Earth regenerated - Attended
CL898 | 2020-09-09 | T.V.Kovil | D | A side nozzle leakage | Breakdown | Sathish | 2020-09-09 | - | New nozzle changed - Testing - 2.37 Ltrs - Rectified
CL899 | 2020-09-09 | Kodumudi | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-09 | - | Rule 18 work completed - ACME Adapter replaced - Attended
CL900 | 2020-09-10 | Erode | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-10 | - | Rule 18 Work completed - Attended
CL901 | 2020-09-10 | Perundurai | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-10 | - | Rule 18 Work completed - Attended
CL902 | 2020-09-10 | Bhavani | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-10 | - | Rule 18 Work completed - Attended
CL903 | 2020-09-11 | Tirunelveli | D | Dispenser not working | Breakdown | Nepolean | 2020-09-12 | - | Dispenser fuse replaced - Control Panel Relay replaced - Batchen dispenser B side oil seal kit and bearing changed - Pneumatic line changed from panel to tank - Rectified
CL904 | 2020-09-11 | Kangeyam | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-11 | - | Rule 18 Work completed - Earth regenerated - Dispensing spider changed - Attended
CL905 | 2020-09-12 | Dharapuram | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-12 | - | Rule 18 Work completed - Earth regenerated - Dispensing spider changed - Attended
CL906 | 2020-09-15 | Bodi | G | Canopy cable changing work | New Project | Chandrasekar & Kathiresan | 2020-09-15 | - | Canopy cable changed - Rectified
CL907 | 2020-09-15 | Uthamapalayam | G | Canopy cable changing work | New Project | Chandrasekar & Kathiresan | 2020-09-15 | - | Canopy cable changed - Rectified
CL908 | 2020-09-15 | Namakkal 2 | G | Site visit | New Project | Prakash | 2020-09-15 | - | Site visit completed - Attended
CL909 | 2020-09-15 | Dharmapuri | T | Hydro test and welding | New Project | Thirumalaisamy | 2020-09-15 | - | Hydro test & Pipe welding completed - Attended
CL910 | 2020-09-15 | Theni | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-15 | - | Rule 18 work completed - Power cord changed due to short circuit - Testing 58.94 Ltrs - Earth Regenerated - Attended
CL911 | 2020-09-15 | Vadivelan Nagar | R | Surge protector failed due to transformer short circuit | Breakdown | Suneel sagar | 2020-09-17 | - | Surge Protector element replaced - Rectified
CL912 | 2020-09-16 | Tirunelveli | C | Rule 18 Work | Certification | Chandrasekar | 2020-09-16 | - | Rule 18 work completed - Earth regenerated - SRV needs to be replaced - Attended
CL913 | 2020-09-16 | Vellakovil | D | Batchen dispenser slow delivery due to metering unit filter block | Breakdown | Prabu | 2020-09-16 | - | Metering unit filter replaced - Working fine - Rectified
CL914 | 2020-09-16 | Krishnagiri | C | Stamping work | Certification | Nepolean | 2020-09-16 | - | Stamping Completed - Attended
CL915 | 2020-09-17 | Virudhunagar | C | Rule 18 work | Certification | Chandrasekar | 2020-09-17 | - | Rule 18 Work completed - Earth Regenerated - Pneumatic lines replaced - Attended
CL916 | 2020-09-18 | Hosur | C | Stamping work | Certification | Nepolean | 2020-09-18 | - | Stamping Completed - Attended
CL917 | 2020-09-18 | Pudukkottai | C | Rule 18 work | Certification | Chandrasekar | 2020-09-18 | - | Rule 18 Work completed - Attended
CL918 | 2020-09-19 | Dharmapuri | G | Mechanical, Welding & Electrical cable laying | New Project | Thirumalaisamy | 2020-09-19 | - | Mechanical work completed - GI patta welding completed - Electrical cable laying completed - Attended
CL919 | 2020-09-19 | Theni | D | B side not working and A side low flow & slow delivery | Breakdown | Nepolean | 2020-09-21 | - | B side Metering unit bearing and oil seal kit changed - Solenoid coil cleaned - A side solenoid coil cleaned - Rectified
CL920 | 2020-09-21 | Ariyamangalam | D | A side Nozzle problem | Breakdown | Nepolean | 2020-09-21 | - | A side service nozzle changed - Testing 1.14 Ltrs - Rectified
CL921 | 2020-09-22 | Cantonment | C | Rule 18 work | Certification | Nepolean | 2020-09-22 | - | Rule 18 completed - Earth regenerated - Attended
CL922 | 2020-09-22 | Ariyamangalam | C | Rule 18 work | Certification | Nepolean | 2020-09-22 | - | Rule 18 completed - Earth regenerated - Attended
CL923 | 2020-09-22 | T.V.Kovil | C | Rule 18 work | Certification | Nepolean | 2020-09-22 | - | Rule 18 completed - Earth regenerated - Attended
CL924 | 2020-09-23 | Saravanampatty | D | Error 34 occurred | Breakdown | Prabu | 2020-09-23 | - | Dispenser parameter changed - Working fine - Rectified
CL925 | 2020-09-23 | T.V.Kovil | A | Mobile billing stopped due to network issue | Breakdown | Madhavan | 2020-09-27 | - | Network channel adjusted - Resolved and kept under observation - Rectified
CL926 | 2020-09-24 | Thuraiyur | D | Dispenser power cord problem | Breakdown | Nepolean | 2020-09-24 | - | Power cord reconnected - Under observation - Rectified
CL927 | 2020-09-24 | Mulanur | C | Third party inspection | New Project | Thirumalaisamy | 2020-09-24 | - | Third party inspection for Rule 33 and other certificates completed - Attended
CL928 | 2020-09-25 | Cantonment | D | B & D side nozzle hose sleeve changing | Preventive | Ravichandran M | 2020-09-25 | - | Hose sleeve changed - Testing B Side: 1.15 Ltrs; D Side: 0.91 Ltrs - Attended
CL929 | 2020-09-27 | Velachery | G | Preventive Maintenance | Preventive | Suneel sagar | 2020-09-27 | - | Preventive Maintenance completed
CL930 | 2020-09-27 | T.V.Kovil | D | B side Nozzle broken | Breakdown | Kathiresan | 2020-09-27 | - | Spare nozzle replaced - Testing : 3.58 Ltrs - Rectified
CL931 | 2020-09-28 | Avinashi | G | Additional dispenser installation | New Project | Prakash, Prabu, Chandrasekar & Kathiresan | 2020-10-01 | - | Additional dispenser installed and testing & Stamping completed - Attended
CL932 | 2020-09-28 | Thuraiyur | D | Dispenser power cord problem | Breakdown | Prakash & Nepolean | 2020-09-28 | - | Power cord replaced - Working fine - Under Observation - Rectified
CL933 | 2020-09-28 | Palladam | D | Dispenser slow delivery due to excess flow valve broken | Breakdown | Prabu & Chandrasekar | 2020-10-02 | - | Excess flow valve replaced - Cp junction box replaced - Rectified
CL934 | 2020-09-30 | T.V.Kovil | A | Pump going offline for Automation Maintenance | Preventive | Madhavan | 2020-09-30 | - | Maintenance done - Back online - Attended
CL935 | 2020-10-01 | T.V.Kovil | D | B side OPW nozzle lock problem | Breakdown | Nepolean | 2020-10-01 | - | New lock replaced - Working fine - Rectified
CL936 | 2020-10-01 | Palayam | T | Tank installation | New Project | Thirumalaisamy | 2020-10-01 | - | Tank installation completed - Attended
CL937 | 2020-10-01 | Aravakurichi | G | Online UPS connection | Preventive | Thirumalaisamy | 2020-10-01 | - | Connection done - Attended
CL938 | 2020-10-02 | Theni | T | Dispensing motor contactor problem | Breakdown | Nepolean | 2020-10-03 | - | Contactor replaced - B side metering unit and oil seal kit changed - B side new Breakaway coupling replaced - working fine - Rectified
CL939 | 2020-10-02 | Bhavani | T | Unloading problem | Breakdown | Prabu | 2020-10-02 | - | Unloading contactor LT MNX12 replaced- Unloading completed - Rectified
CL940 | 2020-10-03 | Tirunelveli | D | Batchen dispenser Error 39 and SRV fitting | Breakdown | Nepolean | 2020-10-04 | - | Software updated - SRV fitting completed - Working fine - Rectified
CL941 | 2020-10-03 | Aravakurichi | T | Dispensing motor continuous running | Breakdown | Thirumalaisamy | 2020-10-03 | - | Contactor line changed to W2 from W1 and UPS line seperated from Control panel - Working fine - Keeping under observation
CL942 | 2020-10-05 | Hosur | D | B side nozzle teeth problem | Breakdown | Suresh | 2020-10-05 | - | Nozzle changed - Working fine - Testing : 0.97 Ltrs - Rectified
CL943 | 2020-10-06 | Cantonment | G | Oil dispenser problem | Breakdown | Ravichandran M | 2020-10-06 | - | Dust cleaned from the flow meter of oil dispenser - Testing: 500 ml - Rectified
CL944 | 2020-10-07 | Pudukkottai | C | Stamping work | Certification | Nepolean & Kathiresan | 2020-10-07 |  | Stamping work completed - Attended
CL945 | 2020-10-08 | Ariyamangalam | D | Nozzle Leakage due to teeth problem & Hosur nozzle testing | Breakdown | Nepolean | 2020-10-08 | - | Nozzle teeth and O Ring changed - Hosur nozzle teeth and Lock changed - Tested - Working fine - Testing Litres - 1.64 Ltrs - Rectified
CL946 | 2020-10-09 | Manapparai | C | Rule 18 work | Certification | Chandrasekar, Kathiresan & Vignesh | 2020-10-09 | - | Rule 18 completed - Earth regenerated - Attended
CL947 | 2020-10-09 | Namakkal 2 | T | Tank Flanges fitment | New Project | Thirumalaisamy | 2020-10-09 | - | Flange fitment completed
CL948 | 2020-10-09 | Dindigul | C | Rule 18 work | Certification | Chandrasekar, Kathiresan & Vignesh | 2020-10-09 | - | Rule 18 completed - Earth regenerated - Attended
CL949 | 2020-10-10 | Ariyamangalam | D | Batchen dispenser power cord testing | Preventive | Nepolean | 2020-10-10 | - | Power cord tested - working fine - Rectified
CL950 | 2020-10-10 | Aravakurichi | C | Rule 18 work - A side slow delivery & Online UPS connected with ATG | Certification | Chandrasekar | 2020-10-10 | - | Rule 18 completed - Excess flow valve directed and changed on 14-10-2020 - Online UPS Connected with ATG - Working fine - Rectified
CL951 | 2020-10-10 | Vellakovil | C | Rule 18 work | Certification | Chandrasekar | 2020-10-10 | - | Rule 18 completed - Earth regenerated - Attended
CL952 | 2020-10-11 | Ariyamangalam | D | D side nozzle not working due to Power card shorted | Breakdown | Nepolean & Prakash | 2020-10-11 | 2 Hours | Spare power card replaced - Rectified
CL953 | 2020-10-11 | Namakkal 2 | G | Tank pipe line & Electrical cable measurement | New Project | Thirumalaisamy | 2020-10-11 | - | Pipe line work completed - Cable measurement completed - Attended
CL954 | 2020-10-11 | Hosur | D | B side nozzle leakage | Breakdown | Suresh | 2020-10-11 | - | Nozzle replaced - Working fine - Testing: 0.97 Ltrs - Rectified
CL955 | 2020-10-12 | Pudukkottai | T | Decanting ROV leakage | Breakdown | Chandrasekar | 2020-10-12 | - | Ball valve stem nut tightened - Leakage arrested - Rectified
CL956 | 2020-10-13 | Perundurai | C | CCOE Inspection | Certification | Prakash | 2020-10-13 | - | CCOE inspection completed - Attended
CL957 | 2020-10-13 | Erode | C | Stamping work | Certification | Prabu | 2020-10-13 | - | Stamping Completed - Attended
CL958 | 2020-10-14 | Karur | C | Rule 18 Work | Certification | Chandrasekar | 2020-10-14 | - | Rule 18 completed - Earth regenerated - Attended
CL959 | 2020-10-14 | Kodungaiyur | A | USB Hub problem | Breakdown | Suneel Sagar | 2020-10-14 | - | USB hub changed - Working fine - Rectified
CL960 | 2020-10-15 | Salem | D | Error 39 occurred | Breakdown | Prabu | 2020-10-15 | - | Reset done - Working fine - Rectified
CL961 | 2020-10-15 | Kodumudi | D | Dispenser keypad problem & panel board operator switch problem | Breakdown | Prabu | 2020-10-15 | - | Flat Cable repunching and working fine - Panel Board operator switch replaced - Rectified
CL962 | 2020-10-16 | T.V.Kovil | T | Unloading point liquid and vapour line LPG leakage | Breakdown | Kathiresan | 2020-10-16 | - | Leakage arrested by Tightening the Bolts - Rectified
CL963 | 2020-10-16 | Karur | G | Control panel not running EB mode and Turbo drive MOL occurred due to power fluctuation | Breakdown | Nepolean | 2020-10-16 | - | MOL arrested by regulating EB power supply - Rectified
CL964 | 2020-10-16 | Namakkal 2 | G | Pipe line welding and hydro test | New Project | Thirumalaisamy | 2020-10-16 | - | Welding and hydro test completed - Attended
CL965 | 2020-10-16 | Cantonment | A | CP voltage data updation in live screen | New Project | Madhavan | 2020-10-16 | - | CP Voltage data updated in live screen - Completed
CL966 | 2020-10-17 | Ariyamangalam | D | B side Nozzle LPG Leakage | Breakdown | Nepolean | 2020-10-17 | - | New nozzle replaced - Hosur nozzle tested - Nozzle teeth replaced - Working fine - Testing B Side: 5.06 Ltrs - Rectified
CL967 | 2020-10-17 | Paramathivelur | T | Dispensing motor spider damage | Breakdown | Thirumalaisamy | 2020-10-17 | - | Dipensing motor spider replaced - Working fine - Rectified
CL968 | 2020-10-18 | Namakkal 2 | G | Mechanical & Welding work | New Project | Thirumalaisamy | 2020-10-17 | - | Mechanical work completed - GI Patta welding work partially completed - Rule 33 data collected - Attended
CL969 | 2020-10-19 | Sankagiri | T | Tank installation | New Project | Prabu | 2020-10-19 | - | Tank installation completed - Attended
CL970 | 2020-10-20 | Avinashi | D | Error 39 occurred | Breakdown | Prabu | 2020-10-20 | - | Flow control adjusted and parameters changed - Working fine - Rectified
CL971 | 2020-10-20 | Chengalpattu | T | Decanting bypass valve alteration & Rule 18 work | Breakdown | Chandrasekar, Gowtham & Vignesh | 2020-10-21 | - | Bypass valve alteration and Rule 18 work completed - Ground earth regenerated - Calibration completed - Rectified
CL972 | 2020-10-20 | T.V.Kovil | G | Yenen offline UPS problem | Breakdown | Kathiresan | 2020-10-20 | - | New UPS replaced - Rectified
CL973 | 2020-10-21 | Sulur | D | Dispenser cutoff problem | Breakdown | Prabu | 2020-10-21 | - | Gas flow changed - Switch replaced - Rectified
CL974 | 2020-10-21 | Chengalpattu | C | Preventive Maintenance | Preventive | Suneel Sagar | 2020-10-21 | - | Preventive Maintenance completed
CL975 | 2020-10-21 | Kodungaiyur | C | Rule 18 work | Certification | Chandrasekar | 2020-10-21 | - | Rule 18 completed - Ground earth regenerated - Attended
CL976 | 2020-10-22 | T.V.Kovil | G | Compressor continuous running due to air leakage | Breakdown | Kathiresan | 2020-10-22 | - | Air hose replaced from EB room to oil dispensing area (40 Mtrs) - Working fine - Rectified
CL977 | 2020-10-22 | Velachery | C | Rule 18 work | Certification | Chandrasekar | 2020-10-22 | - | Rule 18 completed - Ground earth regenerated - Attended
CL978 | 2020-10-22 | Vadivelan Nagar | C | Rule 18 work | Certification | Chandrasekar | 2020-10-22 | - | Rule 18 completed - Ground earth regenerated - Attended
CL979 | 2020-10-23 | Kodungaiyur | C | Stamping work | Certification | Chandrasekar | 2020-10-23 | - | Stamping Completed - Attended
CL980 | 2020-10-23 | T.V.Kovil | A | Cable laying for automation (Office room to CP junction box) to bring CP Volt to live screen. | New Project | kathiresan | 2020-10-23 | - | Cable Laying done - Attended
CL981 | 2020-10-23 | Paramathivelur | D | Noise from dispensing solenoid coil | Breakdown | Thirumalaisamy | 2020-10-23 | - | Dispensing and decanting solenoid coils interchanged - Working Fine - Rectified
CL982 | 2020-10-24 | Theni | D | B side not working due to excess flow valve block & Air leakage | Breakdown | Nepolean | 2020-10-24 | 5 Hours | Excess flow valve, DP Valve, Angle Valve & High flow Low Flow Solenoid coil cleaned - FRC Directed to arrest air leakage - Working fine - Rectified
CL983 | 2020-10-25 | Velachery | T | Tank 1 Float stuck up | Breakdown | Suneel sagar | 2020-10-25 | - | A vibration given to release the float stuck up - Rectified
CL984 | 2020-10-25 | Palayam | T | Tank Hydro Test | New Project | Thirumalaisamy | 2020-10-25 | - | Hydro test completed - Attended
CL985 | 2020-10-28 | Uthamasolapuram | T | Nitrogen Test | New Project | Gowtham | 2020-10-28 | - | Nitrogen Testing completed.No leakage process found satisfactory - attended
CL986 | 2020-10-29 | Ariyamangalam | D | Nozzle testing | Preventive | Nepolean | 2020-10-29 | - | Nozzle Tested and serviced - Testing : 2.46 Ltrs - Attended
CL987 | 2020-10-29 | Sulur | D | Dispenser keypad not working | Breakdown | Prabu | 2020-10-29 | - | Keypads both sides replaced - Working fine - Rectified
CL988 | 2020-10-29 | Kumbakonam | T | Tank big & small flange and excess flow valve fitting | New Project | Kathiresan | 2020-10-29 | - | Flange and Excess flow valve fitment completed - Attended
CL989 | 2020-10-31 | Sulur | C | Dispenser Calibration | Certification | Prabu | 2020-10-31 | - | Dispenser calibration completed - Testing : 429.49 Ltrs - Attended
CL990 | 2020-10-31 | Udumalpet | D | Batchen dispenser metering unit changing and calibration | Breakdown | Prabu & Gowtham | 2020-11-01 | - | Metering unit replaced - Working fine - Testing : 670.57 Ltrs Rectified
CL991 | 2020-11-01 | Velachery | D | D side nozzle problem | Breakdown | Suneel sagar | 2020-11-01 | - | New yenen nozzle replaced - Working fine - Rectified
CL992 | 2020-11-01 | Karur | D | A side on/off switch & dispensing line pressure gauge problem | Breakdown | Thirumalaisamy | 2020-11-01 | - | On/off switch and Pressure Gauge changed - Rectified
CL993 | 2020-11-01 | Palayam | T | CP Installation | New Project | Nepolean | 2020-11-01 | - | CP installation completed - Attended
CL994 | 2020-11-02 | Ariyamangalam | G | Mass flow meter testing | Preventive | Chandrasekar | 2020-11-02 | - | Tested - Testing Litres - 165.10 - Attended
CL995 | 2020-11-02 | Cantonment | A | "Test Litre" software checking | New Project | Madhavan | 2020-11-02 | - | " Test liter " software checked and test liter added in shift closing report. Testing liters : 15.29 liters - Rectified
CL996 | 2020-11-03 | Theni | D | Error 39 and LPG cut off problem | Breakdown | Nepolean | 2020-11-03 | - | Software updated - B side metering unit DP Valve & Angle valve cleaned - DP Valve small o ring changed - Working fine - Rectified
CL997 | 2020-11-03 | Uthamasolapuram | G | Commissioning work | New Project | Chandrasekar, Gowtham & Vignesh | 2020-11-05 | - | Commissioning and Dispenser stamping completed - Attended
CL998 | 2020-11-03 | Ariyamangalam | G | Air compressor not working | Breakdown | Kathiresan | 2020-11-03 | - | Compressor starter coil connector refitted - Working fine - Rectified
CL999 | 2020-11-04 | Tirunelveli | D | Batchen dispenser hung | Breakdown | Nepolean | 2020-11-04 | 5 Hours | Mother board power card cables refitted - Cold Boot done - Working fine - Rectified
CL1000 | 2020-11-04 | Palladam | T | Unloading training & Tank area ROV leakage | Breakdown | Prabu | 2020-11-04 | - | Unloading training completed - ROV Leakage arrested by tightening - Working fine - Rectified
CL1001 | 2020-11-04 | Namakkal 1 | R | Surge protector failed | Breakdown | Thirumalaisamy | 2020-11-04 | - | Surge Protector replaced - Rectified
CL1002 | 2020-11-06 | Karur | D | Dispenser one side not working | Breakdown | Nepolean | 2020-11-06 | - | A side solenoid coil and DP Valve cleaned - B side Solenoid valve cleaned - Working fine - Rectified
CL1003 | 2020-11-06 | Kumbakonam | G | Pipe line hydro test | New Project | Kathiresan | 2020-11-06 | - | Pipe line hydro test completed - Rule 33 data collected - Attended
CL1004 | 2020-11-06 | Uthamasolapuram | A | Automation installation | New Project | Madhavan | 2020-11-06 | - | Automation brought online with mobile billing - Attended
CL1005 | 2020-11-06 | Hosur | C | Rule 18 work | Certification | Chandrasekar, Gowtham & Vignesh | 2020-11-07 | - | Rule 18 work completed - Ground earth regenerated - Leakages found and arrested - Attended
CL1006 | 2020-11-06 | Krishnagiri | C | Rule 18 work | Certification | Chandrasekar, Gowtham & Vignesh | 2020-11-07 | - | Rule 18 work completed - Ground earth regenerated - Leakages found and arrested - Attended
CL1007 | 2020-11-07 | Salem | C | Rule 18 work | Certification | Chandrasekar, Gowtham & Vignesh | 2020-11-07 | - | Rule 18 work completed - Ground earth regenerated - Leakages found and arrested - Attended
CL1008 | 2020-11-08 | Vellakovil | D | Nozzle one side cutoff problem | Breakdown | Thirumalaisamy | 2020-11-08 | - | Selector switch replaced - Working fine - Rectified
CL1009 | 2020-11-08 | Attur | C | Rule 18 work | Certification | Chandrasekar, Gowtham & Vignesh | 2020-11-08 | - | Rule 18 work completed - Ground earth regenerated - Leakages found and arrested - Attended
CL1010 | 2020-11-08 | Thuraiyur | C | Rule 18 work | Certification | Chandrasekar, Gowtham & Vignesh | 2020-11-08 | - | Rule 18 work completed - Ground earth regenerated - Leakages found and arrested - Attended
CL1011 | 2020-11-09 | Ariyamangalam | D | A side nozzle LPG Leakage | Breakdown | Nepolean | 2020-11-09 | - | Serviced nozzle replaced - Working fine - Testing: 1.13 Ltrs - Rectified
CL1012 | 2020-11-09 | Virudhachalam | G | Nitrogen Test | New Project | Kathiresan and Thirumalaisamy | 2020-11-09 | - | Nitrogen test completed - Attended
CL1013 | 2020-11-09 | Ariyamangalam | G | Mass flow meter testing | Preventive | Nepolean | 2020-11-09 | - | Mass flow meter tested - Tesing C side: 223.66 Ltrs - D side : 208.13 Ltrs - Attended
CL1014 | 2020-11-10 | Krishnagiri | D | Metering unit problem | Breakdown | Nepolean & Thirumalaisamy | 2020-11-11 | - | High flow low flow solenoid valve cleaned - Excess flow valve cleaned metering unit primary coil cleaned and inlet changed - Working fine - Rectified
CL1015 | 2020-11-10 | Uthamapalayam | G | Nitrogen Test | New Project | Kathiresan & Gowtham | 2020-11-11 | - | Nitrogen test completed - Attended
CL1016 | 2020-11-10 | Dindigul | D | Dispensing hose leakage | Breakdown | Gowtham | 2020-11-10 | - | B side dispensing hose changed - Hose testing: 0.84 Ltrs - Rectified
CL1017 | 2020-11-10 | Dindigul | T | Unloading process not working | Breakdown | Nepolean | 2020-11-10 | - | Vapour balance done - Working fine - Rectified
CL1018 | 2020-11-11 | Udumalpet | C | Dispenser Calibration | Certification | Prabu | 2020-11-11 | - | Dispenser calibration completed - Attended
CL1019 | 2020-11-11 | Bodi | G | Nitrogen Test | New Project | Kathiresan & Gowtham | 2020-11-11 | - | Nitrogen test completed - Attended
CL1020 | 2020-11-12 | Namakkal 2 | C | Rule 33 third party inspection | New Project | Krishna bhalaji | 2020-11-12 | - | Inspection completed - Attended
CL1021 | 2020-11-12 | Uthamasolapuram | G | Loading and unloading training | New Project | Prabu | 2020-11-12 | - | Training completed - Attended
CL1022 | 2020-11-16 | T.V.Kovil | D | A side nozzle leakage | Breakdown | Kathiresan | 2020-11-16 | - | Spare nozzle changed - Working fine - Testing: 1.92 Ltrs - Rectified
CL1023 | 2020-11-17 | Uthamasolapuram | G | Unloading & Unloading operator training | New Project | Krishna bhalaji | 2020-11-17 | - | Unloading done and training provided - Attended
CL1024 | 2020-11-18 | Ariyamangalam | D | C side nozzle LPG leakage | Breakdown | Nepolean | 2020-11-18 | - | Nozzle replaced - Working fine - Testing: 0.85 Ltrs - Rectified
CL1025 | 2020-11-18 | Udumalpet | C | Dispenser stamping | Certification | Prabu | 2020-11-18 | - | Stamping Completed - Attended
CL1026 | 2020-11-19 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2020-11-19 | - | Nozzle serviced & Tested - Working fine - Testing: 1.63 Ltrs - Rectified
CL1027 | 2020-11-19 | Karur | G | Voltage fluctuation | Breakdown | Thirumalaisamy | 2020-11-19 | - | Voltage regulated - Fill point emergency push button stuck up released - Working fine - Rectified
CL1028 | 2020-11-20 | Theni | G | Servo stabilizer servo mode problem | Breakdown | Nepolean | 2020-11-20 | - | Control panel MNX22 Contactor replaced - Servo stabilizer serviced by concern person - Rectified
CL1029 | 2020-11-20 | Udumalpet | R | PLC stop id problem | Breakdown | Prabu | 2020-11-20 | 15 Mins | PLC Reset done - Working fine - Rectified
CL1030 | 2020-11-20 | Krishnagiri | R | STP Motor MOL occurred due to voltage fluctutaion | Breakdown | Nepolean | 2020-11-20 | - | Reset done - MOL released - Rectifed
CL1031 | 2020-11-20 | Perundurai | G | Unloading Training | Preventive | Prabu | 2020-11-20 | - | Training completed - Attended
CL1032 | 2020-11-20 | Kodumudi | T | Unloading hose leakage | Breakdown | Prabu | 2020-11-20 | - | Hose thread tightened with teflon tape - Leakage arrested - Rectified
CL1033 | 2020-11-21 | Uthamasolapuram | T | Product unloading | New Project | Prabu | 2020-11-21 | - | Product unloaded safely - Attended
CL1034 | 2020-11-21 | Krishnagiri | D | Dispenser cutoff problem | Breakdown | Prabu | 2020-11-22 | - | Dispenser communication cable refitted - LPG Flow adjusted - A and B side display interchanged - Working fine - Testing: 10 Ltrs - Rectified
CL1035 | 2020-11-22 | Ariyamangalam | D | Dispenser power card problem | Breakdown | Chandrasekar | 2020-11-22 | - | Power card replaced - Working fine - D side testing : 14.51 Ltr - Rectified
CL1036 | 2020-11-23 | Rasipuram | T | Unloading liquid hose leakage | Breakdown | Thirumalaisamy | 2020-11-23 | - | Hose thread tightened - Leakage arrested - Rectified
CL1037 | 2020-11-23 | Kodungaiyur | D | Leakage in ROV under Dispenser | Breakdown | Suneel Sagar | 2020-11-23 | - | ROV under dispense replaced - Leakage arrested - Working fine - Rectified
CL1038 | 2020-11-23 | T.V.Kovil | D | Yenen keypad testing | Preventive | Chandrasekar | 2020-11-23 | - | Keypad - 5 nos tested - Working fine - Attended
CL1039 | 2020-11-23 | Paramathivelur | D | Spare nozzle testing | Preventive | Thirumalaisamy | 2020-11-23 | - | Nozzle serviced and tested - Nozzle teeth 4 nos changed - Testing: 0.85 Ltrs - Attended
CL1040 | 2020-11-23 | Ariyamangalam | D | Dispenser B side not working | Breakdown | Chandrasekar | 2020-11-23 | - | DP Valve and High Flow and Low Flow Solenoid valve cleaned - Working fine - B side testing: 61.59 Ltrs - Rectified
CL1041 | 2020-11-24 | Kangeyam | D | Kalvacha dispenser problem | Breakdown | Prabu | 2020-11-24 | - | Power line reconnected - V1 V2 and P1 P2 relays interchanged - Yenen dispenser flow adjusted - Working fine - Testing: 80.43 Ltrs - Rectified
CL1042 | 2020-11-25 | T.V.Kovil | G | Mass flow meter testing | Preventive | Nepolean | 2020-11-25 | - | Mass flow meter tested - Testing A side - 145.48 Ltrs; B side - 110.91Ltrs; C side - 138.67 Ltrs; D side - 146.24 Ltrs; Total: 541.30 Ltrs - Attended
CL1043 | 2020-11-26 | Pudukkottai | D | B side nozzle leakage | Breakdown | Chandrasekar | 2020-11-26 | - | Nozzle teeth - 4 Nos changed - Rectified
CL1044 | 2020-11-30 | Ariyamangalam | D | Power card and Nozzle testing work | Preventive | Nepolean | 2020-11-30 | - | Power Card and nozzle testing completed - C side: 2.54 Ltr; D side - 2.38 Ltr - Attended
CL1045 | 2020-11-30 | Vellakovil | D | Excess dispensing of ALPG to retail customer | Breakdown | Prabu | 2020-11-30 | - | K Factor changed - Rectified A side old k factor 11100 new k factor 11000 B side Old k factor 10800 New k factor 10500
CL1046 | 2020-12-01 | Paramathivelur | A | CP Cable laying for automation | New Project | Thirumalaisamy | 2020-12-01 | - | Cable laying completed - Attended
CL1047 | 2020-12-02 | Palakkad - FCRI | G | Mass flow meter recalibration | Preventive | Chandrasekar & Prabu | 2020-12-03 | - | Mass flow recalibration completed - Attended
CL1048 | 2020-12-04 | Namakkal 1 | R | B phase surge arrester defected | Breakdown | Thirumalaisamy | 2020-12-04 | - | Surge arrester replaced - Working fine - Rectified
CL1049 | 2020-12-04 | Paramathivelur | G | Compressor starter and contactor damaged | Breakdown | Thirumalaisamy | 2020-12-18 | - | Compressor starter replaced - Working fine - Rectified
CL1050 | 2020-12-04 | T.V.Kovil | A | CP voltage data updation in live screen | New Project | Madhavan | 2020-12-04 | - | CP Voltage data updated in live screen - Completed
CL1051 | 2020-12-04 | Dharapuram | C | Rule 19 work | Certification | Chandrasekar, Gowtham & Vignesh | 2020-12-07 | 2 Days 9 Hours (10 hours delay due to fire accident) | Rule 19 Completed - Attended
CL1052 | 2020-12-04 | Paramathivelur | A | CP voltage data updation in live screen | New Project | Madhavan & Thirumalaisamy | 2020-12-04 | - | CP Voltage data updated in live screen - Completed
CL1053 | 2020-12-05 | Namakkal 1 | A | CP voltage data updation in live screen | New Project | Prabu | 2020-12-05 | - | CP Voltage data updated in live screen - Completed
CL1054 | 2020-12-05 | Rasipuram | T | Unloading ROV not rotating | Breakdown | Prabu | 2020-12-05 | - | Refitted and Oil applied - Rectified
CL1055 | 2020-12-07 | Attur | T | Decanting pump leakage | Breakdown | Nepolean & Dharmesh | 2020-12-08 | - | Decanting pump bearing and O rings refitted with teflon applied - Grease applied - Leakage arrested - Rectified
CL1056 | 2020-12-07 | Sulur | C | Rule 19 work | Certification | Prakash | 2020-12-10 | 2 Days 10 Hours (24 hours delay due to Nitrogen arrangements) | Rule 19 work completed and above ground pipeling welding work completed - Attended
CL1057 | 2020-12-09 | Attur | T | Decanting pump leakage | Breakdown | Prabu | 2020-12-10 | - | Grease applied - Leakage arrested - Rectified
CL1058 | 2020-12-10 | Aravakurichi | T | Unloading liquid hose leakage | Breakdown | Thirumalaisamy | 2020-12-10 | - | Hose adapters refitted applying teflon to arrest leakage - Rectified
CL1059 | 2020-12-10 | Paramathivelur | G | Unloading training to new staff | Preventive | Krishna bhalaji | 2020-12-10 | - | Training completed - Attended
CL1060 | 2020-12-11 | Velachery | D | Kalvacha dispenser slow delivery | Breakdown | Prabu | 2020-12-12 | - | High flow low flow solenoid valve cleaned - Filter cleaned - Excess flow valve directed - Working fine - Testing: 32.26 Ltrs - Rectified
CL1061 | 2020-12-11 | Rasipuram | G | Unloading training to new staff | Preventive | Krishna bhalaji | 2020-12-11 | - | Training completed - Attended
CL1062 | 2020-12-12 | Virudhachalam | G | Tank purging, unloading, dispenser commissioning, Stamping and Pump opening with automation | New Project | Prakash & Madhavan | 2020-12-14 | - | Outlet is open to public with automation - Attended
CL1063 | 2020-12-13 | Velachery | T | Unloading motor abnormal noise and vibration | Breakdown | Prabu | 2020-12-13 | - | Decanting pump bearing and O rings refitted with teflon applied - Grease applied- Dispensing motor lovejaw coupling changed - Motor Alignment changed - Working Fine - Rectified
CL1064 | 2020-12-14 | Tirunelveli | D | Batchen dispenser metering unit leakage | Breakdown | Kathiresan | 2020-12-15 | - | Metering unit bottom O ring replaced - Working fine - Testing : 87.35 Ltrs - Rectified
CL1065 | 2020-12-15 | Ariyamangalam | D | B side nozzle problem | Breakdown | Nepolean | 2020-12-16 | - | Nozzle Teeth 4 nos replaced - Rectified
CL1066 | 2020-12-15 | Kodungaiyur | D | Dispenser offline UPS problem | Breakdown | Suneel Sagar | 2020-12-15 | - | Dispenser offline ups replaced by new one - Sales is normal on both EB & DG supply - Rectified
CL1067 | 2020-12-15 | Palladam | D | Nozzle leakage | Breakdown | Gowtham | 2020-12-15 | - | Nozzle teeth replaced for both the nozzles - Testing : A Side - 55.22 Ltrs; B side - 12.14 Ltrs - Rectified
CL1068 | 2020-12-15 | Vellakovil | D | B side low flow and cutoff problem | Breakdown | Thirumalaisamy | 2020-12-15 | - | Low flow High flow valve cleaned - Working fine - Testing: 24 Ltrs- Rectified
CL1069 | 2020-12-15 | Namakkal 1 | D | Dispenser display and keypad problem | Breakdown | Prabu | 2020-12-15 | - | Displays interchanged - Keypad replaced - Working fine - Rectified
CL1070 | 2020-12-16 | Rasipuram | C | Stamping work | Certification | Vignesh & Prabu | 2020-12-16 | - | Stamping completed Old k factor A side 10150 B side 10150 New k factor A side 10050 B side 10100 Total testing 611.87lit - Attended
CL1071 | 2020-12-16 | Namakkal 1 | C | Stamping work | Certification | Vignesh & Prabu | 2020-12-16 | - | Stamping completed. Total testing - 264.26lit - Attended
CL1072 | 2020-12-16 | Kodungaiyur | R | Surge protecter problem | Breakdown | Suneel Sagar | 2020-12-16 | - | Surge protecter bypassed and working fine - Material will be replaced - Rectified
CL1073 | 2020-12-16 | Palladam | D | Batchen dispenser one side improper working | Breakdown | Gowtham | 2020-12-16 | - | Dispensre power card problem - Kept under observation
CL1074 | 2020-12-16 | Ariyamangalam | D | D side nozzle problem | Breakdown | Nepolean | 2020-12-16 | - | Nozzle teeth 2 nos changed - Working fine - Rectified
CL1075 | 2020-12-16 | Bodi | G | Commissioning work, Automation & Camera installation | New Project | Prakash, Vignesh, Chandrasekar & Kathiresan | 2020-12-25 | - | Commissioning completed - Sales Started with automation - Attended
CL1076 | 2020-12-16 | Uthamapalayam | G | Commissioning work, Automation & Camera installation | New Project | Prakash, Vignesh, Chandrasekar & Kathiresan | 2020-12-25 | - | Commissioning completed - Sales Started with automation - Attended
CL1077 | 2020-12-17 | Velachery | C | Dispenser calibration & Stamping | Certification | Vignesh & Prabu | 2020-12-18 | - | Stamping completed - Dispenser excess flow valve replaced - Attended
CL1078 | 2020-12-17 | Palayam | G | Material Unloading | New Project | Thirumalaisamy | 2020-12-17 | - | Material unloading safety done - Attended
CL1079 | 2020-12-18 | Ariyamangalam | G | Compressor Fenner B47 Belt problem | Breakdown | Nepolean | 2020-12-18 | - | New belt replaced - Working fine - Rectified
CL1080 | 2020-12-18 | Tharamangalam | C | CCOE Inspection | Certification | Prakash | 2020-12-18 | - | CCOE inspection completed - Attended
CL1081 | 2020-12-18 | Uthamasolapuram | C | CCOE Inspection | Certification | Prakash | 2020-12-18 | - | CCOE inspection completed - Attended
CL1082 | 2020-12-18 | Pudukkottai | T | Dispensing motor line problem | Breakdown | Nepolean | 2020-12-18 | - | Dispensing line by pass valve cleaned - Working fine - Rectified
CL1083 | 2020-12-18 | Udumalpet | T | DOL starter return signal problem | Breakdown | Gowtham | 2020-12-18 | - | Wiring recorrected - Working fine - Rectified
CL1084 | 2020-12-18 | Vadivelan Nagar | C | Stamping work | Certification | Vignesh & Prabu | 2020-12-18 | - | Stamping completed - Attended
CL1085 | 2020-12-19 | Bhavani | C | Stamping work | Certification | Vignesh & Prabu | 2020-12-19 | - | Stamping Completed - Attended
CL1086 | 2020-12-19 | Kodumudi | C | Stamping work | Certification | Vignesh & Prabu | 2020-12-20 | - | Stamping Completed - Attended
CL1087 | 2020-12-19 | Kodungaiyur | R | Surge protecter problem | Breakdown | Suneel Sagar | 2020-12-19 | - | Surge protecter replaced - Working fine - Rectified
CL1088 | 2020-12-20 | Palayam | T | Tank cleaning & Excess flow valve fitting | New Project | Thirumalaisamy | 2020-12-20 | - | Tank cleaned and excess flow valve fitting completed - Attended
CL1089 | 2020-12-20 | Aravakurichi | G | 1 Kva online UPS battery problem | Breakdown | Thirumalaisamy | 2020-12-20 | - | Battery replaced under warranty - Rectified
CL1090 | 2020-12-21 | Pudukkottai | T | Dispensing pump suction problem | Breakdown | Nepolean & Thirumalaisamy | 2020-12-21 | - | DPS directed - Kept under observation - Rectified
CL1091 | 2020-12-22 | Mettupalayam | C | Dispenser stamping work | Certification | Prabu & Gowtham | 2020-12-22 | - | Stamping Completed - Attended
CL1092 | 2020-12-24 | Dindigul | C | Stamping work | Certification | Nepolean & Vigneshwaran | 2020-12-24 | - | Stamping Completed - Attended
CL1093 | 2020-12-25 | Theni | D | Dispenser not working | Breakdown | Kathiresan | 2020-12-25 | - | Dispenser parameter changed - Working fine - Rectified
CL1094 | 2020-12-25 | Chengalpattu | T | Unloading vapour hose leakage | Breakdown | Suneel Sagar | 2020-12-25 | - | Hose replaced - Working fine - Rectified
CL1095 | 2020-12-26 | Erode | T | Dispensing motor love jaw coupling complaint | Breakdown | Prabu | 2020-12-26 | - | Love jaw coupling replaced - Working fine - Rectified
CL1096 | 2020-12-26 | Palayam | G | Pipe line hydro test | New Project | Thirumalaisamy | 2020-12-26 | - | Hydro test completed - Pressure = 48 Kg/cm2 - Rule 33 data collected - Completed
CL1097 | 2020-12-26 | Palladam | T | Dispensing pneumatic hose damaged | Breakdown | Gowtham | 2020-12-26 | - | Pneumatic hose replaced - Rectified
CL1098 | 2020-12-26 | Theni | C | Stamping work | Certification | Kathiresan | 2020-12-26 | - | Stamping completed - Dispenser on off switch changed and online UPS serviced - Attended
CL1099 | 2020-12-27 | Paramathivelur | D | Dispenser Error 99 occurred | Breakdown | Thirumalaisamy | 2020-12-27 | - | USB port and cable replaced - Working fine - Under observation - Rectified
CL1100 | 2020-12-28 | Tirunelveli | R | Control panel problem | Breakdown | Nepolean | 2020-12-28 | - | R2 relay changed - Working fine - Rectified
CL1101 | 2020-12-28 | Palayam | G | SS pipe welding | New Project | Vignesh | 2020-12-29 | - | SS Pipe welding completed - Attended
CL1102 | 2020-12-28 | Tharamangalam | G | Unloading training | Preventive | Prabu | 2020-12-28 | - | Unloading training completed - Attended
CL1103 | 2020-12-28 | Vadivelan Nagar | G | Compressor starter defective | Breakdown | Suneel Sagar | 2020-12-28 | - | Starter contactor replaced - working fine - Rectified
CL1104 | 2020-12-29 | Thuraiyur | G | Ball valve leakage | Breakdown | Nepolean | 2020-12-29 | - | ROV replaced - Leakage arrested - Rectified
CL1105 | 2020-12-29 | Namakkal 1 | G | Compressor not working | Breakdown | Prabu | 2020-12-29 | - | Compressor starter and pressure switch adjusted - Oil changed - Working fine - Rectified
CL1106 | 2020-12-29 | Kodumudi | D | A side nozzle leakage | Breakdown | Thirumalaisamy | 2020-12-29 | - | Nozzle teeth 4 nos changed - Leakage arrested - Rectified
CL1107 | 2020-12-30 | Cantonment | A | Automation bill reprint option enabling | New Project | Madhavan | 2020-12-30 | - | Bill reprint option enabled - Completed
CL1108 | 2020-12-30 | Ariyamangalam | G | Mass flow meter testing | Preventive | Nepolean | 2020-12-30 | - | Mass flow meter tested - Testing D side : 319.41 Ltrs - Attended
CL1109 | 2020-12-30 | Namakkal 2 | G | Nitrogen Test | New Project | Prabu & Vignesh | 2020-12-30 | - | Nitrogen (N2) test completed. Testing pressure @ 14kg/cm^2.Pressure holded @10kg/cm^2. ATG SS pipe 4 nos leakage test done
CL1110 | 2020-12-30 | Ariyamangalam | G | Mass flow meter testing | Preventive | Nepolean | 2020-12-30 | - | Mass flow meter tested - Testing C side: 12.95 Ltrs; D side : 52.08 Ltrs - Attended
CL1111 | 2020-12-31 | Dindigul | D | Dispenser slow delivery | Breakdown | Chandrasekar & Kathiresan | 2020-12-31 | - | Motor bypass valve and dispenser filter cleaned - B side nozzle 4 nos replaced - Working fine - Rectified
CL1112 | 2020-12-31 | Velachery | D | Dispensing hoses defective | Breakdown | Suneel Sagar | 2020-12-31 | - | 5m and 0.5m hoses replaced - Rectified
CL1113 | 2020-12-31 | Ariyamangalam | D | Virudhunagar nozzle testing | Preventive | Nepolean | 2020-12-31 | - | Nozzle tested at D side Testing : 1.59 Ltrs - Attended
CL1114 | 2020-12-31 | Namakkal 2 | G | Electrical and mechanical work | New Project | Prabu & Vignesh | 2020-12-31 | - | Electrical and mechanical work completed - Attended