## All
Service Logs - Jan' 2021 to Dec' 2021
ticket_no | date | name_of_the_outlet | code | nature_of_the_complaint | breakdown__ preventive | service_engineer | rectified_on | interruption_of_sales_if_any__time_duration | details_of_work_done
CL1115 | 2021-01-01 | Dharmapuri | G | Nitrogen Test | New Project | Prabu & Vignesh | 2021-01-01 | - | Nitrogen (N2) test completed. Testing pressure @ 14kg/cm^2.Pressure holded @10kg/cm^2. Mechanical and electrical final work completed - Attended
CL1116 | 2021-01-02 | Mulanur | G | Nitrogen Test | New Project | Vignesh & Thirumalaisamy | 2021-01-03 | - | Mulanur station (N2) test completed. Tested at 13.5kg/cm^2.pressure holded at 10.5kg/cm^2 - Attended
CL1117 | 2021-01-02 | Ariyamangalam | A | Dispenser automation testing | New Project | Nepolean | 2021-01-02 | - | Testing completed - A side: 0.20 Ltrs - Attended
CL1118 | 2021-01-03 | Avinashi | R | Control panel not working in stabilizer mode | Breakdown | Gowtham | 2021-01-03 | - | Panel working in bypass mode - Temporarily rectified
CL1119 | 2021-01-03 | Velachery | T | Dispensing motor spider problem | Breakdown | Suneel Sagar | 2021-01-03 | - | Spider changed - Working fine - Rectified
CL1120 | 2021-01-04 | Virudhunagar | G | Earthing flat & Dispenser keypad replacing work | Breakdown | Kathiresan | 2021-01-06 | - | Earth flat and B side new keypad replaced - Working fine - Rectified
CL1121 | 2021-01-04 | Virudhachalam | C | CCOE inspection | Certification | Prakash | 2021-01-04 | - | CCOE Inspection completed - Attended
CL1122 | 2021-01-05 | Karur | G | Above ground motor pipeline welding | New Project | Chandrasekar & Thirumalaisamy | 2021-01-09 | - | Pipe line welding work completed - Pipe line hydro test done at 48kg/cm^2 - Completed
CL1123 | 2021-01-06 | Pudukkottai | T | Pumping unit suction problem | Breakdown | Nepolean | 2021-01-07 | - | A new SS tube line fixed and needle valve near pressure gauge is closed - Working fine - Under observation - Rectified
CL1124 | 2021-01-07 | Cantonment | D | Nozzle complaint | Breakdown | Vignesh | 2021-01-07 | - | C & D side nozzle hammer teeth replaced - Rectified
CL1125 | 2021-01-07 | Karur | D | Additional dispenser installation | New Project | Prakash & Vignesh | 2021-01-08 | - | Dispenser installation completed - Working fine - Attended
CL1126 | 2021-01-08 | Ariyamangalam | A | Testing through automation | New Project | Madhavan & Nepolean | 2021-01-08 | - | Testing done - D side: 23.83 Ltrs - Attended
CL1127 | 2021-01-09 | Vadivelan Nagar | D | B side display card - D side keypad and display card problem | Breakdown | Suneel Sagar | 2021-01-09 | - | Keypad and Display cards replaced - Found satisfactory - Rectified
CL1128 | 2021-01-09 | Karur | D | A side breakaway leakage | Breakdown | Thirumalaisamy | 2021-01-09 | - | New breakaway replaced - Rectified
CL1129 | 2021-01-09 | Dindigul | D | Automation installation, Above ground motor and pump changing and Dispenser electronic module replacing | New Project | Prakash, Dharmesh, Chandrasekar & Thirumalaisamy | 2021-01-11 | - | Above ground motor and pump changed - Dispenser electronics module changed - Automation installed and brought online - Completed
CL1130 | 2021-01-09 | T.V.Kovil | A | Individual nozzle dispensing | New Project | Madhavan | 2021-01-09 | - | Individual nozzle dispensing with and without mobile activated - Under observation - Completed
CL1131 | 2021-01-11 | Cantonment | D | D side nozzle LPG leakage | Breakdown | Nepolean | 2021-01-11 | - | New yenen nozzle replaced - D side OB. Reading : 1846955.42 - Testing 0.92 ltrs - Rectified
CL1132 | 2021-01-12 | Uthamapalayam | T | Decanting motor - bypass valve going out of order sometimes - N2 machine and compressor installation | Breakdown | Kathiresan | 2021-01-12 | - | Kept under observation - N2 machine and compressor installed - Attended
CL1133 | 2021-01-13 | Bodi | G | N2 air machine and compressor installation | New Project | Kathiresan | 2021-01-13 | - | N2 machine and compressor installed and ROV Air leakage arrested - Attended
CL1134 | 2021-01-15 | Ariyamangalam | D | Batchen dispenser nozzle problem | Breakdown | Nepolean | 2021-01-15 | - | Dispenser A side and B side nozzle teeth replaced - Working fine - Rectified
CL1135 | 2021-01-15 | Cantonment | D | Batchen dispenser nozzle problem | Breakdown | Nepolean | 2021-01-15 | - | Dispenser A side and B side nozzle teeth replaced - Working fine - Rectified
CL1136 | 2021-01-15 | Sulur | T | Unloading motor rotates in reverse direction | Breakdown | Gowtham | 2021-01-15 | - | Error occurred in EB input phase - Altered - Motor rotates in right direction -New ROV Fixed - Working fine - Rectified
CL1137 | 2021-01-16 | Vadivelan Nagar | T | Unloading strainer filter problem | Breakdown | Suneel Sagar | 2021-01-16 | - | Strainer filter cleaned - Rectified
CL1138 | 2021-01-16 | Ariyamangalam | D | Dispenser nozzle teeth problem | Breakdown | Nepolean | 2021-01-16 | - | A side and C side nozzle teeth changed - Working fine - Rectified
CL1139 | 2021-01-18 | Kodungaiyur | A | Automation cable reroute and repressing | New Project | Suneel Sagar | 2021-01-18 | - | Cable rerout and repressing work completed - Automation found satisfactory - Completed
CL1140 | 2021-01-18 | Palladam | D | Dispenser air hose damaged | Breakdown | Gowtham | 2021-01-18 | - | Pneumatic hose replaced - Rectified
CL1141 | 2021-01-19 | Ariyamangalam | D | D side nozzle testing | Preventive | Nepolean | 2021-01-19 | - | Nozzle tested - Testing D Side : 13.43 Ltrs - Rectified
CL1142 | 2021-01-19 | Cantonment | D | Dispenser A side on/off switch problem | Breakdown | Nepolean | 2021-01-19 | - | Dispenser On / Off switch replaced - Working fine - Rectified
CL1143 | 2021-01-19 | Karur | D | Batchen and Yenen Dispensers stamping | Certification | Thirumalaisamy | 2021-01-19 | 10 Hours | Both dispensers stamping completed - Opening reading : C side:340.37 D side:325.27 - Completed
CL1144 | 2021-01-20 | Avinashi | R | MOL problem | Breakdown | Gowtham | 2021-01-20 | - | STP - Pressure equalizer line leakage arrested and opened - Rectified
CL1145 | 2021-01-20 | Uthamasolapuram | D | Dispensing suction problem | Breakdown | Prabu | 2021-01-20 | - | Suction problem rectified by equalizer ball valve pressure adjusting - Working Fine - Rectified
CL1146 | 2021-01-20 | Uthamapalayam | T | Unloading motor not working | Breakdown | Kathiresan | 2021-01-21 | - | Unloading pump bypass valve cleaned - Motor working normally - Rectified
CL1147 | 2021-01-21 | T.V.Kovil | D | B side nozzle leakage | Breakdown | Vigneshwaran | 2021-01-21 | - | Spare nozzle replaced - Working fine - Testing B side: 1.20 Ltrs - Rectified
CL1148 | 2021-01-21 | Paramathivelur | D | A side nozzle problem and PM Report | Breakdown | Thirumalaisamy | 2021-01-21 | - | A side nozzle teeth replaced and PMR done - Rectified
CL1149 | 2021-01-21 | Bodi | D | Dispensing suction problem | Breakdown | Kathiresan | 2021-01-21 | - | Suction problem rectified by equalizer ball valve pressure adjusting - Working Fine - Rectified
CL1150 | 2021-01-21 | Kodungaiyur | R | Soft starter installation and PM Report | Preventive | Suneel Sagar | 2021-01-21 | - | Soft starter installed in control panel and PMR Done - Attended
CL1151 | 2021-01-21 | Theni | G | Online UPS Cooling fan problem and PM Report | Breakdown | Kathiresan | 2021-01-21 | - | UPS Cooling fan replaced by Consul service person and PMR done - Rectified
CL1152 | 2021-01-22 | Ariyamangalam | D | D side nozzle servicing and testing | Preventive | Nepolean | 2021-01-22 | - | Nozzle NRV O ring, Front black O ring and nozzle teeth replaced - Working fine - Testing : D side - 1.56 Ltrs - Attended
CL1153 | 2021-01-23 | Dharmapuri | G | Commissioning work | New Project | Prakash, Madhavan, Vignesh & Sathyaseelan | 2021-01-25 | - | Tank purging, unloading, Dispensing pumps, Dispenser and Automation commissioning completed - Dispenser Stamping Completed - Sales started with automation - Opening Reading A side - 666.01 B side - 477.83 - Tank 84% - Completed
CL1154 | 2021-01-23 | Sankari | G | Tank cleaning and excess flow valve fitting | New Project | Thirumalaisamy | 2021-01-23 | - | Tank Cleaned - Excess flow valve is fitted and flanges are refitted - Completed
CL1155 | 2021-01-23 | Cantonment | D | Dispenser nozzle problem | Breakdown | Nepolean | 2021-01-23 | - | Yenen dipsenser A and B side nozzles changed - A side OB.reading : 9203157.74 B side OB. Reading : 7610224.45 A side testing : 1.18 B side testing :. 1.14 - Rectified
CL1156 | 2021-01-24 | Perundurai | G | Unloading training and PMR | Preventive | Thirumalaisamy | 2021-01-24 | - | Unloading training done and PM Report completed - Attended
CL1157 | 2021-01-25 | Madurai | G | Site marking | New Project | Kathiresan | 2021-01-25 | - | Site marking completed - Attended
CL1158 | 2021-01-26 | T.V.Kovil | D | Batchen dispenser B side On/Off switch problem | Breakdown | Nepolean | 2021-01-26 | - | B side new on / off switch changed - Working fine - Testing B side : 9.88 Ltrs - Rectified
CL1159 | 2021-01-26 | Palladam | G | Preventive Maintenance Report | Preventive | Gowtham | 2021-01-26 | - | PM Report done - Found Satisfactory - Attended
CL1160 | 2021-01-28 | Ariyamangalam | G | N2 air machine drain exhaust hole problem | Breakdown | Nepolean | 2021-01-28 | - | Air machine filter cleaned - Rectified
CL1161 | 2021-01-29 | Melur | G | Site marking | New Project | Prakash, Kathiresan & Vignesh | 2021-01-29 | - | Site marking completed - Attended
CL1162 | 2021-01-29 | T.V.Kovil | D | Dispenser B side not working | Breakdown | Nepolean | 2021-01-29 | - | On/Off switch terminal changed - Working fine - B side testing: 23.74 Ltrs - Rectified
CL1163 | 2021-01-29 | Dindigul | T | Pump motor conductor alteration | Preventive | Prakash | 2021-01-29 | - | Alteration work completed - Attended
CL1164 | 2021-01-29 | Ariyamangalam | D | D side nozzle LPG leakage | Breakdown | Nepolean | 2021-01-29 | - | Nozzle teeth 4 nos changed - Rectified
CL1165 | 2021-01-29 | Dharmapuri | G | Water drain ballvalve fitting and pipe line leakage testing | Preventive | Prabu | 2021-01-29 | - | Water drain ballvalve fitted and Pipe line leakage test done - Attended
CL1166 | 2021-01-30 | Pudukkottai | T | Unloading ballvalve with ROV leakage | Breakdown | Vigneshwaran | 2021-01-30 | - | Ballvalve nut tightened with teflon and ROV bush tightened - Leakage arrested - Rectified
CL1167 | 2021-02-01 | T.V.Kovil | D | B side not working | Breakdown | Nepolean | 2021-02-01 | - | B side rotary switch replaced - Working fine - Rectified
CL1168 | 2021-02-01 | Palladam | C | ALDS Stamping | Certification | Gowtham | 2021-02-01 | - | Stamping completed - Testing : A side :275.32 B side : 274.12 C side : 389.44 D side : 450.68 Total testing - 1389.56 ltrs - Attended
CL1169 | 2021-02-02 | Sankari | G | Welding work | New Project | Prabu | 2021-02-03 | - | Welding work in process
CL1170 | 2021-02-02 | Ariyamangalam | R | Control panel dispensing air solenoid coil problem | Breakdown | Nepolean | 2021-02-02 | - | Dispensing air solenoid (Master) changed - Working fine - Rectified
CL1171 | 2021-02-03 | Dharmapuri | C | Peso Inspection | New Project | Prabu | 2021-02-03 | - | PESO Inspection completed - Attended
CL1172 | 2021-02-03 | Manapparai | C | DL Stamping work | Certification | Nepolean & Vignesh | 2021-02-03 | - | Stamping completed & PMR completed - Attended
CL1173 | 2021-02-03 | Kodumudi | T | Dispensing motor spider problem | Breakdown | Thirumalaisamy | 2021-02-03 | - | Spider changed - Dispensing and unloading pump grease applied - Working fine - PMR done - Rectified
CL1174 | 2021-02-04 | Vellakovil | D | Low flow cut off problem | Breakdown | Thirumalaisamy | 2021-02-04 | - | High flow low flow valve cleaned- Working fine - Rectified
CL1175 | 2021-02-04 | Bodi | G | Sign board installation | New Project | Kathiresan | 2021-02-04 | - | Sign board installed - Completed
CL1176 | 2021-02-04 | Uthamapalayam | G | Sign board installation | New Project | Kathiresan | 2021-02-04 | - | Sign board installed - Completed
CL1177 | 2021-02-04 | Vadivelan Nagar | T | Dispensing pump spider problem | Breakdown | Suneel Sagar | 2021-02-04 | - | Spider changed -Working fine - Completed
CL1178 | 2021-02-04 | Vadivelan Nagar | A | Automation new software updation | New Project | Madhavan | 2021-02-04 | - | Software updation done - Attended
CL1179 | 2021-02-04 | Madurai | G | Site visit | New Project | Kathiresan | 2021-02-04 | - | Site visit completed
CL1180 | 2021-02-04 | Virudhunagar | G | Compressor air line and electrical line alteration | Preventive | Kathiresan | 2021-02-05 | - | Alteration work completed - Attended
CL1181 | 2021-02-05 | Ariyamangalam | D | D side nozzle testing | Preventive | Nepolean | 2021-02-05 | - | D side nozzle tested - Testing : 5.85 Ltrs - Completed
CL1182 | 2021-02-05 | Mulanur | G | Electrical work and control panel testing | New Project | Chandrasekar & Thirumalaisamy | 2021-02-06 | - | Electrical work and control panel testing completed - Attended
CL1183 | 2021-02-06 | Dindigul | G | Online UPS error | Breakdown | Kathiresan | 2021-02-06 | - | UPS cooling fan dust cleaned - Working fine - Rectified
CL1184 | 2021-02-06 | Bhavani | A | Automation software updation | New Project | Madhavan | 2021-02-06 | - | Software updation done - Attended
CL1185 | 2021-02-06 | Palayam | C | Rule 33 data third party visit | New Project | Thirumalaisamy | 2021-02-06 | - | Third party visit completed
CL1186 | 2021-02-06 | Velachery | D | B side slow delivery problem | Breakdown | Suneel Sagar | 2021-02-06 | - | High flow low flow solenoid valve and excess flow valve cleaned- Working fine - Rectified
CL1187 | 2021-02-07 | Sankari | G | Pipeline Hydro test | New Project | Prabu | 2021-02-07 | - | Pipe line hydro test completed - Attended
CL1188 | 2021-02-08 | Ariyamangalam | G | N2 air machine mouth problem | Breakdown | Nepolean | 2021-02-08 | - | Mouth replaced - Working fine - Rectified
CL1189 | 2021-02-09 | Melur | G | Site visit | New Project | Kathiresan | 2021-02-09 | - | Site visit completed - Tank pit construction completed - Civil work in process - Attended
CL1190 | 2021-02-09 | Kangeyam | G | Fire extinguisher refilling and periodical preventive maintenance | Preventive | Gowtham | 2021-02-09 | - | Fire extinguisher refilling, servicing and PMR done - Completed
CL1191 | 2021-02-10 | Kumbakonam | T | Nitrogen Test | New Project | Chandrasekar & Vignesh | 2021-02-10 | - | Nitrogen (N2) test completed. Testing pressure @ 14kg/cm^2.Pressure held @10kg/cm^2. Automation cable laying completed - Attended
CL1192 | 2021-02-10 | Krishnagiri | R | Control panel dispensing contactor problem | Breakdown | Prabu | 2021-02-10 | - | Dispensing contactor replaced - Working fine - PMR done - Rectified
CL1193 | 2021-02-12 | Dindigul | D | Yenen dispenser program on / off key set changing | Breakdown | Kathiresan | 2021-02-12 | - | Program on / off key set changed - Rectified
CL1194 | 2021-02-12 | Namakkal 1 | G | Unloading training | Preventive | Prabu | 2021-02-12 | - | Unloading training completed - Attended
CL1195 | 2021-02-12 | Palayam | G | Cable laying | New Project | Thirumalaisamy | 2021-02-12 | - | Electrical cable laying completed - GI flat welding in process - Attended
CL1196 | 2021-02-13 | Karur | R | Turbo drive PLC problem | Breakdown | Thirumalaisamy | 2021-02-18 | - | PLC replaced - Working fine - Rectified
CL1197 | 2021-02-14 | Theni | R | Control panel trip light blinking, B nozzle LPG flow problem and A nozzle LPG flow cutoff problem | Breakdown | Nepolean | 2021-02-14 | - | New power card replaced - B side solenoid valve cleaned - A side high flow low flow coil cleaned - Working fine - Rectified
CL1198 | 2021-02-15 | Melur | T | Tank installation | New Project | Chandrasekar & Kathiresan | 2021-02-15 | - | Tank installation and concrete work completed - Attended
CL1199 | 2021-02-15 | Rasipuram | T | Unloading ballvalve leakage | Breakdown | Prabu | 2021-02-15 | - | Ballvalve refitted - Leakage arrested - Rectified
CL1200 | 2021-02-15 | Namakkal 1 | D | Breakaway leakage & Servo stabilizer fuse problem | Breakdown | Prabu | 2021-02-15 | - | Breakaway refitted - Servo stabilizer fuse replaced - Working fine - Rectified
CL1201 | 2021-02-15 | Sankari | C | Rule 33 data, wires and GI flat data collection | New Project | Prabu | 2021-02-15 | - | Data collected - Completed
CL1202 | 2021-02-15 | Vedachandur | T | Tank pit and boundary markings | New Project | Krishna Bhalaji | 2021-02-15 | - | Markings completed
CL1203 | 2021-02-16 | Cantonment | D | Dispenser D side On/Off switch not working | New Project | Nepolean | 2021-02-16 | - | On/off switch changed - Working fine - Rectified
CL1204 | 2021-02-17 | Musiri | G | Boundary marking | New Project | Prakash | 2021-02-17 | - | Boundary marking completed
CL1205 | 2021-02-17 | Namakkal 2 | G | Commissioning work | New Project | Prakash, Madhavan & Kamaraj | 2021-02-17 | - | Commissioning completed with Automation - Attended
CL1206 | 2021-02-17 | Ariyamangalam | D | C side on/off switch not working | Breakdown | Nepolean | 2021-02-17 | - | On/off switch changed - Working fine - Rectified
CL1207 | 2021-02-17 | Ariyamangalam | D | Power card testing on C and D side. | Preventive | Nepolean | 2021-02-17 | - | Power card testing done - Testing: 13.30 Ltrs - Rectified
CL1208 | 2021-02-17 | Namakkal 2 | C | Dispenser Stamping | Certification | Chandrasekar & Vignesh | 2021-02-19 | - | Dispenser stamping completed - Attended
CL1209 | 2021-02-18 | Thanjavur | G | Site marking | New Project | Prakash & Prasanna Narasimmhan | 2021-02-18 | - | Site marking completed - Attended
CL1210 | 2021-02-18 | Mulanur | G | Commissioning work | New Project | Prakash, Chandrasekar & Vignesh | 2021-02-18 | - | Tank purging, unloading & Dispensing pump, Dispenser stamping completed with Automation - Completed
CL1211 | 2021-02-18 | Vadivelan Nagar | T | Dispensing liquid ball valve leakage | Breakdown | Suneel Sagar | 2021-02-18 | - | Ballvalve gland pack leakage arrested - Rectified
CL1212 | 2021-02-18 | Namakkal 2 | G | Pipeline leakage checking | Breakdown | Prabu | 2021-02-18 | - | Pipeline leakage tested - Attended
CL1213 | 2021-02-19 | Virudhunagar | T | Air line alteration & dispensing ROV with ballvalve leakage | Breakdown | Kathiresan | 2021-02-19 | - | PMR done - Airline alteration done and nut tightened to arrest the leakage - Rectified
CL1214 | 2021-02-19 | Namakkal 2 | C | Dispenser calibration & stamping | Certification | Prabu | 2021-02-19 | - | Dispenser stamping completed - Attended
CL1215 | 2021-02-19 | Palladam | D | C side nozzle problem | Breakdown | Gowtham | 2021-02-19 | - | Nozzle hammer replaced - Working fine - Rectified
CL1216 | 2021-02-20 | Mulanur | G | Automation training, pump safety training and pipe leakage testing | Preventive | Thirumalaisamy | 2021-02-20 | - | Automation, pump safety training provided and all pipeline leakage tested - Attended
CL1217 | 2021-02-20 | Velachery | T | Decanting pneumatic solenoid coil problem | Breakdown | Suneel Sagar | 2021-02-20 | - | Pneumatic solenoid coil replaced - Rectified
CL1218 | 2021-02-20 | Sulur | D | A side on / off switch problem & Tank equalizer line leakage | Breakdown | Gowtham | 2021-02-20 | - | NO element replaced - Equalizer line leakage arrested by replacing SS tube along with the fittings
CL1219 | 2021-02-21 | Dharapuram | D | Half meter hose problem | Breakdown | Gowtham | 2021-02-21 | - | Half meter hose replaced - Testing 3 Ltrs - Rectified
CL1220 | 2021-02-22 | Pudukkottai | T | ATG problem & Unloading process cant be done | Breakdown | Nepolean & Kamaraj | 2021-02-22 | - | Software restore done - Unloading process done - PMR done - Rectified
CL1221 | 2021-02-22 | T.V.Kovil | D | A side not working | Breakdown | Vigneshwaran | 2021-02-22 | - | Pulsar card wiring refitted - working fine - Testing: 14.36 Ltrs - Rectified
CL1222 | 2021-02-23 | Avadi | G | Site marking | New Project | Prakash | 2021-02-23 | - | Site marking completed - Attended
CL1223 | 2021-02-23 | Neelambur | T | Tank installation | New Project | Gowtham | 2021-02-23 | - | Tank installation completed - Attended
CL1224 | 2021-02-23 | Namakkal 1 | G | 1 Kva UPS plug point damaged due to power fluctuation & Control panel on light fuse burn out. | Breakdown | Prabu | 2021-02-23 | - | Plug point replaced - Dust cleaned - Control panel on light changed - Rectified
CL1225 | 2021-02-24 | Sulur | D | A side on / off switch problem | Breakdown | Gowtham | 2021-02-24 |  | On/off switch replaced - PMR Completed - Ballvalve and ROV leakage arrested by applying teflon - Rectified
CL1226 | 2021-02-24 | Ariyamangalam | D | B side nozzle teeth problem | Breakdown | Nepolean | 2021-02-24 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL1227 | 2021-02-25 | Melur | T | Tank hydro test | New Project | Chandrasekar & Vignesh | 2021-02-25 | - | Hydro test completed - Testing pressure at 29 kg/cm'2 - Attended
CL1228 | 2021-02-26 | Namakkal 2 | D | One side not working | Breakdown | Prabu, Nepolean & Thirumalaisamy | 2021-02-27 | - | DP valve spring adjusted - Under observation - Testing - A side : 61.39 Ltrs; B side : 10 Ltrs - Rectified
CL1229 | 2021-02-26 | Bodi | D | LPG leakage under dipenser | Breakdown | Kathiresan | 2021-02-26 | - | Liquid ballvalve leakage and unloading ball valve leakage arrested by tightening the bolts - Working fine - Rectified
CL1230 | 2021-02-26 | Cantonment | D | Dispensing 5 mtr hose damaged and unloading motor belt problem | New Project | Chandrasekar | 2021-02-26 | - | Unloading motor belt - 2 nos replaced and A side dispensing hose replaced - Testing 4.55Ltrs - Working fine - Rectified
CL1231 | 2021-02-27 | Neelambur | G | Electrical and non electrical earth provisioning | New Project | Gowtham | 2021-02-27 | - | Electrical and non electrical earth provisioning has made and Tank kept with water for hydro test - Attended
CL1232 | 2021-02-28 | Palayam | T | Nitrogen Test | New Project | Thirumalaisamy | 2021-02-28 | - | N2 test completed - N2 pressure tested @14.5 kg/cm^2.Pressure holded @ 10.5 kg/cm^2 - Attended
CL1233 | 2021-03-01 | Kumbakonam | C | Peso Inspection | Certification | Prakash & Venkatesh | 2021-03-01 | - | PESO Inspection completed - Attended
CL1234 | 2021-03-01 | Melur | T | CP Installation | New Project | Kathiresan | 2021-03-01 | - | CP installation completed - Attended
CL1235 | 2021-03-01 | Karur | C | Rule 19 work | Certification | Chandrasekar, Thirumalaisamy & Dharmesh | 2021-03-03 | 31 Hours | Rule 19 work completed - Sales started - Attended
CL1236 | 2021-03-01 | Rasipuram | R | Control panel RYB indicator problem | Breakdown | Prabu | 2021-03-01 | - | New indicators changed - Nozzle serviced - Working fine - Rectified
CL1237 | 2021-03-02 | Perundurai | R | Control panel is not booting & A side keypad problem | Breakdown | Gowtham | 2021-03-02 | - | Fill point emergency switch stuck up released - Booting done - A side new keypad changed - Rectified
CL1238 | 2021-03-02 | Theni | D | Dispenser amount keypad problem | Breakdown | Kathiresan | 2021-03-02 | - | Power card to mother board connector and amount keypad serviced and refitted - Rectified
CL1239 | 2021-03-03 | Krishnagiri | C | Rule 19 work | Certification | Chandrasekar, Vignesh & Prabu | 2021-03-06 | 30 Hours | Tank hydro test completed - Rule 19 Completed - Sales started - Completed
CL1240 | 2021-03-03 | Palladam | D | D side nozzle teeth problem | Breakdown | Gowtham | 2021-03-03 | - | Nozzle teeth 4 nos replaced - Rectified
CL1241 | 2021-03-03 | Avadi | T | Tank installation | New Project | Suneel Sagar | 2021-03-03 | - | Tank installed - Completed
CL1242 | 2021-03-04 | Kangeyam | D | Kalvacha dispenser problem | Breakdown | Gowtham | 2021-03-04 | - | Motherboard wiring termination reassembled - Working fine - Testing C side: 17.56 Ltrs - D Side : 24.14 Ltrs - Rectified
CL1243 | 2021-03-04 | Ariyamangalam | D | A side nozzle leakage | Breakdown | Nepolean | 2021-03-04 | - | New nozzle teeth 4 nos replaced - Working fine - Rectified
CL1244 | 2021-03-04 | Karur | T | New CP Installation | Breakdown | Thirumalaisamy | 2021-03-04 | - | New CP installed - Completed
CL1245 | 2021-03-04 | Cantonment | G | Servo Stabilizer problem | Breakdown | Nepolean | 2021-03-04 | - | New servo stabilizer installed - Working fine - Rectified
CL1246 | 2021-03-04 | KR Gases | T | Tank hydro test, SRV, Unloading hose and NDT testing | Preventive | Prakash | 2021-03-04 | - | Tank hydro test, SRV, Unloading hose and NDT testing completed - Attended
CL1247 | 2021-03-05 | Dharapuram | C | Periodical preventive maintenance | Preventive | Gowtham | 2021-03-05 | - | PMR done - Everything working fine - Attended
CL1248 | 2021-03-05 | Vellakovil | D | Dispenser slow delivery problem | Breakdown | Thirumalaisamy | 2021-03-05 | - | Dispenser both side High flow and low flow valve cleaned - Rectified
CL1249 | 2021-03-05 | Udumalpet | C | Periodical preventive maintenance | Preventive | Gowtham | 2021-03-05 | - | PMR done - Everything working fine - Attended
CL1250 | 2021-03-05 | T.V.Kovil | G | Turbo drive problem | Breakdown | Nepolean | 2021-03-05 | - | Turbo Drive Line directed -Relay refitted - Rectified
CL1251 | 2021-03-07 | Krishnagiri | T | CP Installation | Preventive | Prabu | 2021-03-07 | - | New cathodic protection installed - Working fine - EB room to Tank area PVC pipe and pneumatic air line changed - Completed
CL1252 | 2021-03-07 | Mulanur | G | Unloading process | Preventive | Thirumalaisamy | 2021-03-07 | - | Unloading completed safely with trained person - Attended
CL1253 | 2021-03-08 | Kumbakonam | G | Unloading and commissioning | New Project | Chandrasekar & Kamaraj | 2021-03-09 | - | Outlet commissioned with automation - Completed
CL1254 | 2021-03-08 | T.V.Kovil | D | D side nozzle problem | Breakdown | Vigneshwaran | 2021-03-08 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL1255 | 2021-03-08 | Cantonment | D | A side not working | Breakdown | Nepolean | 2021-03-08 | - | On/ off switch changed and limit switch adjusted - Rectified
CL1256 | 2021-03-09 | Vedachandur | T | Tank pit marking | New Project | Kathiresan | 2021-03-09 | - | Tank pit marking and dispenser area marking completed - Attended
CL1257 | 2021-03-09 | Musiri | G | Floor filling level fixing and tank pit marking | New Project | Prakash, Nepolean & Dharmesh | 2021-03-09 | - | Floor filling Level fixed and tank pit marking done - Completed
CL1258 | 2021-03-09 | Cantonment | D | A side on/off switch problem | Breakdown | Nepolean | 2021-03-09 | - | New switch replaced - Working fine - Rectified
CL1259 | 2021-03-09 | Kumbakonam | C | Stamping & Calibration | Certification | Krishna Bhalaji & Chandrasekar | 2021-03-09 | - | Stamping and Calibration completed - Attended
CL1260 | 2021-03-09 | Perundurai | C | Stamping work | Certification | Thirumalaisamy | 2021-03-09 | - | Stamping completed - Attended
CL1261 | 2021-03-10 | T.V.Kovil | R | Turbo drive MOL problem | Breakdown | Nepolean | 2021-03-10 | - | MOL released by resetting - Rectified
CL1262 | 2021-03-11 | Neelambur | T | Tank hydrotest | Breakdown | Gowtham | 2021-03-11 | - | Tank hydro test completed - Motor bed , pipe line trench and dispenser island marking completed - Completed
CL1263 | 2021-03-11 | Uthamasolapuram | T | DPS switch SS tube leakage | Breakdown | Prabu | 2021-03-11 | - | Refitted and teflon applied - Leakage arrested - Rectified
CL1264 | 2021-03-12 | Avadi | T | CP Installation | New Project | Prakash & Suneel Sagar | 2021-03-12 | - | CP installation completed - Attended
CL1265 | 2021-03-12 | Attur | C | Dispenser stamping and calibration | Certification | Prabu | 2021-03-12 | - | Attur station dispenser stamping completed. K factors A side 101000 B side 103000 Total testing A side 110.00lit B side 160.21lit Total 270.21lit - Completed
CL1266 | 2021-03-12 | Kangeyam | D | Kalvacha dispenser problem | Breakdown | Gowtham | 2021-03-13 | 60 hours | Wiring recorrected - Kept under observation - Rectified
CL1267 | 2021-03-12 | Thuraiyur | D | One side limit switch problem | Breakdown | Nepolean | 2021-03-12 | - | Limit switch adjusted - Rectified
CL1268 | 2021-03-12 | Krishnagiri | T | Above ground motor pipeline welding & Hydrotest | Preventive | Prabu | 2021-03-13 | - | Pipe line welding & Hydro test completed - Attended
CL1269 | 2021-03-13 | Neelambur | T | CP Installation | New Project | Gowtham | 2021-03-13 | - | CP installation completed - Attended
CL1270 | 2021-03-13 | Ariyamangalam | D | C side nozzle LPG leakage | Breakdown | Nepolean | 2021-03-13 | - | C side service nozzle replaced - Working fine - Testing : 0.82 Ltrs - Rectified
CL1271 | 2021-03-14 | Musiri | T | Tank installation | New Project | Prakash | 2021-03-14 | - | Tank installation & Foundation concrete work completed - Attended
CL1272 | 2021-03-15 | Cantonment | G | N2 air machine hose burst out | Breakdown | Chandrasekar | 2021-03-15 | - | New air hose replaced - Rectified
CL1273 | 2021-03-15 | Dindigul | D | 3/4" excess flow valve damaged | Breakdown | Kathiresan | 2021-03-19 | - | B side new excess flow valve replaced - Working fine - Rectified
CL1274 | 2021-03-16 | Ariyamangalam | D | D side nozzle teeth problem | Breakdown | Nepolean | 2021-03-16 | - | Nozzle teetj 4 nos replaced - Working fine - Rectified
CL1275 | 2021-03-16 | Vedachandur | G | Site visit | New Project | Kathiresan | 2021-03-16 | - | Site visit completed
CL1276 | 2021-03-17 | Kangeyam | D | Kalvacha dispenser display problem | Breakdown | Nepolean & Gowtham | 2021-03-18 | - | Display cable replaced - Working fine - Rectified
CL1277 | 2021-03-17 | Madurai | G | Tank pit retaining valve installation | New Project | Prakash | 2021-03-17 | - | Tank pit retaining valve installed - Completed
CL1278 | 2021-03-17 | Vedachandur | G | Site marking | New Project | Prakash, Kathiresan & Vignesh | 2021-03-17 | - | As per drawing, Canopy foundation & office room markings completed - Attended
CL1279 | 2021-03-17 | Aravakurichi | D | Dispenser slow delivery due to A side 3/4" Excess flow valve broken | Breakdown | Thirumalaisamy | 2021-03-26 | - | Excess flow valve replaced - Working fine - Testing 5.53 Ltrs - Rectified
CL1280 | 2021-03-18 | Salem | C | Dispenser calibration & stamping | Certification | Prabu | 2021-03-18 | - | Calibration and stamping completed - K Factor A side 101000 B side 103530 Testing A side 100lit B side 100lit Total testing 200lit calibration A side 10lit= 10.04 B side 10lit = 10.01 - Completed
CL1281 | 2021-03-19 | Attur | T | Unloading pump leakage | Breakdown | Prabu | 2021-03-19 | - | Unloading pump leakage arrested by applied new grease packing - Rectified
CL1282 | 2021-03-19 | Tanjore | T | Tank installation | New Project | Chandrasekar & Vignesh | 2021-03-19 | - | Tank installed and foundation concrete work completed - Attended
CL1283 | 2021-03-19 | Udumalpet | T | Tank 1 - STP liquid ball valve LPG leakage | Breakdown | Nepolean | 2021-03-19 | - | Leakage arrested by changing new gaskets - Rectified
CL1284 | 2021-03-19 | Udumalpet | D | Yenen dispenser offline UPS problem | Breakdown | Nepolean | 2021-03-19 | - | New offline UPS fixed - Working Fine - Rectified
CL1285 | 2021-03-19 | Mulanur | T | Unloading hose leakage | Breakdown | Thirumalaisamy | 2021-03-19 | - | Leakage arrested by adjusting the seating position of the adapters - Rectified
CL1286 | 2021-03-20 | Palladam | D | C side and D side LPG slow delivery and cutoff problem | Breakdown | Nepolean | 2021-03-20 | - | High flow low flow valve and excess flow valve cleaned - A side high flow low flow valve and DP valve cleaned - Working fine - Rectified
CL1287 | 2021-03-20 | Attur | T | New unloading pump concrete work & Installation | Preventive | Prabu | 2021-03-21 | - | Unloading pump installed and tank unloading completed safely - Attended
CL1288 | 2021-03-20 | Vedachandur | T | Tank pit construction | New Project | Kathiresan | 2021-03-20 | - | Tank pit work & Canopy piller measurement checked - completed
CL1289 | 2021-03-20 | Cantonment | D | A side yenen nozzle leakage | Breakdown | Nepolean | 2021-03-20 | - | Nozzle teeth 4 nos changed - Working fine - Nozzle fixed date: 23.01.2021 Opening Reading: 9203155.56 Closing Reading:9322502.61- Rectified
CL1290 | 2021-03-20 | Aravakurichi | A | Automation application updation | New Project | Madhavan & Thirumalaisamy | 2021-03-20 | - | Automation application updated - Completed
CL1291 | 2021-03-22 | Mulanur | G | Unloading training | Preventive | Thirumalaisamy | 2021-03-22 | - | Unloading training completed - Attended
CL1292 | 2021-03-23 | Madurai | T | Tank installation | New Project | Kathiresan | 2021-03-24 | - | Tank installation and concrete work completed - Attended
CL1293 | 2021-03-23 | Dharmapuri | G | Compressor motor and starter replacment | Breakdown | Prabu | 2021-03-23 | - | 2 HP compressor motor and starter replaced - Compressor working fine - Rectified
CL1294 | 2021-03-23 | Vedachandur | T | Tank installation | New Project | Thirumalaisamy | 2021-03-23 | - | Tank installation and concrete work completed - Attended
CL1295 | 2021-03-23 | Manapparai | G | New mass flow meter testing | Preventive | Prakash | 2021-03-23 | - | Mass flow meter testing done - Working fine - Completed
CL1296 | 2021-03-23 | Cantonment | G | Tyre inflator not working | Breakdown | Nepolean | 2021-03-23 | - | Tyre inflator mouth replaced - Working fine - Rectified
CL1297 | 2021-03-23 | Namakkal 2 | G | Compressor motor and starter replacment | Breakdown | Prabu | 2021-03-23 | - | 2 HP compressor motor and starter replaced - Compressor working fine - Rectified
CL1298 | 2021-03-24 | Thuraiyur | D | B side neutral problem | Breakdown | Nepolean | 2021-03-24 | - | New rotary switch changed - Dispenser working good - Rectified
CL1299 | 2021-03-24 | Cantonment | D | Dispenser C side and D side nozzle problem | Breakdown | Chandrasekar | 2021-03-24 | - | C and D side nozzle teeth replaced - Working fine - Rectified
CL1300 | 2021-03-24 | Avadi | G | Pipeline hydro test | New Project | Suneel Sagar | 2021-03-24 | - | Pipeline hydro test completed - Found satisfactory - Attended
CL1301 | 2021-03-24 | Kodumudi | D | B side nozzle and keypad problem | Breakdown | Thirumalaisamy | 2021-03-24 | - | Nozzle teeth and latch spring changed and keypad changed - Working fine - Rectified
CL1302 | 2021-03-25 | Madurai | G | Site marking and tank data collection | New Project | Kathiresan | 2021-03-25 | - | Dispensing and decanting pump motor bed marking and canopy piller marking completed - Tank data collected - Attended
CL1303 | 2021-03-27 | Kodungaiyur | D | A side nozzle problem | Breakdown | Suneel Sagar | 2021-03-27 | - | A side new classic nozzle replaced - Rectified
CL1304 | 2021-03-27 | Namakkal 1 | G | Compressor switch and servo stabilizer problem | Breakdown | Prabu | 2021-03-27 | 1 Hour | Compressor starter wires reconnected - Stabilizer fuse changed - Working fine - Rectified
CL1305 | 2021-03-27 | T.V.Kovil | A | Automation software updation | Preventive | Madhavan | 2021-03-27 | - | Automation software updated -Completed
CL1306 | 2021-03-28 | Cantonment | A | Automation software updation | Preventive | Madhavan | 2021-03-28 | - | Automation software updated -Completed
CL1307 | 2021-03-28 | Ariyamangalam | A | Automation software updation | Preventive | Madhavan | 2021-03-28 | - | Automation software updated -Completed
CL1308 | 2021-03-28 | Hosur | A | Automation software updation | Preventive | Madhavan | 2021-03-28 | - | Automation software updated -Completed
CL1309 | 2021-03-29 | Tirunelveli | C | Stamping work | Certification | Nepolean & Kathiresan | 2021-03-29 | - | Stamping work completed - Attended
CL1310 | 2021-03-29 | Musiri | T | Tank hydro test | New Project | Chandrasekear | 2021-03-29 | - | Tank hydro test completed - Pressure held at 29 kg/cm^2 - Attended
CL1311 | 2021-03-29 | Dharmapuri | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1312 | 2021-03-29 | Tharamangalam | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1313 | 2021-03-29 | Bhavani | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1314 | 2021-03-29 | Rasipuram | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1315 | 2021-03-29 | Kodungaiyur | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1316 | 2021-03-29 | Kumbakonam | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1317 | 2021-03-29 | Virudhachalam | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1318 | 2021-03-29 | Namakkal 1 | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1319 | 2021-03-29 | Namakkal 2 | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1320 | 2021-03-29 | Krishnagiri | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1321 | 2021-03-29 | Uthamacholapuram | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1322 | 2021-03-29 | Bodi | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1323 | 2021-03-29 | Uthamapalayam | A | Automation software updation | Preventive | Madhavan | 2021-03-29 | - | Automation software updated -Completed
CL1324 | 2021-03-30 | Ariyamangalam | G | New mass flow meter testing | Preventive | Nepolean | 2021-03-30 | - | New mass flow meter tested - D side testing : 264.19 ltrs - Completed
CL1325 | 2021-03-31 | Ariyamangalam | D | D side nozzle 2 nos testing | Preventive | Nepolean | 2021-03-31 | - | Nozzle testing done - Testing : 4.26 Ltrs - Completed
CL1326 | 2021-04-01 | Udumalpet | C | Dispenser calibration work | Certification | Chandrasekar & Gowtham | 2021-04-02 | - | Calibration completed at both side - Attended
CL1327 | 2021-04-01 | Sankari | G | Electrical work | New Project | Prabu | 2021-04-01 | - | Electrical work completed - Attended
CL1328 | 2021-04-02 | Bhavani | G | UPS continous beep sounding due to fan stuck | Breakdown | Prabu | 2021-04-02 | - | UPS cleaned and fan released - Rectified
CL1329 | 2021-04-02 | Vedachandur | T | Tank hydro test | New Project | Kathiresan | 2021-04-02 | - | Hydro test completed - Testing pressure at 29 kg/cm'2 - Attended
CL1330 | 2021-04-02 | Mettupalayam | C | Dispenser calibration work | Certification | Chandrasekar & Gowtham | 2021-04-03 | - | Calibration completed at both side - Dispensing motor cooling impeller replaced - Attended
CL1331 | 2021-04-02 | Avinashi | T | Tank 1 unloading problem | Breakdown | Prabu | 2021-04-02 | - | HLA damaged wire replaced - Working fine - Unloading completed - Rectified
CL1332 | 2021-04-03 | Tanjore | T | Tank hydro test | New Project | Vignesh & Kamaraj | 2021-04-03 | - | Tank hydro test completed - Pressure held at 28 kg/cm^2 - Attended
CL1333 | 2021-04-03 | Krishnagiri | R | MOL problem | Breakdown | Prabu | 2021-04-03 | - | Turbo Drive wiring recorrected and reset done - Rectified
CL1334 | 2021-04-03 | Vedachandur | T | CP Installation | New Project | Kathiresan | 2021-04-03 | - | CP installation completed - Dispenser and decating motor bed marking completed - Attended
CL1335 | 2021-04-03 | Ariyamangalam | R | Turbo drive PLC testing | Preventive | Nepolean | 2021-04-03 | - | PLC tested - Working fine - Completed
CL1336 | 2021-04-03 | Sulur | C | Dispenser calibration work | Certification | Chandrasekar | 2021-04-03 | - | Calibration completed at both side - Attended
CL1337 | 2021-04-04 | Velachery | C | Quarterly preventive maintenace | Preventive | Suneel Sagar | 2021-04-04 | - | PM Report done - Found Satisfactory - Attended
CL1338 | 2021-04-04 | Vadivelan Nagar | C | Quarterly preventive maintenace | Preventive | Suneel Sagar | 2021-04-04 | - | PM Report done - Found Satisfactory - Attended
CL1339 | 2021-04-04 | Karur | C | Dispenser calibration work | Certification | Chandrasekar | 2021-04-04 | - | Calibration completed at both side - Attended
CL1340 | 2021-04-05 | Pudukkottai | G | Compressor air leakage | Breakdown | Nepolean | 2021-04-05 | - | Safety valve serviced - Pressure switch has to be replaced - Temporarily rectified
CL1341 | 2021-04-05 | Namakkal 1 | G | Servo Stabilizer problem | Breakdown | Prabu | 2021-04-05 | - | Fuse replaced - Working fine - Rectified
CL1342 | 2021-04-05 | Dindigul | D | A side nozzle leakage | Breakdown | Kathiresan | 2021-04-05 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL1343 | 2021-04-06 | Kodumudi | T | Unloading liquid hose adapter leakage | Breakdown | Thirumalaisamy | 2021-04-06 | - | Adapter leakage arrested by applying teflon and anabond paste - Rectifed
CL1344 | 2021-04-06 | Cantonment | C | Batchen dispenser calibration | Certification | Nepolean | 2021-04-06 | - | New "K" factor changed for Batchen Dispenser. A side : 100300 B side : 100100 Quantity checked : A side 10 ltr - 10.01 B side 10 ltr - 10.01. Testing Litres: A side - 406.56 ltrs B side - 367.28 ltrs Calibration done - Completed
CL1345 | 2021-04-07 | Dindigul | C | Calibration work | Certification | Nepolean & Kathiresan | 2021-04-08 | - | Calibration completed at both side - Attended
CL1346 | 2021-04-07 | Theni | C | Calibration work | Certification | Nepolean & Kathiresan | 2021-04-08 | - | Calibration completed at both side - Attended
CL1347 | 2021-04-08 | Madurai | T | Tank hydro test | New Project | Nepolean & Kathiresan | 2021-04-08 | - | Tank hydro test completed - Pressure held in 29 kg/Cm^2 - Attended
CL1348 | 2021-04-08 | Cantonment | G | Oil air hose damaged | Breakdown | Ravichandran | 2021-04-08 | - | New air hose adapter clip changed - Rectified
CL1349 | 2021-04-08 | Madurai | G | Site visit | New Project | Prakash & Venkatesh | 2021-04-08 | - | Site visit completed - Attended
CL1350 | 2021-04-08 | Tirunelveli | D | Batchen dispenser B side metering unit leakage due to blue bearing damaged | Breakdown | Nepolean & Kathiresan | 2021-04-09 | - | B side Bearing and oil seal kit changed - Kept under observation - Rectified
CL1351 | 2021-04-09 | Madurai | T | CP Installation | New Project | Chandrasekar & Vignesh | 2021-04-09 | - | CP installation completed - Attended
CL1352 | 2021-04-09 | Erode | D | Nozzle teeth damage and PM Report | Breakdown | Thirumalaisamy | 2021-04-09 | - | A side nozzle teeth replaced - Air compressor oil changed and PMR done - Rectified
CL1353 | 2021-04-09 | Palladam | D | Old nozzles servicing | Preventive | Gowtham | 2021-04-09 | - | 3 nozzles servicing done - Testing : 6 Ltrs - Completed
CL1354 | 2021-04-10 | Virudhunagar | C | Dispenser calibration work | Certification | Nepolean | 2021-04-10 | - | Calibration completed at both side - Attended
CL1355 | 2021-04-10 | Dindigul | G | Online UPS error 42 | Breakdown | Nepolean | 2021-04-10 | - | UPS restarted - Fan has to be replaced - Temporarily rectified
CL1356 | 2021-04-10 | Vadivelan Nagar | D | Dispenser 1 emergency switch cable loose contact | Breakdown | Suneel Sagar | 2021-04-10 | - | Emergency switch cables recorrected - C side nozzle serviced - Rectified
CL1357 | 2021-04-12 | Uthamasolapuram | T | Tank area liquid ROV leakage | Breakdown | Prabu | 2021-04-12 | - | Teflon tape applied and refitted - Leakage arrested - Rectified
CL1358 | 2021-04-13 | Virudhunagar | G | Turbo drive problem and new stabilizer installation | Breakdown | Kathiresan | 2021-04-13 | - | Turbo drive PCB new (MOV) ceramic capacitor soldered & Stablizer installation completed - Completed
CL1359 | 2021-04-13 | Namakkal 2 | T | Dispensing motor noise & Pressure Gauge Broken | Breakdown | Prabu | 2021-04-13 | - | Bypass Valve & Equaliser valve adjusted. Pressure gauge replaced - Rectified
CL1360 | 14-04-2021 | Ariyamangalam | T | Control panel to Tank area air hose damage | Breakdown | Nepolean | 14-04-2021 | - | New Pnemautic hose replaced - Rectified
CL1361 | 15-04-2021 | Palladam | D | D side nozzle servicing | Preventive | Gowtham | 15-04-2021 | - | Nozzle service done - Nozzle teeth replaced - Testing : 0.98 Ltrs - Attended
CL1362 | 15-04-2021 | Pudukkottai | G | Compressor shaft valve problem | Breakdown | Kamaraj | 15-04-2021 | - | Air line bypass with another compressor - Compressor pressure switch has to be replaced - Rectified
CL1363 | 15-04-2021 | Theni | D | LPG leakage under dipenser | Breakdown | Kathiresan | 15-04-2021 | - | Liquid line valve stem leakage arrested by tightening - Vapour line ballvalve with ROV to be replaced - Rectified
CL1364 | 15-04-2021 | Erode | D | Dispenser vapour ROV problem | Breakdown | Thirumalaisamy | 15-04-2021 | - | ROV leakage arrested by tughtening the nut of the stem of the ballvalve - Rectified
CL1365 | 16-04-2021 | Musiri | T | Excess flow valve installation | New Project | Vignesh | 2021-04-16 | - | Excess flow valve installation on Tank flange done - Completed
CL1366 | 16-04-2021 | Melur | G | Site marking | New Project | Krishna Balaji | 16-04-2021 | - | Site marking completed - Attended
CL1367 | 18-04-2021 | Tharamangalam | D | Nozzle leakage & ROV leakage | Breakdown | Prabu | 18-04-2021 | - | Nozzle teeth replaced for two nozzles - Nozzle mount cleaned - ROV leakage arrested by applying teflon - Rectified
CL1368 | 19-04-2021 | Velachery | C | Calibration work | Certification | Suneel Sagar | 19-04-2021 | - | Calibration completed at both side - Attended
CL1369 | 19-04-2021 | Cantonment | D | B side nozzle problem | Breakdown | Nepolean | 19-04-2021 | - | Nozzle teeth replaced - Working fine - Rectified
CL1370 | 19-04-2021 | Tharamangalam | G | DOL starter power problem - MCB automatically switch off due to over load | Breakdown | Prabu | 19-04-2021 | - | MCB replaced - DOL starter working good - Rectified
CL1371 | 20-04-2021 | Madurai | G | Mechanical work & Civil work | New Project | Kathiresan | 2021-04-24 | - | Mechanical work completed - Earth chamber and earth pipeline installed - Attended
CL1372 | 20-04-2021 | Musiri | G | Cable and GI flat measuring | New Project | Vignesh | 20-04-2021 | - | Electrical cable & GI flat measuring completed. Welding work in process - Attended
CL1373 | 20-04-2021 | Madurai | G | Site visit | New Project | Prakash & Chandrasekar | 20-04-2021 | - | Site visit completed - Pipeline and welding instructions given - Attended
CL1374 | 20-04-2021 | Vadivelan Nagar | C | Calibration work | Certification | Suneel Sagar | 20-04-2021 | - | Calibration completed at both side - Attended
CL1375 | 20-04-2021 | Rasipuram | T | Dispensing motor spider problem & Nozzle problem | Breakdown | Prabu | 20-04-2021 | - | Spider replaced - 1 no Nozzle serviced - Rectified
CL1376 | 20-04-2021 | Thuraiyur | C | Stamping work | Certification | Nepolean | 20-04-2021 | - | Stamping work completed - Attended
CL1377 | 21-04-2021 | Neelambur | T | Tank cleaning and excess flow valve fitting | New Project | Gowtham | 21-04-2021 | - | Tank cleaning completed & Excess flow valve installation process going on - Attended
CL1378 | 21-04-2021 | Avadi | T | Nitrogen Test | New Project | Suneel Sagar | 2021-04-21 | - | Nitrogen test, Electrical work and canopy work completed - Attended
CL1379 | 2021-04-22 | Neelambur | T | Tank flange installation | New Project | Gowtham | 2021-04-22 | - | Tank both flanges installed - Completed
CL1380 | 2021-04-22 | Theni | D | Dispenser not working due to ROV failure | Breakdown | Kathiresan | 2021-04-22 | 5 Hours | Dispenser ROV not working properly. Temporarily adjusted - ROV needs to be replaced
CL1381 | 2021-04-22 | Musiri | G | Pipeline hydro test | New Project | Vignesh | 2021-04-22 | - | Pipeline hydro test completed - Pressure Held at 48 Kg/cm^2- Found satisfactory - Attended
CL1382 | 2021-04-23 | Ariyamangalam | C | Batchen dispenser calibration | Certification | Nepolean | 2021-04-23 | - | New "K" factor for Batchen Dispenser. A side : 100180 B side : 100143 Quantity checked: A side 10 lit - 10.02 B side 10 lit - 10.02 Testing Litres: A side - 307.03 B side - 351.18 Total - 658.21 ltrs Calibration done - Completed
CL1383 | 2021-04-23 | Bathlagundu | G | Site civil marking | New Project | Krishnabalaji & Kathiresan | 2021-04-23 | - | Boundaries, Tank pit and boundaries marking completed - Attended
CL1384 | 2021-04-23 | Neelambur | G | Pipeline erection | New Project | Gowtham | 2021-04-23 | - | Motor beds extended - Erecton process completed - Attended
CL1385 | 2021-04-23 | Ariyamangalam | A | Automation software checking | Preventive | Madhavan | 2021-04-23 | - | Software testing done - Testing Litres - A nozzle - 2.19 liters B nozzle - 2.12 liters Total testing - 4.31 liters - Completed
CL1386 | 2021-04-23 | Ariyamangalam | D | A side nozzle problem | Breakdown | Nepolean | 2021-04-23 | - | Service nozzle replaced - Working fine - Rectified
CL1387 | 2021-04-23 | Ariyamangalam | C | Dispenser calibration work | Certification | Nepolean | 2021-04-23 | - | C and D side calibration completed - C side testing : 517.48 lit D side testing : 112.85 lit - Attended
CL1388 | 2021-04-23 | Ariyamangalam | C | Batchen dispenser calibration | Certification | Nepolean | 2021-04-23 | - | Calibration completed A side : 100180 B side :. 100143 C side : 99766 D side :. 105500 Quantity checked: A side 10 lit : 10.02 B side 10 lit : 10.02 C side. 10 lit : 10.00 D side 10 lit : 9.97 Attended
CL1389 | 2021-04-24 | Manapparai | T | Dispensing motor love jaw coupling problem | Breakdown | Nepolean & Kamaraj | 2021-04-24 | - | New spider replaced - Dispensing motor working fine - Rectified
CL1390 | 2021-04-26 | Dindigul | T | Decanting pump motor V belt damaged | Breakdown | Kathiresan | 2021-04-26 | - | New V belt 2 nos replaced - Working fine - Rectified
CL1391 | 2021-04-27 | Melur | G | Site marking and civil work | New Project | Kathiresan | 2021-04-27 | - | Dispenser, Canopy piller, Dispensing bed, decanting bed and earth chamber pit marking work completed - Attended
CL1392 | 2021-04-27 | Namakkal 1 | T | Tank area ROV problem & B side keypad problem | Breakdown | Prabu | 2021-04-27 | - | ROV and ballvalve replaced - B side keypad replaced - Tank area to EB room pneumatic hose replaced - Working fine - Rectified
CL1393 | 2021-04-27 | Paramathivelur | D | Slow delivery problem due to insufficient dispensing pump delivery pressure | Breakdown | Thirumalaisamy | 2021-04-27 | - | Equalizer valve adjusted - slow delivery arrested - PMR done - Rectified
CL1394 | 2021-04-27 | Pudukkottai | T | Unloading problem | Breakdown | Nepolean | 2021-04-27 | - | Vapour balancing done - Unloading completed - Rectified
CL1395 | 2021-04-27 | T.V.Kovil | D | Dispenser C side nozzle problem | Breakdown | Vigneshwaran | 2021-04-27 | - | C side nozzle teeth replaced - Working fine - Rectified
CL1396 | 2021-04-27 | Mettupalayam | G | Unloading training, safety measure instruction and automation training with mobile operation | Preventive | Gowtham | 2021-04-27 | - | Training completed - Attended
CL1397 | 2021-04-27 | Ariyamangalam | A | Separate automation circuir control implementation & C side hose changing | New Project | Madhavan | 2021-04-27 | - | Separate automation circuir control for C and D side implemented - Keeping under observation - C side Hose changing and testing done - Testing : 43.90 Ltrs - Completed
CL1398 | 2021-04-28 | Virudhunagar | A | New mother board installation, Calibration & Automation installation | New Project | Madhavan, Vigneshwaran & Kathiresan | 2021-04-28 | 6 hours | Yenen new motherboard replaced - Sales stopped due tomother board to display card connector with 15 pin port cable problem - Cable replaced - Voltage scanner serviced - working fine - Rectified
CL1399 | 2021-04-28 | Vedachandur | T | Tank cleaning and flanges installation | New Project | Thirumalaisamy | 2021-04-28 | - | Tank cleaned - Flanges, Pipline and excess flow valve installed - Completed
CL1400 | 2021-04-28 | Avinashi | G | Unloading training | Preventive | Gowtham | 2021-04-28 | - | ALDS unloading training completed - Attended
CL1401 | 2021-04-28 | Manapparai | T | Dispensing motor spider problem | Breakdown | Dharmesh | 2021-04-28 | - | Dispenser motor spider replaced - Working fine - Rectified
CL1402 | 2021-04-29 | Avinashi | R | HLA wire damage & ROV leakage | Breakdown | Gowtham | 2021-04-29 | - | Tank 1 HLA cable reassembled - ROV LPG leakage arrested by tightening the stem - Rectified
CL1403 | 2021-04-29 | Virudhunagar | A | Automation installation | New Project | Madhavan | 2021-04-29 | - | Automation installed and data available in KR admin app - Completed
CL1404 | 2021-04-29 | Neelambur | G | Unloading pipeline welding | New Project | Gowtham | 2021-04-29 | - | Unloading pipeline welding completed - Dispensing line welding in process - Attended
CL1405 | 2021-04-30 | Madurai | G | Pipeline hydro test | New Project | Kathiresan | 2021-04-30 | - | Pipeline hydro testing completed holding pressure 48Kg/cm^2 - Rule 33 data collected - Civil work in process - Attended
CL1406 | 2021-04-30 | Neelambur | G | Pipeline erection | New Project | Gowtham | 2021-04-30 | - | Dispensing pipeline welding completed partially - Erection in process - Attended
CL1407 | 2021-04-30 | Vedachandur | G | Erection and site visit | New Project | Thirumalaisamy | 2021-04-30 | - | Erection completed - Civil and mechanical work in process - Attended
CL1408 | 2021-05-01 | Neelambur | G | Welding work | New Project | Gowtham | 2021-05-01 | - | Welding work completed - Attended
CL1409 | 2021-05-01 | Dindigul | G | Online UPS error 45 occurred | Breakdown | Kathiresan | 2021-05-01 | - | Cooling fan cleaned and dust removed - Working fine - Rectified
CL1410 | 2021-05-01 | Aravakurichi | D | A nozzle 3/4" excess flow valve blocked | Breakdown | Thirumalaisamy | 2021-05-01 | - | Fluid flow valve adjusted - Working fine - Testing : 19.18 Ltrs - Rectified
CL1411 | 2021-05-03 | Theni | T | Unloading pump LPG leakage | Breakdown | Nepolean & Kathiresan | 2021-05-05 | - | Dispenser bottom vapour line 1/2" ROV with ballvalve replaced - Unloading pump O rings replaced - LPG leakage arrested - Rectified
CL1412 | 2021-05-03 | Vedachandur | G | Pipeline hydro test | New Project | Thirumalaisamy | 2021-05-03 | - | Pipeline hydro test completed - Pressure Held at 48 Kg/cm^2- Found satisfactory - Attended
CL1413 | 2021-05-03 | Neelambur | G | Pipeline hydro test | New Project | Gowtham | 2021-05-03 | - | Pipeline hydro test completed - Pressure Held at 48 Kg/cm^2- Found satisfactory - Attended
CL1414 | 2021-05-03 | Cantonment | D | C side nozzle problem | Breakdown | Kamaraj | 2021-05-03 | - | Nozzle teeth 4 nos changed - Working good - Rectified
CL1415 | 2021-05-03 | Ariyamangalam | A | Automation test run software checking | New Project | Madhavan | 2021-05-03 | - | Automation Test Run software checked. Testing liters C nozzle - 14.69 liters - Completed
CL1416 | 2021-05-04 | Virudhunagar | R | Control panel short circuit | Breakdown | Kathiresan | 2021-05-04 | - | Control panel solar line removed - Connected only to EB and Generator - Working fine - Rectified
CL1417 | 2021-05-04 | Neelambur | G | Site visit | New Project | Gowtham | 2021-05-04 | - | Pipeline assembling work in process - Attended
CL1418 | 2021-05-04 | Namakkal 1 | G | Tyre inflator display problem | Breakdown | Prabu | 2021-05-04 | - | Display replaced - Working fine - Rectified
CL1419 | 2021-05-04 | Vedachandur | C | Rule 33 data collection | New Project | Thirumalaisamy | 2021-05-04 | - | Rule 33 data collected - Electrical cable and GI flat measurement done - Rectified
CL1420 | 2021-05-05 | Neelambur | G | Site visit | New Project | Gowtham | 2021-05-05 | - | Welding work and pipeline assembling completed - Attended
CL1421 | 2021-05-06 | Neelambur | G | Welding work | New Project | Gowtham | 2021-05-06 | - | Pipeline support and dispensing pump motor shed welding work completed - Completed
CL1422 | 2021-05-07 | Neelambur | G | Welding work | New Project | Gowtham | 2021-05-07 | - | welding work completed earth flat welding partially completed - Attended
CL1423 | 2021-05-07 | Sulur | R | Unloading solenoid coil problem | Breakdown | Gowtham | 2021-05-07 | - | Unloading coil magnatizer replaced - Unloading completed - Rectified
CL1424 | 2021-05-08 | Virudhunagar | D | Dispenser cutoff problem & STP pressure drop | Breakdown | Kathiresan | 2021-05-08 | - | Dispenser omran relay reconnected - Control Panel PLC wiring reconnected - Testing : 342.59 Ltrs - Rectified
CL1425 | 2021-05-08 | Kodungaiyur | R | CPU issue | Breakdown | Madhavan | 2021-05-14 | - | A new CPU replaced - Rectified
CL1426 | 2021-05-08 | Neelambur | G | Pipeline erection | New Project | Gowtham | 2021-05-08 | - | Pipeline erection completed - Attended
CL1427 | 2021-05-14 | Vedachandur | G | ALDS pending civil work, Site visit & Rule 33 data collection | New Project | Kathiresan | 2021-05-14 | - | Civil work completed - Rule 33 data collected - Attended
CL1428 | 2021-05-16 | T.V.Kovil | G | Oil dispenser nozzle leakage | Breakdown | Nepolean | 2021-05-16 | - | Oil dispenser nozzle spring replaced & serviced - Testing : 6.50 Ltrs - Rectified
CL1429 | 2021-05-19 | Cantonment | A | Automation system maintenance | Preventive | Madhavan | 2021-05-19 | - | System CPU cleaned and Rebooted - Working fine - Attended
CL1430 | 2021-05-19 | Ariyamangalam | A | Automation system maintenance | Preventive | Madhavan | 2021-05-19 | - | System CPU cleaned and Rebooted - Working fine - Attended
CL1431 | 2021-05-19 | T.V.Kovil | A | Automation system maintenance | Preventive | Madhavan | 2021-05-19 | - | System CPU cleaned and Rebooted - Working fine - Attended
CL1432 | 2021-05-19 | Hosur | A | Automation system maintenance | Preventive | Madhavan | 2021-05-19 | - | System CPU cleaned and Rebooted - Working fine - Attended
CL1433 | 2021-05-19 | Dindigul | T | Control panel to Tank area air hose damage | Breakdown | Kathiresan | 2021-05-19 | - | Pneumatic hose replaced - Rectified
CL1434 | 2021-05-24 | Tharamangalam | G | UPS not working | Breakdown | Prabu | 2021-05-24 | - | UPS fan stuck up released - Cleaned - Working fine - Rectified
CL1435 | 2021-05-24 | Kodumudi | R | Control panel fuse damaged | Breakdown | Thirumalaisamy | 2021-05-31 | - | 1A fuse replaced - Panel working fine - Rectified
CL1436 | 2021-05-29 | Paramathivelur | A | CPU (Motherboard) issue | Breakdown | Madhavan | 2021-06-04 | - | New CPU replaced with the old hard disk - Rectified
CL1437 | 2021-06-04 | Namakkal 2 | G | Online UPS not working properly | Breakdown | Prabu | 2021-06-04 | - | Power backup issue - Reset done - Working fine - Rectified
CL1438 | 2021-06-05 | Kodumudi | G | Offline UPS power backup problem | Breakdown | Thirumalaisamy | 2021-06-07 | - | Offline UPS battery replaced - Working fine - PMR done - Rectified
CL1439 | 2021-06-07 | Namakkal 2 | T | Dispensing motor suction problem | Breakdown | Prabu | 2021-06-08 | - | Equalizer valve adjusted -Stabilizer reprogrammed - Working good - Rectified
CL1440 | 2021-06-08 | Avadi | G | Dispenser stamping and outlet opening | New Project | Chandrasekar & Dharmesh | 2021-06-14 | - | Stamping completed and Opened to public. K factor is 10000 A. Testing. 193.52 litre B. Testing. 140.80 litre C. Testing. 161.02 litre D. Testing. 152.46 litre Total Testing. 647.80 litre - Completed
CL1441 | 2021-06-08 | T.V.Kovil | D | B side nozzle problem | Breakdown | Nepolean | 2021-06-08 | - | Nozzle teeth 4 nos replaced - Rectified
CL1442 | 2021-06-10 | Avadi | C | Calibration and automation | New Project | Prakash | 2021-06-11 | - | Calibration and automation completed - Attended
CL1443 | 2021-06-10 | Musiri | G | Chemical earthing | New Project | Vignesh | 2021-06-11 | - | Chemical earthing work completed - Completed
CL1444 | 2021-06-11 | Avinashi | T | Tank 1 MOL problem | Breakdown | Gowtham | 2021-06-11 | - | Bypass valve cleaned - Wiring adjusted - Under observation - Rectified
CL1445 | 2021-06-11 | Tharamangalam | D | Dispenser error 10 | Breakdown | Prabu | 2021-06-11 | - | Dispenser EEPROM IC 39,IC38 connected properly - Rectified
CL1446 | 2021-06-12 | Pudukkottai | G | Compressor problem | Breakdown | Nepolean & Vignesh | 2021-06-12 | - | Damaged pressure switch replaced - N2 machine 6mm air tube replaced - Rectified
CL1447 | 2021-06-12 | Tharamangalam | A | CPU fan issue Outlet running in offline mode due to CPU fan issue | Breakdown | Madhavan | 2021-07-22 | - | CPU fan replaced - Working fine - Outlet automation back online - Rectified
CL1448 | 2021-06-13 | Avinashi | G | Servo Stabilizer problem | Breakdown | Gowtham | 2021-06-13 | - | Arranged for servo stablizer service person - Will be rectified the next day
CL1449 | 2021-06-13 | Musiri | G | N2 unloading & Test | New Project | Vignesh | 2021-06-13 | - | Nitrogen test completed Tested at 15kg/cm^2. Pressure held at 10kg/cm^2 - Attended
CL1450 | 2021-06-14 | Vedachandur | G | Site Visit | New Project | Kathiresan & Vignesh | 2021-06-14 | - | GI flat welding work on process electrical work will be done the next day - Attended
CL1451 | 2021-06-14 | T.V.Kovil | D | A side nozzle not working | Breakdown | Nepolean | 2021-06-14 | - | Dust cleaned - Testing : 1.06 Ltrs - Rectified
CL1452 | 2021-06-14 | Ariyamangalam | D | Batchen dispenser tube light not working | Breakdown | Nepolean | 2021-06-14 | - | New tube light 2 nos changed - Rectified
CL1453 | 2021-06-14 | T.V.Kovil | D | D side nozzle teeth problem | Breakdown | Nepolean | 2021-06-14 | - | Nozzle teeth 4 nos changed - Rectified
CL1454 | 2021-06-14 | Ayothiyapattinam | G | Civil marking | New Project | Prabu | 2021-06-14 | - | Site civil marking completed - Attended
CL1455 | 2021-06-14 | Cantonment | A | Mother board testing | Preventive | Prakash & Madhavan | 2021-06-14 | - | Testing completed - C side: 21.15 Ltrs - Attended
CL1456 | 2021-06-15 | Vedachandur | G | Earth GI flat welding and electrical work | New Project | Kathiresan | 2021-06-15 | - | Welding and electrical work completed - Attended
CL1457 | 2021-06-16 | Pudukkottai | T | Dispensing motor ALPG slow delivery | Breakdown | Nepolean & Vignesh | 2021-06-16 | - | Dispensing motor by pass valve cleaned - Working fine - Kept under observation - Rectified
CL1458 | 2021-06-16 | Melur | G | Site visit and marking | New Project | Kathiresan | 2021-06-16 | - | Pipe line trench and tank area earth chamber marking work completed
CL1459 | 2021-06-16 | Ayothiyapattinam | G | Site visti | New Project | Prabu | 2021-06-16 | - | Tank unloading done and civil work in process - Attended
CL1460 | 2021-06-17 | Attur | G | Unloading trainig and PMR work | Preventive | Prabu | 2021-06-17 | - | Unloading trainig completed - PMR Completed - Nozzle serviced - Attended
CL1461 | 2021-06-17 | Saravanampatty | T | Unloading problem & PMR Work | Breakdown | Gowtham | 2021-06-17 | - | PMR done - Rochester stuck up released - ATG Veedor Root display serviced with the concerned service person - Liquid and vapour ROV leakage arrested by tightening - Rectified
CL1462 | 2021-06-17 | Madurai | G | Site visit | New Project | Prakash & Kathiresan | 2021-06-17 | - | Site visit completed - Attended
CL1463 | 2021-06-17 | T.V.Kovil | A | Automation maintenance | Preventive | Madhavan | 2021-06-17 | - | Maintenance done - Back online - Completed
CL1464 | 2021-06-17 | Ariyamangalam | A | Nozzle testing | Preventive | Nepolean | 2021-06-17 | - | Testing completed - B side: 1.3 Ltrs - Attended
CL1465 | 2021-06-18 | Dharmapuri | T | Tank ROV leakage | Breakdown | Prabu | 2021-06-18 | - | PMR done - ROV leakage arrested by tightening - Rectified
CL1466 | 2021-06-18 | Vedachandur | G | Electrical work | New Project | Kathiresan | 2021-06-18 | - | Electrical work completed - Attended
CL1467 | 2021-06-19 | Melur | G | Mechanical work | New Project | Kathiresan | 2021-06-19 | - | Tank flanges and excess flow valve fitment completed - Tank cleaning in process - Attended
CL1468 | 2021-06-19 | Pudukkottai | T | Dispensing pump suction problem | Breakdown | Prakash & Nepolean | 2021-06-19 | - | Pump suction adjusted - Pipeline to be adjusted at the time of Rule 19 - Temporarily rectified
CL1469 | 2021-06-19 | Musiri | G | Mechanical work | New Project | Madhavan, Vigneshwaran & Kamaraj | 2021-06-19 | - | Mechanical work completed - Automation installation is pending - Attended
CL1470 | 2021-06-19 | Madurai | G | EB room and cable chamber marking | New Project | Kathiresan | 2021-06-19 | - | EB room and cable chamber marking compeleted - Canopy work in process - Attended
CL1471 | 2021-06-20 | Bathlagundu | G | Site tank pit and civil work marking | New Project | Kathiresan | 2021-06-20 | - | Civil boundaries and compount marking completed - Tank pit marking is pending - Attended
CL1472 | 2021-06-20 | Melur | G | Earth pipe installation | New Project | Kathiresan | 2021-06-20 | - | 4 Earth pipe installation completed - Attended
CL1473 | 2021-06-21 | Madurai | G | Electrical and civil work | New Project | Kathiresan | 2021-06-22 | - | Civil work and canopy work in process - Attended
CL1474 | 2021-06-21 | Aravakurichi | A | Outlet running in offline mode due to CPU fan issue | Breakdown | Thirumalaisamy | 2021-07-16 | - | CPU serviced and test run made at HO. Outlet back online - Rectified
CL1475 | 2021-06-21 | Musiri | A | Automation installation | New Project | Madhavan, Chandrasekar & Vigneshwaran | 2021-06-21 | - | Dispensing motor, Decanting motor, electrical, mechanical work test check done. Dispenser brought online - Completed
CL1476 | 2021-06-22 | Pudukkottai | T | Unloading process | Preventive | Nepolean & Kamaraj | 2021-06-22 | - | Decanting completed safely - Attended
CL1477 | 2021-06-22 | Attur | D | B side nozzle leakage | Breakdown | Prabu | 2021-06-22 | - | Spare nozzle replaced - Working fine - Testing B side: 0.85 Ltrs - Rectified
CL1478 | 2021-06-22 | Musiri | C | Peso Inspection | New Project | Prakash | 2021-06-22 | - | PESO Inspection, Commissioning and calibration completed - Attended
CL1479 | 2021-06-22 | Krishnagiri | R | Control panel automatic tripping | Breakdown | Prabu | 2021-06-22 | - | Control panel solenoid replaced - EB line adjusted - Working fine - Kept under observation - Rectified
CL1480 | 2021-06-22 | Velachery | C | Preventive Maintenance Report | Preventive | Suneel Sagar | 2021-06-22 | - | PMR done - Completed
CL1481 | 2021-06-23 | Madurai | G | Electrical pending work | New Project | Kathiresan | 2021-06-23 | - | canopy work & tank area electrical cable laying completed - Attended
CL1482 | 2021-06-23 | Musiri | C | Stamping and automation | Certification | Krishnabhalaji & Madhavan | 2021-06-23 | - | Stamping completed - Automation data available in KR Admin app - Opened to public - Completed
CL1483 | 2021-06-23 | T.V.Kovil | C | Stamping work | Certification | Nepolean | 2021-06-23 | - | Stamping done - Completed
CL1484 | 2021-06-24 | Tanjore | G | Site visit | New Project | Prakash | 2021-06-24 | - | Civil marking completed - Attended
CL1485 | 2021-06-24 | Bathlagundu | G | Site visit | New Project | Kathiresan | 2021-06-24 | - | Site visit completed - Attended
CL1486 | 2021-06-24 | Palayam | A | Automation installation and mechanical work | New Project | Madhavan & Vignesh | 2021-06-24 | - | Mechanical work and automation installation done - Completed
CL1487 | 2021-06-24 | Chengalpattu | C | Stamping work | Certification | Suneel Sagar | 2021-06-24 | - | Stamping done - Completed
CL1488 | 2021-06-24 | Madurai | G | Civil and electrical work | New Project | Kathiresan | 2021-06-24 | - | Cable laying completed - Civil work in process - Attended
CL1489 | 2021-06-24 | Neelambur | G | Electrical work | New Project | Gowtham | 2021-06-25 | - | Cable laying completed - Termination work in process - Attended
CL1490 | 2021-06-24 | Cantonment | C | Calibration work & Stamping | Certification | Nepolean | 2021-06-25 | - | C & D Nozzle calibration done and stamping completed C side old k factor : 10300 D side old k factor: 10300 C side OB : 2251892.59 C side CL : 2252247.11 D side OB : 2247703.93 D side CL : 2247990.90 C side Testing : 354.52 D side Testing : 286.97 C side new k factor: 10170 D side new k factor: 10150. C side 10Lit = 10.003 lit D side 10 Lit = 10.00 lit
CL1491 | 2021-06-25 | Paramathivelur | C | Calibration work & Stamping | Certification | Thirumalaisamy, Vignesh & Kamaraj | 2021-06-25 | - | A & B Nozzle. A side old k factor : 10000 B side old k factor: 10000 A side Opening Reading : 1326807.26 A side Closing Reading : 1326992.78 B side Opening Reading : 1200384.75 B side Closing Reading : 1200747.03 A side Testing : 185.52 B side Testing : 362.28 A side new k factor: 10000 B side new k factor: 10000. A side 10litters = 9.99 litters B side 10 Litters = 9.99 litters
CL1492 | 2021-06-25 | Vadivelan Nagar | G | Diesel generator AVR complaint | Breakdown | Suneel Sagar | 2021-06-25 | - | New AVR replaced - Lighting fluctuations still there - Kept under observation - Partially rectified
CL1493 | 2021-06-25 | Palayam | G | Electrical work | New Project | Thirumalaisamy | 2021-06-25 | - | Electrical work completed - Attended
CL1494 | 2021-06-26 | Neelambur | G | Electrical work | New Project | Gowtham | 2021-06-27 | - | Electrical work partially completed - Attended
CL1495 | 2021-06-26 | Melur | G | Mechanical work | New Project | Kathiresan | 2021-06-26 | - | Mechanical work completed - Pipeline hydro test completed - Pressure held at 48Kg/cm^2 - Attended
CL1496 | 2021-06-26 | Palayam | G | Commissioning work | New Project | Prakash & Chandrasekar | 2021-06-26 | - | Commissioning completed with Automation - Attended
CL1497 | 2021-06-26 | Cantonment | D | A side nozzle leakage | Breakdown | Nepolean | 2021-06-26 | - | Nozzle theeth replaced - Working fine - Rectified
CL1498 | 2021-06-27 | Palayam | A | Automation mobile app updation | New Project | Madhavan | 2021-06-27 | - | Automation data available in KR admin mobile app - Completed
CL1499 | 2021-06-28 | Madurai | G | Civil work | New Project | Kathiresan | 2021-06-28 | - | Civil work in process - Tank area paver blocks work completed - Attended
CL1500 | 2021-06-28 | T.V.Kovil | D | Batchen dispenser on-off switch problem | Breakdown | Vigneshwaran | 2021-06-28 | - | New on off switch replaced - Working good - Rectified
CL1501 | 2021-06-29 | Melur | G | Electrical work | New Project | Kathiresan | 2021-06-29 | - | Welding and fitting completed - Electrical cable laying is in process - Attended
CL1502 | 2021-06-29 | Palayam | C | Calibration and stamping | New Project | Thirumalaisamy | 2021-06-29 | - | A & B Nozzle Calibrated and stamping done A side old k factor : 10150 B side old k factor: 10150 A side Opening Reading : 704.05 A side Closing Reading : 1051.13 B side Opening Reading : 578.00 B side Closing Reading : 879.70 A side Testing : 347.08 B side Testing : 301.70 A side new k factor: 10000 B side new k factor: 10000. A side 10litters = 10.06 litters B side 10 Litters = 10.06 litters
CL1503 | 2021-06-30 | Udumalpet | T | Tank 1 STP not working | Breakdown | Gowtham | 2021-06-30 | - | Kept under observation -Attended
CL1504 | 2021-06-30 | Palladam | G | Fire Extinguisher service | Preventive | Gowtham | 2021-06-30 | - | Fire extinguisher service done and DCP changed for both 10kg and 70 kg. Next renewal/inspection date 28.06.2022 - Attended
CL1505 | 2021-06-30 | Avinashi | G | Fire Extinguisher service | Preventive | Gowtham | 2021-06-30 | - | Fire extinguisher service done and DCP changed for both 10kg and 70 kg. Next renewal/inspection date 20.06.2023 - Attended
CL1506 | 2021-06-30 | T.V.Kovil | A | Dispenser offline due to automation maintenance | Preventive | Madhavan | 2021-06-30 | - | Automation maintenance completed - Dispenser back online - Completed
CL1507 | 2021-06-30 | Cantonment | A | Dispenser offline due to automation maintenance | Preventive | Prasath | 2021-06-30 | - | Automation maintenance completed - Dispenser back online - Completed
CL1508 | 2021-07-01 | Melur | G | Electrical work | New Project | Kathiresan | 2021-07-01 | - | GI flat welding work and electrical work completed - Attended
CL1509 | 2021-07-01 | Ariyamangalam | D | B and D side nozzle lock damaged & Nitrogen machine air mouth damaged | Breakdown | Nepolean | 2021-07-01 | - | Both side nozzle locks replaced - N2 machine air mouth replaced - Working fine - Rectified
CL1510 | 2021-07-02 | Uthamasolapuram | R | Control panel not working | Breakdown | Prabu | 2021-07-02 | - | Panel transformer glass fuse broken - Fuse replaced - Rectified
CL1511 | 2021-07-02 | Virudhunagar | T | STP motor run mode not working | Breakdown | Kathiresan | 2021-07-02 | - | Current Voltage Transformer output voltaged drop - New power connection installed - Leakage test done - PMR done - Working fine - Testing : 110 Ltrs - Rectified
CL1512 | 2021-07-02 | Hosur | D | B side nozzle problem | Breakdown | Suresh | 2021-07-02 | - | Nozzle teeth 4 nos replaced - Rectified
CL1513 | 2021-07-03 | Madurai | G | Civil work | New Project | Kathiresan | 2021-07-03 | - | Civil work and paver work in process - Tank area fencing completed - Attended
CL1514 | 2021-07-03 | Musiri | T | Dispensing motor slow delivery due to suction problem | Breakdown | Nepolean & Vignesh | 2021-07-03 | - | Pump impeller replaced - Bypass valve cleaned - Kept under observation -Attended
CL1515 | 2021-07-03 | Madurai | G | Site visit | New Project | Prakash | 2021-07-03 | - | Site visit completed - Attended
CL1516 | 2021-07-03 | Palayam | G | Servo Stabilizer installation | New Project | Thirumalaisamy | 2021-07-03 | - | Installation completed - Attended
CL1517 | 2021-07-03 | Krishnagiri | G | Fire Extinguisher service | Preventive | Prabu | 2021-07-03 | - | fire extinguisher service done and DCP changed for both 10kg and 70 kg - Completed
CL1518 | 2021-07-03 | Palladam | T | Unloading ROV pneumatic hose damaged | Breakdown | Gowtham | 2021-07-03 | - | Pneumatic hose replaced - Rectified
CL1519 | 2021-07-04 | Thuraiyur | D | Dispenser hose leakage | Breakdown | Kamaraj | 2021-07-04 | - | 5m dispensing hose replaced - Testing : 0.92 ltrs - Working fine - Rectified
CL1520 | 2021-07-05 | Paramathivelur | D | Control panel master solenoid coil air leakage | Breakdown | Thirumalaisamy | 2021-07-05 | - | New solenoid replaced - Soft starter installed - Working fine - Rectified
CL1521 | 2021-07-05 | Namakkal 2 | T | Tank area liquid line ball valve leakage | Breakdown | Prabu | 2021-07-05 | - | Tank area liquid line ball valve leakage arrested by applying teflon and tightening the bolts - Rectified
CL1522 | 2021-07-05 | Udumalpet | T | Tank 1 STP problem | Breakdown | Gowtham | 2021-07-05 | - | STP stops working anonymously - Kept under observation to find the root cause of the problem - Attended
CL1523 | 2021-07-05 | T.V.Kovil | D | Dispenser B side nozzle lock problem | Breakdown | Vignesh | 2021-07-05 | - | Spare nozzle replaced - Working fine - Testing B side: 1.21 Ltrs - Rectified
CL1524 | 2021-07-05 | Avadi | R | Control panel internal wiring loose contact | Breakdown | Suneel Sagar | 2021-07-05 | - | Wiring loose contacts adjusted - ATG to automation cable laying completed - Attended
CL1525 | 2021-07-07 | Ramnad | T | Tank installation | New Project | Prakash, Prasath & Ravikumar | 2021-07-07 | - | Tank installation done - Rectified
CL1526 | 2021-07-07 | Velachery | C | Rule 19 work | Certification | Suneel Sagar, Chandrasekar & Kamaraj | 2021-07-11 | - | Rule 19 work completed - Sales started - Attended
CL1527 | 2021-07-07 | Ayothiyapattinam | G | Site visit | New Project | Prabu | 2021-07-07 | - | Civil work in process - Attended
CL1528 | 2021-07-07 | Karur | D | D side nozzle problem | Breakdown | Thirumalaisamy | 2021-07-07 | - | Nozzle teeth replaced - Working fine - Rectified
CL1529 | 2021-07-07 | T.V.Kovil | D | Dispenser D side nozzle leakage | Breakdown | Vignesh | 2021-07-07 | - | Spare nozzle replaced - Testing : 0.97 Ltrs - Rectified
CL1530 | 2021-07-07 | Ariyamangalam | G | N2 machine output air hose fittings problem | Breakdown | Nepolean | 2021-07-07 | - | Air hose fittings replaced - Rectified
CL1531 | 2021-07-07 | Thanjavur | T | Main flange fitting | New Project | Nepolean & Dharmesh | 2021-07-07 | - | Main flange fitting done - Attended
CL1532 | 2021-07-07 | Kodumudi | G | Control panel trips when running in Genset mode | Breakdown | Thirumalaisamy | 2021-08-07 | - | Genset and Stabilizer service persons attended and adjusted the cutoff voltage - Working fine - Rectified
CL1533 | 2021-07-08 | Madurai | A | EB and genset cable laying, Automation installation and electrical work | New Project | Kathiresan, Dharmesh & Vignesh | 2021-07-11 | - | Electrical work, Pavors work completed - N2 test completed at the pressure of 14.5kg/cm^2 - Canopy and facia work completed - Attended
CL1534 | 2021-07-08 | Ariyamangalam | A | Batchen dispenser going offline due to automation maintenance | Preventive | Madhavan | 2021-07-09 | - | Maintenance done - Back online - Testing B side : 1.23 ltrs - Completed
CL1535 | 2021-07-09 | Avinashi | C | Stamping work | Certification | Gowtham | 2021-07-09 | - | Dispenser stamping completed for both dispensers - Attended
CL1536 | 2021-07-11 | Karur | D | Dispenser on/off switch problem and ROV with ballvalve LPG leakage | Breakdown | Thirumalaisamy | 2021-07-11 | - | Batchen dispenser on/off side changed both side - Key actuator replaced - ROV with ball valve lpg leakage arrested by tightening the bolts - Rectified
CL1537 | 2021-07-11 | Avadi | T | ATG configuration | Breakdown | Suneel Sagar, Chandrasekar & Kamaraj | 2021-07-11 | - | ATG configuration, above ground motor alignment and spider replaced - Rectified
CL1538 | 2021-07-12 | Tharamangalam | T | Liquid line ballvalve leakage | Breakdown | Prabu | 2021-07-12 | - | Leakage arrested by tighening the bolt nut - Nozzle serviced - Working fine - Rectified
CL1539 | 2021-07-12 | Avadi | T | Dispensing motor base plate thread re taping work and realignment | Breakdown | Suneel Sagar | 2021-07-12 | - | Dispensing motor base plate thread re taping work and realignment completed with the help of corken service engineer now dispensing motor performance is satisfactory. This misalignment and wrong threading happened at factory assembly and problem acknowledged by corken service engineer - Rectified
CL1540 | 2021-07-13 | Sankari | G | Civil work | New Project | Prabu | 2021-07-14 | - | Paver block work completed - N2 test completed - Tested at 14.5 Kg/cm^2 - Pressure held at 11kg/cm^2 - Painting work in process - Attended
CL1541 | 2021-07-13 | Chengalpattu | C | Yenen dispenser calibration | Certification | Suneel Sagar, Chandrasekar & Kamaraj | 2021-07-13 | - | Yenen dispenser calibrated, dispenser display outside glass changed both sides and unloading vapour acme coupling changed - Batchen dispenser decommissioned - Attended
CL1542 | 2021-07-13 | Madurai | C | PESO final inspection | Certification | Prakash | 2021-07-13 | - | PESO final inspection completed - Attended
CL1543 | 2021-07-14 | Melur | G | Site Visit & Rule 33 data collection | New Project | Kathiresan | 2021-07-14 | - | Dispenser island civil work completed - Rule 33 data collected - Attended
CL1544 | 2021-07-14 | Rasipuram | A | Offline due to CPU booting and fan issue | Breakdown | Madhavan | 2021-09-14 | - | Dispenser A side nozzle teeth and trigger changed - UPS fan replaced and serviced and connected - Outlet back online - Rectified
CL1545 | 2021-07-14 | Ayothiyapattinam | T | Tank installation | New Project | Prakash & Dharmesh | 2021-07-15 | - | Tank installation completed - Attended
CL1546 | 2021-07-14 | Sankari | C | Site inspection & Online UPS Servo Stabilizer installation | Certification | Prakash & Dharmesh | 2021-07-14 | - | Site inspection & Online UPS Servo Stabilizer installation completed - Attended
CL1547 | 2021-07-14 | Vellakovil | T | Control panel trips while dispensing motor running | Breakdown | Thirumalaisamy | 2021-07-14 | - | 1kva online UPS fan has to be replaced by consul - Informed to Consul service engineers - Soft starter to be installed - Attended
CL1548 | 2021-07-15 | Kumbakonam | T | Decanting process, decanting training and sign board fixing work | Preventive | Nepolean, Vignesh & Prasanna Narasimhan | 2021-07-15 | - | Decanting process, decanting training and sign board fixing work completed
CL1549 | 2021-07-15 | Erode | T | Tank area pneumatic hose air leakage | Breakdown | Thirumalaisamy | 2021-07-15 | - | EB room to Tank area pneumatic line hose replaced - ROV with ballvalve leakage arrested by tightenening the bolts - B side nozzle teeth replaced - PMR done - Completed
CL1550 | 2021-07-15 | Ariyamangalam | A | Batchen dispenser going offline due to automation maintenance | Preventive | Madhavan | 2021-07-15 | - | Maintenance done - Dispenser back online - Attended
CL1551 | 2021-07-16 | Madurai | A | Automation & Control Panel testing | New Project | Kathiresan, Chandrasekar & Vignesh | 2021-07-16 | - | Automation installed and dispenser connected online - Control panel testing completed - Attended
CL1552 | 2021-07-16 | Cantonment | D | C side nozzle problem | Breakdown | Kamaraj | 2021-07-16 | - | Nozzle teeth 4nos replaced - Working fine - Rectified
CL1553 | 2021-07-17 | Mettupalayam | A | General visit and automation system position replacing | Breakdown | Gowtham | 2021-07-17 | - | Automation monitor and CPU position changed and outlet visit completed - attended
CL1554 | 2021-07-17 | T.V.Kovil | A | Yenen dispenser going offline due to automation maintenance | Preventive | Madhavan | 2021-07-17 | - | Maintenance done - Dispenser back online - Attended
CL1555 | 2021-07-18 | Ramnad | C | Rule 33 inspection work | Certification | Chandrasekar & Kamaraj | 2021-07-18 | - | Rule 33 third party inspection completed - Attended
CL1556 | 2021-07-18 | Madurai | C | Rule 33 inspection work | Certification | Chandrasekar, Kathiresan & Kamaraj | 2021-07-18 | - | Rule 33 third party inspection completed - Attended
CL1557 | 2021-07-18 | Melur | C | Rule 33 inspection work | Certification | Chandrasekar & Kamaraj | 2021-07-18 | - | Rule 33 third party inspection completed - Attended
CL1558 | 2021-07-19 | Thanjavur | C | Rule 33 inspection work | Certification | Chandrasekar & Kamaraj | 2021-07-19 | - | Rule 33 third party inspection completed - Attended
CL1559 | 2021-07-19 | Madurai | G | Commissioning & stamping work | New Project | Prakash & Kathiresan | 2021-07-21 | - | Outlet bollard & steps work completed - Tank purgind and unloading completed - Stamping and calibration done - Outlet is open to public - Attended
CL1560 | 2021-07-19 | Mulanur | G | Online UPS - Error 56 | Breakdown | Thirumalaisamy | 2021-07-19 | - | Online UPS (Error 56 failur) complaint reported to Motish Power Solutions. The supply to the computer now goes from offline UPS.Automated CPU and fan place changed(12U rack to nearby monitor).PMR completed - Attended
CL1561 | 2021-07-19 | Vedachandur | C | Rule 33 inspection work | Certification | Chandrasekar & Kamaraj | 2021-07-19 | - | Rule 33 third party inspection completed - Attended
CL1562 | 2021-07-19 | Ariyamangalam | D | C and D side nozzle problem | Breakdown | Nepolean | 2021-07-19 | - | Nozzle teeth changed for both nozzles - Working fine - Rectified
CL1563 | 2021-07-19 | Neelambur | C | Rule 33 inspection work | Certification | Chandrasekar, Gowtham & Kamaraj | 2021-07-19 | - | Rule 33 third party inspection completed - Attended
CL1564 | 2021-07-20 | Ayothiyapattinam | C | Rule 33 inspection work | Certification | Chandrasekar, Prabu & Kamaraj | 2021-07-20 | - | Rule 33 third party inspection completed - Attended
CL1565 | 2021-07-20 | T.V.Kovil | G | Compressor oil changing and unloading point earth clamps changing | Preventive | Vigneshwaran | 2021-07-20 | - | Oil changed in both compressors - Earth clamps replaced - Completed
CL1566 | 2021-07-20 | Madurai | A | Automation installation | New Project | Madhavan | 2021-07-20 | - | Automation online and data available in KR admin app - Completed
CL1567 | 2021-07-21 | Neelambur | G | Site visit | New Project | Gowtham | 2021-07-21 | - | ATG well welding completed - Attended
CL1568 | 2021-07-22 | Perundurai | A | CPU fan issue Outlet running in offline mode due to CPU fan issue | Breakdown | Thirumalaisamy | 2021-08-28 | - | CPU serviced - Automation maintenance done - Dispensing line pneumatic hose replaced - Rectified
CL1569 | 2021-07-22 | Neelambur | G | Nitrogen testing work | New Project | Gowtham | 2021-07-23 | - | N2 test (tested @14.5 kg/cm3) completed - Pressure held @ 11 kg/cm3 - Attended
CL1570 | 2021-07-22 | Virudhunagar | D | A nozzle not working | Breakdown | Kathiresan | 2021-07-22 | - | A side high flow low flow solenoid valve cleaned - B side spare nozzle replaced - Working fine - Testing : A side - 6.15 Ltrs; B side - 0.95 Ltrs - Rectified
CL1571 | 2021-07-22 | Hosur | G | Tyre inflator air hose damaged | Breakdown | Prabu | 2021-07-22 | - | New Polyurethane Flexible Pneumatic Hose 10 Meters changed - Rectified
CL1572 | 2021-07-23 | Melur | G | Earthing work | New Project | Kathiresan | 2021-07-23 | - | Earthing work completed - Attended
CL1573 | 2021-07-23 | Kodumudi | D | A side nozzle problem | Breakdown | Thirumalaisamy | 2021-07-23 | - | A side nozzle teeth replaced - Working fine - Rectified
CL1574 | 2021-07-23 | Ayothiyapattinam | T | Tank hydro test | New Project | Prabu | 2021-07-23 | - | Hydro test completed - Testing pressure - 28 kg/cm'2 - Attended
CL1575 | 2021-07-23 | Bhavani | T | Dispensing motor problem | Breakdown | Prabu | 2021-07-23 | - | Dispensing motor damaged spider replaced - Tank area pneumatic hose replaced - Rectified
CL1576 | 2021-07-23 | T.V.Kovil | D | Batchen dispenser A nozzle problem | Breakdown | Vignesh | 2021-07-23 | - | Nozzle teeth 4 nos replaced - Rectified
CL1577 | 2021-07-23 | Virudhunagar | T | Dispenser mother board problem | Breakdown | Kathiresan | 2021-07-23 | - | 1.5 amps fuse worn out - To be replaced - Rectified temporarily
CL1578 | 2021-07-23 | Vellakovil | G | Fire extinguisher hose damaged | Breakdown | Thirumalaisamy | 2021-07-23 | - | Fire extinguisher 70 kg hose 2 nos replaced - Rectified
CL1579 | 2021-07-23 | Avadi | T | Dipensing pump alignment & impeller condition checking | Breakdown | Suneel Sagar | 2021-07-23 | - | Impeller few teeth damaged - Reassembled with a same one - To be replaced with new impeller - Temporarily rectified
CL1580 | 2021-07-24 | Madurai | G | Tyre inflator installation and front elevation name board installation | New Project | Kathiresan | 2021-07-24 | - | N2 machine installation done - Complete leakage testing done - Working satisfactory - Attended
CL1581 | 2021-07-24 | Cantonment | D | D side nozzle problem | Breakdown | Kamaraj | 2021-07-24 | - | Nozzle teeth 4 nos replaced - Rectified
CL1582 | 2021-07-25 | Ayothiyapattinam | T | CP Installation | New Project | Prabu | 2021-07-25 | - | CP installation completed - Attended
CL1583 | 2021-07-25 | Dharapuram | T | ACME adapter replacement | Breakdown | Gowtham | 2021-07-25 | - | ACME adapter replaced in vapour line - PMR done - Testing: 110 Ltrs - Rectified
CL1584 | 2021-07-26 | Madurai | G | Oil dispenser and compressor installation | New Project | Kathiresan | 2021-07-28 | - | Oil dispenser and compressor installation completed - Attended
CL1585 | 2021-07-26 | Attur | G | Above ground motor bed and additional dispenser bed civil work | New Project | Prabu | 2021-07-27 | - | Civil work completed - Attended
CL1586 | 2021-07-27 | Neelambur | C | PESO final inspection, Commissioning, Stamping and Outlet opening | Certification | Prakash, Gowtham, Chandrasekar & Kamaraj | 2021-07-30 | - | Tank purging , unloading , Dispensing pumps and Dispenser commissioning, Stamping completed - Open to Public - Attended
CL1587 | 2021-07-27 | Vedachandur | T | Tank N2 test | New Project | Dharmesh & Vignesh | 2021-07-27 | - | N2 testing work completed. Testing pressure 14.5Kg/cm^²Holding pressure 10 kg/cm^² - Completed
CL1588 | 2021-07-27 | Palayam | G | Unloading Training | Preventive | Thirumalaisamy | 2021-07-27 | - | Unloading training completed - Attended
CL1589 | 2021-07-27 | Kodungaiyur | G | PMR work | Preventive | Suneel Sagar | 2021-07-27 | - | PMR done - Attended
CL1590 | 2021-07-28 | Ayothiyapattinam | T | Tank area earth chamber pit marking and earth work | New Project | Prabu | 2021-07-28 | - | Earth chamber pit marking and earthing work completed - Tank flanges, Excess flow valves and pipe hydro test completed - Attended
CL1591 | 2021-07-28 | Madurai | D | D side pulsar not working | Breakdown | Kathiresan | 2021-07-28 | - | New pulsar replaced - Working fine - Testing : C side : 5.05 Ltrs; D side : 5.32 & 17.10 Ltrs - Rectified
CL1592 | 2021-07-28 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2021-07-28 | - | B side VNR nozzle serviced and tested - Testing : 2.41 Ltrs - Completed
CL1593 | 2021-07-29 | Ayothiyapattinam | G | Civil marking | New Project | Prabu | 2021-07-29 | - | Dispenser and canopy pillar and dispenser bed, decanting bed marking - Mechanical work in process - Attended
CL1594 | 2021-07-29 | Manapparai | A | LPG slow delivery | Breakdown | Vignesh | 2021-07-29 | - | Dispenser high flow solenoid coil replaced - Working fine - Rectified
CL1595 | 2021-07-29 | Ariyamangalam | D | Dispenser china nozzle trigger problem | Breakdown | Nepolean | 2021-07-29 | - | Nozzle lock trigger replaced - Working fine - Rectified
CL1596 | 2021-07-29 | Velachery | T | Unloading vapour insulation gasket leakage | Breakdown | Suneel Sagar | 2021-07-29 | - | Gasket leakage arrested by replacing new Teflon gasket - Rectified
CL1597 | 2021-07-29 | Neelambur | A | Automation installation | New Project | Madhavan | 2021-07-29 | - | Automation installation completed and data available online in KR Admin app - Completed
CL1598 | 2021-07-30 | Tirunelveli | D | Yenen dispenser Error 10 occurred | Breakdown | Nepolean | 2021-07-31 | 5 Hours | Error 10 rectified by cleaning the motherboard - Batchen dispenser metering unit serviced - Control panel and Tank 1 air hose to be replaced - Rectified
CL1599 | 2021-07-30 | Attur | C | Rule 19, Additional dispenser installation and Above ground motor pipe line welding | Certification | Prakash, Chandrasekar, Prabu & Kamaraj | 2021-08-06 | - | Rule 19 for both tank completed - Additional dispenser installation completed - Above ground dispensing pump pipe line for both tank completed and tested - ATG installed - Completed
CL1600 | 2021-07-31 | Bodi | G | Camera, Sign board fixing and Dispenser keypad servicing | Preventive | Prasath, Prasanna Narasimhan & Kathiresan | 2021-08-01 | - | Camera fixing, sign board fixing, Automation installation completed - PMR done - Working fine - Attended
CL1601 | 2021-07-31 | Uthamapalayam | G | Camera, Sign board fixing and Dispenser keypad servicing | Preventive | Prasath, Prasanna Narasimhan & Kathiresan | 2021-08-01 | - | Camera fixing, sign board fixing, Automation installation completed - PMR done - Working fine - Attended
CL1602 | 2021-07-31 | Paramathivelur | T | Unloading liquid line ROV with ball valve LPG leakage | Breakdown | Thirumalaisamy | 2021-07-31 | - | ROV with ball valve LPG leakage arrested by tightening the nut with teflon - Automated CPU place changed - PMR done - Rectified
CL1603 | 2021-07-31 | Neelambur | G | EB provision | New Project | Gowtham | 2021-07-31 | - | EB provision done - Working good - Completed
CL1604 | 2021-08-01 | Mettupalayam | A | Wifi range extension & PMR | Preventive | Gowtham | 2021-08-01 | - | Additional router installed for automation billing due and wifi range extension - PMR completed - Attended
CL1605 | 2021-08-02 | Madurai | C | Stamping work | Certification | Kathiresan | 2021-08-02 | - | Oil dispenser stamping completed - Attended
CL1606 | 2021-08-02 | Aravakurichi | D | Dispenser A side slow delivery | Breakdown | Thirumalaisamy | 2021-08-02 | - | A side 3/4" excess flow valve blocks cleaned - Dispenser bottom ROV and tank area unloading ROV leakage arrested by tightening the bolt nut - PMR done - Testing: 0.75 Ltrs - Rectified
CL1607 | 2021-08-02 | Ariyamangalam | D | B side nozzle LPG leakage | Breakdown | Nepolean | 2021-08-02 | - | Service nozzle replaced - Working fine - Tseting: 1.18 Ltrs - Rectified
CL1608 | 2021-08-02 | Thuraiyur | D | Dispenser limit switch problem | Breakdown | Nepolean & Dharmesh | 2021-08-02 | - | Limit switch connection directed - Rectified
CL1609 | 2021-08-03 | Mulanur | G | Unloading trainig | Preventive | Thirumalaisamy | 2021-08-03 | - | Unloading training completed - Attended
CL1610 | 2021-08-03 | Avadi | G | Stabilizer B phase variac not working | Breakdown | Suneel Sagar | 2021-08-03 | - | Variac replaced - Working satisfactory - Rectified
CL1611 | 2021-08-03 | Virudhunagar | G | Offline UPS problem | Breakdown | Kathiresan | 2021-08-03 | - | Offline UPS replaced - Rectified
CL1612 | 2021-08-04 | Madurai | D | D side nozzle leakage | Breakdown | Kathiresan | 2021-08-04 | - | D side nozzle replaced due to lock bottom manufacturing defect - Testing : 0.84 Ltrs - Working fine - Rectified
CL1613 | 2021-08-04 | Kodumudi | T | Dispensing motor spider problem | Breakdown | Thirumalaisamy | 2021-08-04 | - | Dispensing pump spider replaced - Dispensing line damaged pneumatic hose replaced - Working fine - Rectified
CL1614 | 2021-08-04 | Vadivelan Nagar | D | Dispenser liquid line gasket leakage | Breakdown | Suneel Sagar | 2021-08-04 | - | Gasket leakage arrested replacing - A side retraction rope adjusted - C nozzle serviced - Rectified
CL1615 | 2021-08-04 | T.V.Kovil | D | Batchen dispenser A nozzle leakage | Breakdown | Vigneshwaran | 2021-08-04 | - | Spare nozzle replaced - Testing : 1.16 Ltrs - Working fine - Rectified
CL1616 | 2021-08-05 | Ariyamangalam | D | C side nozzle servicing and testing | Preventive | Nepolean | 2021-08-05 | - | Nozzle serviced and tested - Testing : 1.61 Ltrs - Completed
CL1617 | 2021-08-06 | Theni | T | Unloading pump leakage | Breakdown | Kathiresan | 2021-08-06 | - | Unloading pump inner and center O ring damaged - New O rings replaced - Leakage arrested - Rectified
CL1618 | 2021-08-06 | Dharapuram | G | Emergency switch at fill point is not working | Breakdown | Gowtham | 2021-08-06 | - | Emergency push button replaced - Love jaw coupling spider changed - PRV 2 nos fixed in dispensing liquid line - Working satisfactory - Rectified
CL1619 | 2021-08-06 | Uthampalayam | D | Dispenser run mode not working | Breakdown | Kathiresan | 2021-08-06 | - | Dispenser relay fuse replaced - Working in Run mode - Rectified
CL1620 | 2021-08-06 | Tharamangalam | D | Dispenser error 10 | Breakdown | Prabu | 2021-08-07 | 5.30 Hours | New dispenser parameters changed - Testing : 19.45 Ltrs - Working fine - Rectified
CL1621 | 2021-08-06 | Ariyamangalam | G | Servo Stabilizer MOL occurred | Breakdown | Nepolean | 2021-08-07 | - | Servo stabilizer reset done - Working fine - Rectified
CL1622 | 2021-08-07 | Melur | T | N2 testing work | New Project | Kathiresan | 2021-08-07 | - | N2 testing completed - Testing pressure - 14.5kg/cm2 - Holding pressure 10 kg/cm^² - ALDS control panel testing work done - Attended
CL1623 | 2021-08-07 | Palayam | D | B side nozzle rope unleashed | Breakdown | Thirumalaisamy | 2021-08-07 | - | Retraction rope adjusted both sides - Rectified
CL1624 | 2021-08-07 | Ariyamangalam | D | B side breakaway coupling leakage and 1/2 m dispensing hose problem | Breakdown | Nepolean | 2021-08-07 | - | B side breakaway coupling and 1/2 m dispensing hose replaced - Madurai nozzle testing done - Working fine - Rectified
CL1625 | 2021-08-07 | Attur | C | Dispenser stamping | Certification | Prakash | 2021-08-07 | - | Stamping completed - Attended
CL1626 | 2021-08-07 | Madurai | D | Pulsar box and nozzle testing (Madurai returned) | Preventive | Nepolean | 2021-08-07 | - | Pulsar box and nozzle testing done - Pulsar box not working and nozzle handle leakage - Testing : 0.47 Ltrs - Attended
CL1627 | 2021-08-08 | Uthamapalayam | T | Dispensing motor not working | Breakdown | Kathiresan | 2021-08-08 | - | Control panel ( W1) dispensing contactor NO problem. Connected with another NO- Working fine - Tank 2 mode looping connection work done - Rectified
CL1628 | 2021-08-08 | Namakkal 1 | A | RS485 to USB converter board damaged | Breakdown | Thirumalaisamy | 2021-08-08 | - | Converter board replaced - Automation back online - Automation maintenance completed - Rectified
CL1629 | 2021-08-08 | Neelambur | G | Unloading process | Preventive | Gowtham | 2021-08-08 | - | Unloading completed safely with trained person - Attended
CL1630 | 2021-08-08 | Cantonment | D | A side display card not working | Breakdown | Chandrasekar | 2021-08-08 | - | Old spare display card changed - Rectified
CL1631 | 2021-08-09 | Thuraiyur | D | A side solenoid cutoff problem | Breakdown | Nepolean & Dharmesh | 2021-08-09 | - | A side high flow low flow solenoid valve cleaned - Working fine - Rectified
CL1632 | 2021-08-09 | Neelambur | G | Genset not working | Breakdown | Gowtham | 2021-08-09 | - | Genset start/stop actuator serviced by Service Engineer from Ojus - Rectified
CL1633 | 2021-08-09 | Kodungaiyur | T | Strainer leakage and compressor drain valve damage | Breakdown | Suneel Sagar | 2021-08-09 | - | Strainer leakage arrested by applying teflon and compressor drain valve replaced - Rectified
CL1634 | 2021-08-10 | Cantonment | D | New nozzle changing, Control panel indicator damaged & Compressor oil damaged | Preventive | Chandrasekar | 2021-08-10 | - | New nozzles replaced all 4 side - Control panel CC indicator replaced - Compressor oil changed - Testing: A. Testing. 1.15 litre B. Testing. 1.14 litre C. Testing. 0.98 litre D. Testing. 0.88 litre Total testing. 4.15 litre - Rectified
CL1635 | 2021-08-11 | Ramnad | T | CP Installation | New Project | Chandrasekar | 2021-08-11 | - | CP installation completed - Attended
CL1636 | 2021-08-12 | Ariyalur | T | Tank installation | New Project | Chandrasekar & Babu | 2021-08-12 | - | Tank installation and foundation concrete work completed - Attended
CL1637 | 2021-08-12 | T.V.Kovil | D | Batchen dispenser A side nozzle leakage | Breakdown | Vigneshwaran | 2021-08-12 | - | Spare nozzles replaced at both A and D side - A side Testing: 1.19 Ltrs D side Testing: 0.35 : Ltrs Total : 1.54 Ltrs - Rectified
CL1638 | 2021-08-12 | Ariyamangalam | D | C side nozzle problem | Breakdown | Nepolean | 2021-08-12 | - | Spare nozzle replaced - Testing: 0.81 Ltrs - Rectified
CL1639 | 2021-08-13 | Dindigul | D | B side excess flow valve 3/4" problem | Breakdown | Kathiresan | 2021-08-13 | - | Excess flow valve to be replaced - Line directed - Temporarily rectified
CL1640 | 2021-08-13 | Namakkal 2 | D | Slow flow due to pressure drop | Breakdown | Thirumalaisamy | 2021-08-13 | - | DP Valve to be changed - Temporarily rectified
CL1641 | 2021-08-14 | Palayam | R | New VFD installation | Preventive | Prakash & Thirumalaisamy | 2021-08-14 | - | Variable Frequency Drive installed and connected to control panel - Working fine - Completed
CL1642 | 2021-08-14 | Ariyamangalam | D | C side nozzle (from Madurai) testing | Preventive | Nepolean | 2021-08-14 | - | Nozzle tested - Testing C Side : 1.59 Ltrs - Rectified
CL1643 | 2021-08-15 | Rasipuram | D | Nozzle leakage and compressor continuous running | Breakdown | Prabu | 2021-08-15 | - | Nozzle serviced and Solenoid valve cleaned - EB room to tank area air hose replaced - Working fine - Rectified
CL1644 | 2021-08-16 | Madurai | T | Dispensing motor not running properly and vibrating | Breakdown | Kathiresan | 2021-08-16 | - | Dispensing motor aligned properly - Lov jaw coupling spider redirected - Unloading point ROV leakage arrested by tightening the bolt nut - Rectified
CL1645 | 2021-08-16 | Ayothiyapattinam | G | Rule 33 data collection | New Project | Prabu | 2021-08-16 | - | Rule 33 data collected - Electrical cable and GI flat measurement done - Mechanical work in process - Completed
CL1646 | 2021-08-16 | Pudukkottai | R | Dispensing air solenoid problem | Breakdown | Nepolean & Vignesh | 2021-08-16 | - | Master air solenoid replaced - Working fine - Rectified
CL1647 | 2021-08-16 | Avadi | T | Dispensing motor impeller replacement | Breakdown | Suneel Sagar | 2021-08-16 | - | Impeller replaced - Observed for 3 hours - Found satisfactory - Rectified
CL1648 | 2021-08-16 | Ariyamangalam | C | Calibration work | Certification | Nepolean | 2021-08-16 | - | Calibration completed A side testing : 100.22 lit B side testing : 105.77 lit C side testing : 100.09 lit D side testing : Day shift : 225.62 lit Night shift : 408. 04 lit. Total testing : 939.74.Lit. " K Factor " A side : 100180 B side : 100143 C side : 99766 D side : 105600 A side : 10.00=10.04 B side : 10.00 =10.08 C side : 10.00=10.03 D side : 10.00=10.05
CL1649 | 2021-08-17 | Thanjavur | T | Dispencing motor to dispencer Liquid and vapour pipe line fitting | New Project | Babu | 2021-08-17 | - | Dispencing motor to dispencer Liquid and vapour pipe line fitting completed - Attended
CL1650 | 2021-08-17 | Ayothiyapattinam | T | Site visit | New Project | Prabu | 2021-08-17 | - | Tank to dispenser pipe line welding finished - Dispenser placed - Attended
CL1651 | 2021-08-17 | Palayam | G | VFD cable connection | Preventive | Thirumalaisamy | 2021-08-17 | - | VFD cables connected - Glands and cable dressing completed - Rectified
CL1652 | 2021-08-17 | Ariymangalam | T | Main flange vapour line ballvalve with ROV LPG leakage | Breakdown | Nepolean | 2021-08-17 | - | New ballvalve with ROV replaced - Rectified
CL1653 | 2021-08-18 | Namakkal 2 | D | Dispenser jumping | Breakdown | Prabu | 2021-08-18 | - | DP valve replaced - High flow low flow coil changed - Testing: 15.89 Ltrs - Working fine - Completed
CL1654 | 2021-08-18 | Ariyamangalam | C | Stamping work | Certification | Nepolean | 2021-08-18 | - | Stamping completed - Attended
CL1655 | 2021-08-18 | Pudukkottai | C | Calibration work | Certification | Nepolean & Vignesh | 2021-08-18 | - | Calibration completed - Attended
CL1656 | 2021-08-19 | Thanjavur | T | Pipe line welding & Hydro test | New Project | Babu | 2021-08-19 | - | Tank to dispencer pipe line welding completed and hydro test done - Attended
CL1657 | 2021-08-19 | Ayothiyapattinam | G | Mechanical work and hydro test | New Project | Prabu | 2021-08-19 | - | Mechanical work and hydro test completed at pressure 48 kg/cm^2 - Attended
CL1658 | 2021-08-20 | Thanjavur | G | GI flat and HDP pipe laying | New Project | Babu | 2021-08-20 | - | GI flat and HDP pipe laying work completed - Attended
CL1659 | 2021-08-20 | Bhavani | T | Unloading problem | Breakdown | Prabu | 2021-08-20 | - | Liquid line Ball valve block released and control panel to Tank area new air hose changed - Rectified
CL1660 | 2021-08-21 | Ramnad | C | Rule 33 data collection | New Project | Prakash & Dharmesh | 2021-08-21 | - | Rule 33 data collected - Attended
CL1661 | 2021-08-21 | Dindigul | D | B side excess flow valve 3/4" replacement | Breakdown | Kathiresan | 2021-08-21 | - | Excess flow valve replaced - Working fine - Testing 10 Ltrs - Rectified
CL1662 | 2021-08-21 | T.V.Kovil | G | Fire extinguisher refilling and hose damaged | Breakdown | Vigneshwaran | 2021-08-21 | - | 75 Kg and 5 Kg refilling done and hose replaced - Rectified
CL1663 | 2021-08-22 | Namakkal 1 | G | UPS noise and compressor problem | Breakdown | Prabu | 2021-08-22 | - | UPS cleaned and serviced - Compressor pneumatic hose changed - Rectified
CL1664 | 2021-08-22 | Namakkal 2 | D | Dispenser suction problem | Breakdown | Prabu | 2021-08-25 | - | Dispensing bypass valve adjusted to increase pressure to 13bar - Rectified
CL1665 | 2021-08-22 | Aravakurichi | T | Unloading motor not working | Breakdown | Thirumalaisamy | 2021-08-22 | - | Unloading motor V belt tension adjusted - DOL starter Y phase wire melted - replaced - Unloading completed - Rectified
CL1666 | 2021-08-22 | Neelambur | G | Unloading training | Preventive | Gowtham | 2021-08-22 | - | Unloading training completed - Attended
CL1667 | 2021-08-23 | Thanjavur | G | Electrical work | New Project | Babu | 2021-08-23 | - | Electrical work partially completed - Attended
CL1668 | 2021-08-23 | Neelambur | G | 1/4" coupling repair and to monitor dispensing motor suction | Breakdown | Gowtham | 2021-08-23 | - | Unloading vapour line coupling (venting part) damage sealed by bonding agent which has to be replaced - Dispensing liquid suction line altered to another nozzle at tank - Kept under observation - Rectified
CL1669 | 2021-08-23 | Kumbakonam | G | Compressor motor and starter replacment | Preventive | Nepolean & Vignesh | 2021-08-23 | - | Compressor motor and starter replaced - B side nozzle teeth replaced - Working fine - Rectified
CL1670 | 2021-08-23 | Ariyamangalam | D | A nozzle teeth problem | Breakdown | Nepolean | 2021-08-23 | - | Nozzle teeth 4 nos replaced - Rectified
CL1671 | 2021-08-23 | Sulur | D | A side keypad not working | Breakdown | Kathiresan | 2021-08-23 | - | Keypad replaced - Working good - Rectified
CL1672 | 2021-08-24 | Thanjavur | G | Electrical cable laying | New Project | Babu & Chandrasekar | 2021-08-24 | - | Cable laying completed - Attended
CL1673 | 2021-08-24 | Bathlagundu | G | Fencing and tank pit marking | New Project | Kathiresan | 2021-08-24 | - | Markings completed - Rectified
CL1674 | 2021-08-24 | Bodi | D | Dispenser bottom side LPG leakage & EB mode not working | Breakdown | Kathiresan | 2021-08-24 | - | Dispenser bottom side vapour line ball valve stem leakage arrested by tightening the bolt nut - EB high voltage problem rectified - Dispenser hose rope changed - Rectified
CL1675 | 2021-08-24 | Tharamangalam | G | EB mode continuous MCB tripping | Breakdown | Prabu | 2021-08-24 | - | EB line single phase Electrical melted wire replaced - R231,Y 230,B231, UPS battery distilled water level top up done - Rectified
CL1676 | 2021-08-24 | Kodumudi | G | Sign board fixing | Preventive | Prasanna Narasimhan, Thirumalaisamy & Dharmesh | 2021-08-25 | - | Sign boards placed - Completed
CL1677 | 2021-08-24 | Ariyamangalam | D | D side nozzle 4 Nos servicing and testing (From Sulur) | Preventive | Nepolean | 2021-08-24 | - | Nozzles tested - Testing : 3.23 Ltrs - Attended
CL1678 | 2021-08-24 | Kodungaiyur | D | A and B side nozzle problem | Breakdown | Suneel Sagar | 2021-08-24 | - | A nozzle hammer teeth replaced and B side Yenen nozzle replaced - Rectified
CL1679 | 2021-08-24 | Velachery | T | Veedor root Fill point indicator power adopter problem | Breakdown | suneel Sagar | 2021-08-24 | - | Fill point indicator power adopter replaced - Rectified
CL1680 | 2021-08-24 | Karur | D | B side On/Off switch problem | Breakdown | Thirumalaisamy | 2021-08-24 | - | New on off switch replaced - Working good - Rectified
CL1681 | 2021-08-25 | Namakkal 2 | D | Dispenser suction problem | Breakdown | Prabu | 2021-08-25 | - | Dispensing bypass valve adjusted to increase pressure - Rectified
CL1682 | 2021-08-25 | Neelambur | G | Dispenser suction problem | Breakdown | Chandrasekar & Gowtham | 2021-08-26 | - | By pass valve and equalizer valve adjusted - valve. Liquid Suction line change form emergency line to existing line - Found Satisfactory - Rectified
CL1683 | 2021-08-25 | Namakkal 1 | G | Offline UPS battery problem | Breakdown | Prabu | 2021-08-25 | - | New battery replaced - Rectified
CL1684 | 2021-08-26 | Melur | G | Site visit | New Project | Kathiresan | 2021-08-26 | - | ALDS work completed - Automation pending - Painting and facia work in process - Attended
CL1685 | 2021-08-27 | Neelambur | G | VFD testing with control panel & Unloading training | Preventive | Gowtham | 2021-08-27 | - | New VFD tested and found satisfactory - Attended
CL1686 | 2021-08-27 | Avadi | G | Compressor drain valve leakage | Breakdown | Suneel Sagar | 2021-08-27 | - | Drain valve leakage and nozzle hose retraction rope adjusted - Rectified
CL1687 | 2021-08-28 | Dharmapuri | G | Canopy light replacement | Breakdown | Prabu | 2021-08-28 | - | Canopy light 3 Nos replaced - Tank area liquid ball valve leakage arrested - Total leakage testing and PMR completed - Rectified
CL1688 | 2021-08-28 | Virudhachalam | G | Sign board fixing | Preventive | Prasanna Narasimhan & Vignesh | 2021-08-28 | - | Sign boards placed - Completed
CL1689 | 2021-08-28 | Dharapuram | D | Price jumping | Breakdown | Gowtham | 2021-08-28 | - | Parameters reset done - Found satisfactory - Rectified
CL1690 | 2021-08-28 | Ramnad | G | Pipeline Installation | New Project | Dharmesh | 2021-09-05 | - | Pipeline work, Pipeline welding, and Dispenser installation completed - Attended
CL1691 | 2021-08-29 | Sulur | C | PMR work | Preventive | Gowtham | 2021-08-29 | - | PMR done - Unloading liquid and vapour ROV leakage arrested by tightening the bolt nut - Completed
CL1692 | 2021-08-29 | Tharamangalam | D | Dispensing motor noise | Breakdown | Prabu | 2021-08-29 | - | Equalizer valve adjusted - Nozzle serviced - Nozzle rope replaced - Rectified
CL1693 | 2021-08-29 | Sankari | G | Generator Earthing and change over connection | New Project | Prabu | 2021-08-29 | - | Generator earthing amd change over connection completed - Attended
CL1694 | 2021-08-30 | Sankari | G | Stamping & Commissioing work | New Project | Prakash, Chandrasekar & Kamaraj | 2021-09-01 | - | Stamping, commissioning completed with Automation - Open to Pubic Opening A side 823.36 B side 512.67 Dispenser K factor A side 10200 B side 10200 A side 10.04 B side 10.09 A side testing 135.98 B side testing 114.53 Total testing 250.51lit - Attended
CL1695 | 2021-08-30 | Ayothiyapattinam | G | Site visit | New Project | Prabu | 2021-08-30 | - | Site visit completed - Electrical line and pipe line work in process - Attended
CL1696 | 2021-08-31 | Vadivelan Nagar | G | VFD installation | Preventive | Suneel Sagar | 2021-08-31 | - | VFD installed and Genset performance found satisfactory - Completed
CL1697 | 2021-09-01 | Sankari | A | Automation installation | New Project | Madhavan | 2021-09-01 | - | Automation installation completed and data available online in KR Admin app - Completed
CL1698 | 2021-09-01 | Sulur | D | Dispensing air hose damaged | Breakdown | Gowtham | 2021-09-01 | - | Air hose, fittings and earth clip replaced - Rectified
CL1699 | 2021-09-01 | Tharamangalam | C | Stamping work | Certification | Prabu | 2021-09-01 | - | Dispenser stamping completed Old K factor A side 10000 B side 10000 New K factor A side 10250 B side 10250 A sides 10.03 B side 10.05 A side testing 333.89 B side testing 199.94 Total testing 533.83 lit - Completed
CL1700 | 2021-09-01 | Vadivelan Nagar | T | Tank 1 ATG signal getting disturbance | Breakdown | Suneel Sagar | 2021-09-01 | - | Spare cable from probe to ATG console rerouted - Resolved
CL1701 | 2021-09-02 | Ariyamangalam | D | D side nozzle improper LPG flow | Breakdown | Nepolean | 2021-09-02 | - | Dispenser solenoid coil cleaned - Rectified
CL1702 | 2021-09-02 | Vedachandur | G | Site visit | New Project | Kathiresan | 2021-09-02 | - | Site visit completed - All ALDS work completed - Attended
CL1703 | 2021-09-02 | Manapparai | G | Online UPS not working properly | Breakdown | Nepolean & Madhavan | 2021-09-11 | - | Online UPS serviced by Mothish - Outlet back online - Rectified
CL1704 | 2021-09-02 | Attur | C | Dispenser recalibration | Certification | Prabu | 2021-09-02 | - | Dispenser recalibration completed - Bypass valve cleaned to develop pressure - Testing : A side 109.05 B side 113.84 C side 100.00 D side 311.89 Total 634.78 Ltrs - Completed
CL1705 | 2021-09-03 | Ayothiyapattinam | G | Cable laying | New Project | Prabu | 2021-09-03 | - | Electrical cable laying completed - Attended
CL1706 | 2021-09-03 | Kumbakonam | G | Online UPS installation | Breakdown | Vigneshwaran | 2021-09-03 | - | Online UPS installation completed - Rectified
CL1707 | 2021-09-03 | Paramathivelur | D | Dispenser B side nozzle problem | Breakdown | Thirumalaisamy | 2021-09-03 | - | Nozzle teeth replaced - Working fine - Rectified
CL1708 | 2021-09-03 | Uthamasolapuram | G | CPU not working & one side keypad not working | Breakdown | Prabu | 2021-09-07 | - | CPU fan replaced - Keypad replaced on 06.09.2021 - Rectified
CL1709 | 2021-09-04 | Vedachandur | A | Automation and genset commissioning | New Project | Vigneshwaran | 2021-09-04 | - | Automation and Genset commissioning completed - Working good - Attended
CL1710 | 2021-09-04 | Ayothiyapattinam | T | N2 testing work | New Project | Prabu | 2021-09-04 | - | N2 test completed - N2 pressure tested @14.5 kg/cm^2.Pressure held @ 10kg/cm^2 - Attended
CL1711 | 2021-09-04 | Namakkal 1 | A | Rs485 to USB converter board damaged due to lightning - Outlet going offline | Breakdown | Madhavan | 2021-09-05 | - | Outlet back outlet hence spare RS 485 to USB converter replaced - Kept under observation - Rectified
CL1712 | 2021-09-05 | Thuraiyur | D | A side nozzle problem | Breakdown | Nepolean | 2021-09-05 | - | Nozzle teeth replaced - Rectified
CL1713 | 2021-09-05 | Ramnad | G | Pipeline welding and dispenser installation | New Project | Dharmesh | 2021-09-05 | - | Pipe line welding and dispenser installation completed - Attended
CL1714 | 2021-09-06 | Uthamasolapuram | D | Dispenser keypad not working properly | Breakdown | Prabu | 2021-09-06 | - | Keypad replaced - Working good - Rectified
CL1715 | 2021-09-06 | Perambalur | G | Site marking | New Project | Prakash | 2021-09-06 | - | Site marking completed - Attended
CL1716 | 2021-09-06 | T.V.Kovil | D | Batchen dispenser B side 5m dispensing hose LPG leakage | Breakdown | Vigneshwaran | 2021-09-06 | - | New 5m dispensing hose replaced - Testing: 1.07 Ltr - Working fine - Rectified
CL1717 | 2021-09-06 | Ayothiyapattinam | G | Site visit | New Project | Prabu | 2021-09-07 | - | Electrical work completed and Canopy work in process - Attended
CL1718 | 2021-09-06 | Palladam | D | C side LPG slow delivery | Breakdown | Gowtham | 2021-09-06 | - | High flow low flow solenoid valve cleaned - Nozzle teeth replaced at C and D side - Testing : 43.83 Ltrs - Working fine - Rectified
CL1719 | 2021-09-07 | Tirunelveli | C | Batchen and Yenen dispensers calibration and Rule 18 work | Certification | Nepolean & Vignesh | 2021-09-08 | - | Dispensers calibration ane Rule 18 completed - A side old k Factor: 103000 B side old k Factor: 107600 C side old k Factor:10300 D side old k Factor: 10300 A new k Factor:101700 B new k Factor:101400 C new k Factor:10341 D new k Factor:10330 A side 10Lit -10.02 B side 10Lit- 10.00 C side 10Lit - 9.99 D side 10Lit - 10.02 - Attended
CL1720 | 2021-09-07 | Udumalpet | C | Preventive Maintenance Report | Certification | Gowtham | 2021-09-07 | - | PMR done - Completed
CL1721 | 2021-09-07 | Avinashi | D | Nozzle not working properly | Breakdown | Gowtham | 2021-09-07 | - | B side nozzle replaced - Old nozzle serviced - Testing 2.64 Ltrs - Rectified
CL1722 | 2021-09-07 | Paramathivelur | D | B side nozzle latch damaged | Breakdown | Thirumalaisamy | 2021-09-07 | - | Latch set changed - Working fine - Rectified
CL1723 | 2021-09-07 | Dindigul | T | Unloading motor not working | Breakdown | Kathiresan | 2021-09-07 | - | Motor bearing replaced - Working good - Rectified
CL1724 | 2021-09-07 | Ramnad | G | Pipeline hydro test | New Project | Dharmesh | 2021-09-07 | - | Hydro test completed - Testing pressure - 48 kg/cm'2 - Attended
CL1725 | 2021-09-08 | Ariyalur | T | Tank hydro test | New Project | Chandrasekar & Babu | 2021-09-08 | - | Hydro test completed - Testing pressure - 29 kg/cm'2 - Dispenseing decanting motor bed marking completed - Attended
CL1726 | 2021-09-08 | Ayothiyapattinam | G | Genset earthing and canopy installation | New Project | Prabu | 2021-09-08 | - | Genset earthing and canopy installation completed - Attended
CL1727 | 2021-09-09 | Sankari | D | Dispenser display not working properly | Breakdown | Prabu | 2021-09-09 | - | Display cable connection recorrected - A side keypad to be replaced - Testing 39.79 Ltrs - Rectified
CL1728 | 2021-09-09 | Theni | C | Rule 18 work | Certification | Nepolean | 2021-09-09 | - | Rule 18 Completed - Attended
CL1729 | 2021-09-09 | Bodi | C | Rule 18 work | Certification | Nepolean | 2021-09-09 | - | Rule 18 Completed - Attended
CL1730 | 2021-09-09 | Uthamapalayam | C | Rule 18 work | Certification | Nepolean | 2021-09-09 | - | Rule 18 Completed - Attended
CL1731 | 2021-09-10 | Dindigul | C | Rule 18 work | Certification | Nepolean | 2021-09-10 | - | Rule 18 Completed - Attended
CL1732 | 2021-09-10 | Namakkal 2 | D | Dispensing motor pressure problem | Breakdown | Prabu | 2021-09-10 | - | Dispensing bypass valve cleaned - Motor alignment checked - Working fine - Rectified
CL1733 | 2021-09-10 | Manapparai | C | Rule 18 work | Certification | Nepolean | 2021-09-10 | - | Rule 18 Completed - Attended
CL1734 | 2021-09-10 | Ramnad | G | GI flat welding | New Project | Dharmesh | 2021-09-10 | - | GI flat welding work completed - Rectified
CL1735 | 2021-09-11 | Melur | A | Automation installation | New Project | Vignesh, Nivas & Kathiresan | 2021-09-11 | - | Automation installation completed and all ALDS work completed - Working satisfactory - Attended
CL1736 | 2021-09-12 | Vellakovil | R | Compressor continuous running | Breakdown | Thirumalaisamy | 2021-09-12 | - | EB room to tank area pneumatic hose 10 meters replaced - Dispenser B side On/off switch replaced - Dispenser bottom ROV LPG leakage arrested by tightening the nut - Rectified
CL1737 | 2021-09-13 | Vedachandur | R | Control panel testing | New Project | Kathiresan | 2021-09-13 | - | All ALDS work completed - Attended
CL1738 | 2021-09-13 | Thanjavur | T | Tank N2 test | New Project | Babu | 2021-09-13 | - | N2 test completed - Pressure held at 10 Kg/cm^2 - Testing pressure 14 Kg/cm^2 - Attended
CL1739 | 2021-09-13 | Ayothiyapattinam | T | Site visit | New Project | Prabu | 2021-09-13 | - | Tank area pipe line painting completed - EB line work in process - Attended
CL1740 | 2021-09-14 | Aravakurichi | C | Stamping work | Certification | Thirumalaisamy, Vignesh & Adithyan | 2021-09-14 | - | Stamping completed - A side old k factor- 09900 B side old k factor- 09900 A side new k factor-10050 B side new k factor-10050 A side 10Lit=10.00 B side 10Lit=10.00 A side opening reading=1042784.55 A side closing reading=1043286.19 A side testing=501.64 B side opening reading=855923.53 B side closing reading=856260.14 B side testing=336.61 - Attended
CL1741 | 2021-09-14 | Vedachandur | C | Peso Inspection & Commissioning | New Project | Prakash, Thirumalaisamy, Krishna Bhalaji & Kathiresan | 2021-09-15 | - | PESO inspection, Tank purging, Unloading and Commissioning work completed - Stamping Completed - Outlet Open to Public - Attended
CL1742 | 2021-09-14 | Ayothiyapattinam | G | Commissioning work | New Project | Prakash, Prabu, Dharmesh, Kamaraj & Chandrasekar | 2021-09-16 | - | Commissioning completed - Stamping Completed - Outlet open to public - Attended
CL1743 | 2021-09-14 | Ariyamangalam | D | B side nozzle teeth damaged | Breakdown | Nepolean | 2021-09-14 | - | Nozzle teeth 4 nos replaced - Rectified
CL1744 | 2021-09-15 | Avinashi | C | PMR work | Preventive | Gowtham | 2021-09-15 | - | PMR completed - Tank unloading and dispensing ROV leakage arrested by tightening the nut - Rectified
CL1745 | 2021-09-15 | Hosur | D | B side nozzle problem | Breakdown | Suresh | 2021-09-15 | - | New nozzle replaced - Working fine - Testing : 0.98 Ltrs - Rectified
CL1746 | 2021-09-15 | Kodungaiyur | D | Liquid line ballvalve under dispenser leakage | Breakdown | Suneel Sagar | 2021-09-15 | - | Leakage arrested by tighening the nut - Working fine - Rectified
CL1747 | 2021-09-16 | Avinashi | D | Dispenser not getting power supply due to offline UPS output problem | Breakdown | Gowtham | 2021-09-16 | 10 Hours | UPS cleaned and serviced - Rectified
CL1748 | 2021-09-16 | Vedachandur | A | Automation installation | New Project | Madhavan | 2021-09-16 | - | Automation online and data available in KR admin app - Completed
CL1749 | 2021-09-16 | Ayothiyapattinam | A | Automation installation | New Project | Madhavan | 2021-09-16 | - | Automation online and data available in KR admin app - Completed
CL1750 | 2021-09-17 | Ariyalur | T | CP Installation | New Project | Babu | 2021-09-17 | - | CP installation completed - Attended
CL1751 | 2021-09-17 | Mulanur | G | Online UPS - Error 56 & Error 6 | Breakdown | Thirumalaisamy | 2021-10-20 | - | UPS replaced by vendor - Rectified
CL1752 | 2021-09-17 | Thanjavur | T | Tank area pipe line painting | New Project | Babu | 2021-09-17 | - | Painting work completed - Attended
CL1753 | 2021-09-17 | T.V.Kovil | A | Automation going offline for testing CPU replacement | Preventive | Madhavan | 2021-09-17 | - | CPU replaced - Back online - Completed
CL1754 | 2021-09-18 | Melur | G | CCOE inspection | New Project | Prakash & Kathiresan | 2021-09-18 | - | CCOE inspection completed - Tank purging and Commissioning completed - Attended
CL1755 | 2021-09-18 | Thanjavur | C | CCOE inspection | New Project | Nepolean & Dharmesh | 2021-09-18 | - | CCOE inspection completed - Attended
CL1756 | 2021-09-18 | Palladam | C | PMR work | Preventive | Gowtham | 2021-09-18 | - | PMR completed - Attended
CL1757 | 2021-09-19 | Melur | A | Automation installation | New Project | Madhavan | 2021-09-19 | - | Automation online and data available in KR admin app - Completed
CL1758 | 2021-09-19 | Melur | C | Stamping & Commissioning work | New Project | Kathiresan | 2021-09-19 | - | All equipments commissioning completed - Stamping completed - A side "K" factor =10000 B side "K" factor = 10000 - Attended
CL1759 | 2021-09-20 | Namakkal 1 | D | Dispenser both side nozzle leakage | Breakdown | Prabu | 2021-09-20 | - | Nozzle teeth replaced - PMR Completed - Leakage arrested - Rectified
CL1760 | 2021-09-20 | Rasipuram | A | Automation system CPU problem | Breakdown | Prabu | 2021-09-20 | - | CPU fan replaced - Compressor and Genset oil changed - Recitified
CL1761 | 2021-09-20 | Sulur | C | Stamping and Rule 18 work | Certification | Nepolean, Gowtham & Dharmesh | 2021-09-21 | - | Rule 18 and stamping completed - Attended
CL1762 | 2021-09-20 | Saravanampatty | C | Stamping and Rule 18 work | Certification | Nepolean, Gowtham & Dharmesh | 2021-09-21 | - | Rule 18 and stamping completed - Attended
CL1763 | 2021-09-21 | Hosur | A | Outlet going offline due to CPU problem | Breakdown | Madhavan | 2021-09-22 | - | Outlet back online with standby PC - Rectified
CL1764 | 2021-09-21 | Sankari | D | Dispenser display problem | Breakdown | Prabu | 2021-09-21 | 2 Hours (A side) | Display cable reconnected - Unloading training completed - Rectified
CL1765 | 2021-09-21 | T.V.Kovil | D | Yenen dispenser D side nozzle teeth problem | Breakdown | Vigneshwaran | 2021-09-21 | - | Nozzle teeth replaced - Control panel input pneumatic hose replaced - Working fine - Rectified
CL1766 | 2021-09-21 | Perambalur | T | Tank installation | New Project | Prakash & Babu | 2021-09-21 | - | Tank installation completed - Attended
CL1767 | 2021-09-21 | Kangeyam | C | Calibration and stamping | Certification | Nepolean, Gowtham, Thirumalaisamy & Dharmesh | 2021-09-22 | - | Rule 18 and stamping completed - Attended
CL1768 | 2021-09-21 | Vellakovil | C | Calibration and stamping | Certification | Nepolean, Gowtham, Thirumalaisamy & Dharmesh | 2021-09-22 | - | Rule 18 and stamping completed - Attended
CL1769 | 2021-09-21 | Dharapuram | C | Calibration and stamping | Certification | Nepolean, Gowtham, Thirumalaisamy & Dharmesh | 2021-09-22 | - | Rule 18 and stamping completed - Attended
CL1770 | 2021-09-22 | Ayothiyapattinam | T | Dispensing motor coil winding damaged | Breakdown | Prabu | 2021-09-23 | 10 Hours | Spare motor replaced - Defected motor to be replaced - Working fine - Rectified
CL1771 | 2021-09-22 | Cantonment | D | Yenen dispenser D side on/off switch damaged | Breakdown | Vigneshwaran | 2021-09-22 | - | New on/off switch replaced - Working good - Rectified
CL1772 | 2021-09-22 | Melur | A | TP link box installation | New Project | Kathiresan | 2021-09-22 | - | TP link box set up done - Mobile billing working fine - Rectified
CL1773 | 2021-09-22 | Sankari | C | PESO Inspection | Certification | Prakash & Venkatesh | 2021-09-22 | - | PESO Inspection completed - Attended
CL1774 | 2021-09-22 | Ayothiyapattinam | C | PESO Inspection | Certification | Prakash & Venkatesh | 2021-09-22 | - | PESO Inspection completed - Attended
CL1775 | 2021-09-22 | Madurai | D | C and D side display card problem | Breakdown | Kathiresan | 2021-09-22 | - | Display card reconnected - Rectified
CL1776 | 2021-09-22 | Cantonment | A | Outlet going offline for system update | Preventive | Madhavan | 2021-09-23 | - | System updation done - Outlet back online - Completed
CL1777 | 2021-09-23 | Ayothiyapattinam | T | Tank area vapour line insulation gasket got damaged | Breakdown | Prabu | 2021-09-23 | - | Gasket changed - Leakage arrested - Rectified
CL1778 | 2021-09-23 | Kodungaiyur | D | A side nozzle teeth damaged | Breakdown | Suneel Sagar | 2021-09-23 | - | Nozzle teeth and front bush changed - Rectified
CL1779 | 2021-09-23 | Namakkal 2 | T | Dispensing motor alignment checking | Preventive | Prabu | 2021-09-23 | - | Alignment checked and Love jaw coupling replaced - Working fine - Rectified
CL1780 | 2021-09-23 | Ramnad | G | Electrical work and control panel testing | New Project | Chandrasekar | 2021-09-23 | - | Electrical work and control panel testing completed - Nitrogen testing completed - Testing pressure : 14.5Kg/cm^2 - Attended
CL1781 | 2021-09-23 | Udumalpet | C | Calibration and stamping | Certification | Nepolean, Gowtham, Thirumalaisamy & Dharmesh | 2021-09-23 | - | Rule 18 and stamping completed - Attended
CL1782 | 2021-09-23 | Palladam | C | Calibration and stamping | Certification | Nepolean, Gowtham, Thirumalaisamy & Dharmesh | 2021-09-23 | - | Rule 18 and stamping completed - Attended
CL1783 | 2021-09-24 | Ayothiyapattinam | T | Unloading and pipeline leakage testing | Preventive | Prabu | 2021-09-24 | - | Unloading completed and pipe line leakage testing completed - Attended
CL1784 | 2021-09-24 | Bhavani | C | Rule 18 work | Certification | Prabu & Nepolean | 2021-09-24 | - | Rule 18 work completed - Attended
CL1785 | 2021-09-24 | Vedachandur | T | Unloading and pipeline leakage testing | Preventive | Kathiresan | 2021-09-24 | - | Unloading completed and pipe line leakage testing completed - Unloading point ballvalve leakage arrested - Attended
CL1786 | 2021-09-24 | Avinashi | C | Rule 18 work | Certification | Prabu & Nepolean | 2021-09-24 | - | Rule 18 work completed - Attended
CL1787 | 2021-09-24 | Mettupalayam | C | Rule 18 work | Certification | Prabu & Nepolean | 2021-09-24 | - | Rule 18 work completed - Attended
CL1788 | 2021-09-24 | Perundurai | C | Rule 18 work | Certification | Prabu & Nepolean | 2021-09-24 | - | Rule 18 work completed - Attended
CL1789 | 2021-09-24 | Erode | C | Rule 18 work | Certification | Prabu & Nepolean | 2021-09-24 | - | Rule 18 work completed - Attended
CL1790 | 2021-09-25 | Kodumudi | C | Rule 18 work | Certification | Nepolean | 2021-09-25 | - | Rule 18 work completed - Attended
CL1791 | 2021-09-25 | Mulanur | C | Rule 18 work | Certification | Nepolean | 2021-09-25 | - | Rule 18 work completed - Attended
CL1792 | 2021-09-25 | Aravakurichi | C | Rule 18 work | Certification | Nepolean | 2021-09-25 | - | Rule 18 work completed - Attended
CL1793 | 2021-09-25 | Karur | C | Rule 18 work | Certification | Nepolean | 2021-09-25 | - | Rule 18 work completed - Attended
CL1794 | 2021-09-27 | Melur | R | Servo Stabilizer problem | Breakdown | Kathiresan | 2021-09-27 | - | High input voltage problem resolved by reprogramming the stabilizer - Rectified
CL1795 | 2021-09-27 | Ariyamangalam | D | Nozzle teeth damaged | Breakdown | Nepolean | 2021-09-27 | - | B side nozzle lock replaced and C side nozzle teeth replaced - Working fine - Testing : 1.65 Ltrs - Rectifed
CL1796 | 2021-09-27 | Madurai | T | Dispensing motor love jaw coupling spider problem | Breakdown | Kathiresan | 2021-09-27 | - | Love jaw coupling spider replaced - Motor alignment checked - Working fine - Rectified
CL1797 | 2021-09-28 | Krishnagiri | C | Rule 18 and stamping work | Certification | Prabu, Dharmesh & Nivas | 2021-09-28 | - | Rule 18 and stamping completed - Tank area ROV and ballvalve leakage arrested by tightening the nut - Earth regenerated - Nozzle 2 nos serviced - Testing : A side - 142.68 B side - 114.84 -Total testing liters - 257.52 - Attended
CL1798 | 2021-09-28 | Thanjavur | A | Automation installation | New Project | Kamaraj, Babu & Adhithyan | 2021-09-28 | - | Automation installation done - Mechanical work completed - Attended
CL1799 | 2021-09-28 | Tirunelveli | T | Unloading motor problem | Breakdown | Kathiresan | 2021-09-29 | - | DOL Starter contactor with relay replaced to resolve unloading motor problem - Tank 1 SRV replaced and unloading ballvalve with ROV replaced - Rectified
CL1800 | 2021-09-28 | Ariyalur | D | Dispenser pipeline and placing | New Project | Babu | 2021-09-28 | - | Tank to dispenser pipe line work done - Dispenser placed - Completed
CL1801 | 2021-09-28 | Vellakovil | D | Site visit | New Project | Thirumalaisamy | 2021-09-28 | - | Cables and material required additional dispenser installation has been noted - Attended
CL1802 | 2021-09-28 | Thanjavur | G | Site visit | New Project | Prakash & Prasath | 2021-09-28 | - | General site visit completed - Attended
CL1803 | 2021-09-28 | Ariyalur | G | Site visit | New Project | Prakash & Prasath | 2021-09-28 | - | General site visit completed - Attended
CL1804 | 2021-09-28 | Pudukkottai | D | Dispenser B side not working due to on/off switch problem | Breakdown | Vigneshwaran | 2021-09-28 | - | B side On/Off switch replaced - Working fine - Rectified
CL1805 | 2021-09-28 | Hosur | C | Rule 18 and stamping work | Certification | Prabu, Dharmesh & Nivas | 2021-09-29 | - | Rule 18, Calibration and stamping completed - Dispensing motor spider replaced - Earth regenerated - "A" Side =394.53 "B" Side =217.24 Total testing litters:611.77 - Completed
CL1806 | 2021-09-29 | T.V.Kovil | D | Batchen dispenser A nozzle teeth damaged | Breakdown | Vigneshwaran | 2021-09-29 | - | Nozzle teeth 4 nos replaced - Rectified
CL1807 | 2021-09-29 | Vadivelan Nagar | G | VFD error and Tank liquid line ROV leakage | Breakdown | Suneel Sagar | 2021-09-30 | - | VRF reconfigured with the service person to solve over voltage error - ROV leakage arrested by tightening the nut - Kept under observation - Rectified
CL1808 | 2021-09-29 | Vellakovil | D | Additional dispenser installation | New Project | Thirumalaisamy, Chandrasekar & Vignesh | 2021-09-01 | - | Additional dispenser installed - Welding and testing completed - Calibration and pipeline work completed - Batchen dispenser B side metering unit bearing and lip seal changed due to arrest the leakage - Yenen dispenser open to sales - Yenen dispenser Opening reading C side-342.56 D side-260.79. K factor both side-10000 C side 10lit-10.02 D side 10lit-10.05 - Completed
CL1809 | 2021-09-30 | Dharmapuri | C | Rule 18 work | Certification | Prabu, Dharmesh & Nivas | 2021-09-30 | - | Rule 18 Completed - Unloading hose and ACME adapter leakage arrested by applying teflon - Earth regenerated - Attended
CL1810 | 2021-09-30 | Tharamangalam | C | Rule 18 work | Certification | Prabu, Dharmesh & Nivas | 2021-09-30 | - | Rule 18 completed - Filling point liquid line ROV leakage arrested by tightening the nut applying teflon - Earth regenerated - Rectified
CL1811 | 2021-09-30 | Melur | G | Unloading training | Preventive | Kathiresan | 2021-09-30 | - | Unloading training completed - Unloading ballvalve LPG leakage arrested by tightening the nut - Completed
CL1812 | 2021-09-30 | Salem | C | Rule 18 work | Certification | Prabu, Dharmesh & Nivas | 2021-09-30 | - | Rule 18 completed - Unloading hose vapour line continuity is not satisfactory - Attended
CL1813 | 2021-09-30 | Uthamasolapuram | C | Rule 18 work | Certification | Prabu, Dharmesh & Nivas | 2021-09-30 | - | Rule 18 completed - Filling point vapour line ROV leakage arrested by tightening the nut applying teflon - Earth regenerated - Rectified
CL1814 | 2021-10-01 | Thanjavur | G | Site visit | New Project | Nepolean & Kamaraj | 2021-10-01 | - | DG power, control panel, Dispensing and decanting motor, compressor, ATG, ROV and automation checked and found satisfactory - Dispenser rate setting done - Completed
CL1815 | 2021-10-01 | Neelambur | T | Unloading vapour line coupling welding | Breakdown | Gowtham | 2021-10-01 | - | Coupling welding completed - Leakage checked - Rectified
CL1816 | 2021-10-01 | Sankari | T | Dispensing motor not working in Genset mode | Breakdown | Prabu, Dharmesh & Nivas | 2021-10-05 | - | Motor coil rewinded - Unloading completed - Rectified
CL1817 | 2021-10-01 | Ayothiyapattinam | T | Dispensing motor rewinding changing | Breakdown | Prabu, Dharmesh & Nivas | 2021-10-01 | - | Rewinding done - Kept under observation - Rectified
CL1818 | 2021-10-01 | Perundurai | D | Dispenser power problem | Breakdown | Gowtham | 2021-10-02 | - | New fuse replaced - RS485 to USB converter replaced as it got damaged due to lightening - Compressor oil changed - Unloading training completed - Rectified
CL1819 | 2021-10-02 | Ayothiyapattinam | C | Recalibration work | Certification | Prabu | 2021-10-02 | - | Recalibration and testing done - A side 100 B side 100 Total 200 ltrs - Attended
CL1820 | 2021-10-02 | Cantonment | D | A side nozzle breakaway coupling LPG leakage | Breakdown | Nepolean | 2021-10-02 | - | New breakaway couping replaced - Working fine - Testing : 1.12 Ltrs - Rectified
CL1821 | 2021-10-02 | Bhavani | R | Control panel problem due to surge protector not working | Breakdown | Prabu | 2021-10-04 | - | New RYB surge protector replaced - RS485 to USB converter board replaced - Dispenser back online - PMR done - Resolved
CL1822 | 2021-10-03 | Perundurai | G | Online UPS Error - Fault 15 | Breakdown | Thirumalaisamy | 2021-10-03 | - | Standby UPS replaced - UPS taken for service by Mothish's service person - Attended
CL1823 | 2021-10-04 | Uthamapalayam | A | CPU fan issue and dispenser one side keypad not working | Breakdown | Kathiresan | 2021-10-04 | - | CPU fan replaced - Working fine - Dispenser keypad to be replaced - Dispensing motor bypass valve adjusted - Rectified
CL1824 | 2021-10-04 | Vellakovil | G | Site visit | Preventive | Thirumalaisamy | 2021-10-04 | - | Dispenser and tank leakage checked - Working good - Attended
CL1825 | 2021-10-05 | Pudukkottai | C | Rule 18 & stamping work | Certification | Dharmesh & Vignesh | 2021-10-05 | - | Rule 18 & Stamping work completed - Earth regenerated - Air machine and compressor oil changed - Testing : A side testing - 114.75 ltr B side testing - 120.55 ltr - Completed
CL1826 | 2021-10-05 | Erode | T | Unloading motor not working | Breakdown | Thirumalaisamy | 2021-10-05 | - | Starter contactor Y phase wire melted - Wire replaced - Unloading motor bypass valve cleaned - Working fine - Rectified
CL1827 | 2021-10-06 | Thuraiyur | C | Rule 18 work | Certification | Chandrasekar & Kamaraj | 2021-10-06 | - | Rule 18 completed - Liquid ROV leakage arrested by applying teflon and tighening the nut - Earth regenerated - PMR completed - Resolved
CL1828 | 2021-10-06 | Namakkal 1 | G | Online UPS not working properly | Breakdown | Prabu | 2021-10-06 | - | Spare UPS connected - Working fine - Rectified
CL1829 | 2021-10-06 | T.V.Kovil | C | Rule 18 work | Certification | Vigneshwaran | 2021-10-06 | - | Rule 18 completed - Ground earth regenerated - PMR done - Attended
CL1830 | 2021-10-07 | Ariyamangalam | C | Rule 18 work | Certification | Kamaraj | 2021-10-07 | - | Rule 18 completed - Ground earth regenerated - SRV replaced - Dispensing ROV air leakage arrested by tightening the nut - PMR done - Attended
CL1831 | 2021-10-08 | Ariyalur | G | Site visit | New Project | Chandrasekar & Kamaraj | 2021-10-08 | - | Electrical and mechanical work in process - Attended
CL1832 | 2021-10-08 | Avinashi | D | Batchen dispenser one side flow cutoff problem | Breakdown | Gowtham | 2021-10-08 | - | On/off switch replaced - Flow controlled in preset mode - Rectified
CL1833 | 2021-10-09 | Ayothiyapattinam | T | Dispensing motor pressure problem | Breakdown | Prabu | 2021-10-09 | - | Bypass valve cleaned and adjusted - Unloading motor pressure gauge replaced - Rectified
CL1834 | 2021-10-09 | Ariyamangalam | D | Nozzle teeth damaged | Breakdown | Ravi | 2021-10-09 | - | A side nozzle teeth replaced - Working fine - Rectified
CL1835 | 2021-10-09 | Cantonment | C | Rule 18 work | Certification | Chandrasekar | 2021-10-09 | - | Rule 18 completed - Ground earth regenerated - PMR done - Attended
CL1836 | 2021-10-09 | Thanjavur | T | Unloading and testing | New Project | Prakash, Chandrasekar, Kathiresan & Kamaraj | 2021-10-10 | - | Unloading, dispenser commissioning completed - Attended
CL1837 | 2021-10-10 | Mulanur | T | Unloading and unloading training | Preventive | Thirumalaisamy | 2021-10-10 | - | Unloading training completed - Unloading completed - Attended
CL1838 | 2021-10-10 | Sankari | R | Control panel not working | Breakdown | Prabu | 2021-10-10 | - | Emergency switch wiring recorrected -Rectified
CL1839 | 2021-10-10 | Aravakurichi | A | Automation not working | Breakdown | Thirumalaisamy | 2021-10-10 | - | Automation rewiring done - Outlet back online - Earthing checked - Automation maintenance done - Completed
CL1840 | 2021-10-11 | Sankari | T | Unloading and unloading training | Preventive | Prabu | 2021-10-11 | - | Unloading training completed - Unloading completed - Attended
CL1841 | 2021-10-11 | Melur | T | Unloading and unloading training | Preventive | Kathiresan | 2021-10-11 | - | Unloading training completed - Unloading completed - ATG cut off checked - Dispensing line ballvalve LPG leakage arrested by applying teflon and tightening the nut - Attended
CL1842 | 2021-10-11 | Mettupalayam | A | Outlet going offline due to CPU problem | Breakdown | Gowtham | 2021-10-12 | - | Automation CPU maintenance done - Working fine - Outlet back online - Rectified
CL1843 | 2021-10-11 | Thanjavur | C | Calibration and stamping | Certification | Chandrasekar | 2021-10-11 | - | Calibration and stamping completed - Attended
CL1844 | 2021-10-12 | Erode | C | Stamping work | Certification | Kamaraj & Thirumalaisamy | 2021-10-12 | - | Stamping completed - Attended
CL1845 | 2021-10-12 | Paramathivelur | C | Rule 18 work | Certification | Kamaraj & Thirumalaisamy | 2021-10-12 | - | Rule 18 completed - Earth regenerated - Attended
CL1846 | 2021-10-12 | Dindigul | A | Outlet going offline due to earthing issue | Breakdown | Kathiresan | 2021-10-12 | - | Automation earth leakage checked and rewiring done - Working good -Outlet back online - Rectified
CL1847 | 2021-10-13 | Madurai | T | Dispensing motor love jaw coupling spider problem | Breakdown | Kathiresan | 2021-10-13 | - | Love jaw coupling spider replaced - Working fine - Rectified
CL1848 | 2021-10-13 | Namakkal 2 | R | Compressor motor fan is not rotating due to lock pin broken | Breakdown | Prabu | 2021-10-13 | - | Compressor motor fan lock pin changed - Rectified
CL1849 | 2021-10-15 | Thanjavur | T | ATG float stuck up | New Project | Prakash, Kamaraj & Chandrasekar | 2021-10-15 | - | Float released - Dispensing decanting motor working good with EB mode - Attended
CL1850 | 2021-10-16 | Perambalur | T | Tank hydro test | New Project | Kamaraj | 2021-10-17 | - | Hydro test completed - 27.43 kg/cm^2 holding pressure - No leakage found - Completed
CL1851 | 2021-10-16 | Ariyalur | C | Rule 33 inspection work | Certification | Kamaraj | 2021-10-16 | - | Rule 33 inspection completed - Attended
CL1852 | 2021-10-16 | Sankari | D | Dispenser error 0 | Breakdown | Prabu | 2021-10-16 | - | Dispenser fuse changed - Dispenser working fine - Rectified
CL1853 | 2021-10-17 | Namakkal 1 | G | UPS not working | Breakdown | Prabu | 2021-10-17 | - | UPS board replaced - Working fine - Rectified
CL1854 | 2021-10-17 | Neelambur | T | Unloading process is slow | Breakdown | Gowtham | 2021-10-17 | - | Bypass valve cleaned and adjusted - Rectified
CL1855 | 2021-10-18 | Thanjavur | G | Commissioning work & Outlet opening | New Project | Nepolean, Vignesh & Dharmesh | 2021-10-18 | - | All equipments commissioning completed - Outlet open to public - Attended
CL1856 | 2021-10-18 | Krishnagiri | D | A side display problem | Breakdown | Prabu | 2021-10-19 | - | Display replaced - Working fine - Unloading liquid and vapour Rov serviced - Rectified
CL1857 | 2021-10-18 | Vellakovil | D | Low flow cut off not working | Breakdown | Thirumalaisamy | 2021-10-18 | - | High flow low flow solenoid valve cleaned - Testing : 47 Ltrs - Working fine - Tyre inflator air leakage arrested by replacig T joint - Rectified
CL1858 | 2021-10-18 | Thanjavur | A | Automation installation | New Project | Madhavan | 2021-10-18 | - | Automation online and data available in KR admin app - Completed
CL1859 | 2021-10-19 | Ariyamangalam | D | D side nozzle teeth problem | Breakdown | Nepolean | 2021-10-19 | - | Nozzle teeth 4 nos replaced - Rectified
CL1860 | 2021-10-20 | Vedachandur | T | Dispensing motor running time alteration and alignment checking | Preventive | Kathiresan | 2021-10-20 | - | Dispensing motor running time alteration and alignment checked - Unloading training given - Dispenser bottom ball valve lpg leakage arrested by tightening the nut - Rectified
CL1861 | 2021-10-20 | Uthamasolapuram | C | Stamping work | Certification | Prabu | 2021-10-20 | - | Stamping done - K factor A side 10100 B side 10100 openings A side 288357.66 B side 282739.93 Closings A side 288457.66 B side 282839.93 Total testing 200lit - Completed
CL1862 | 2021-10-20 | Palayam | G | Unloading training | Preventive | Thirumalaisamy | 2021-10-20 | - | Unloading training completed - ROV leakage arrested by tightening the nut - Completed
CL1863 | 2021-10-20 | Tharamangalam | A | Outlet going offline due to power supply not coming | Breakdown | Prabu | 2021-10-20 | - | Junction box worn out - Supply connection altered with rewiring - Outlet back online - Rectified
CL1864 | 2021-10-21 | Chengalpattu | C | Rule 18 work | Certification | Chandrasekar & Kamaraj | 2021-10-21 | - | Rule 18 completed - Earth regenerated - Dispenser bottom liquid line ROV LPG leakage arrested by tightening the nut - Attended
CL1865 | 2021-10-21 | Dindigul | G | Dispenser offline UPS not working | Breakdown | Kathiresan | 2021-10-21 | - | New UPS replaced - Rectified
CL1866 | 2021-10-21 | Namakkal 1 | C | Rule 18 work | Certification | Prabu, Vignesh & Nivas | 2021-10-21 | - | Rule 18 completed - Ground earth regenerated - PMR done - Attended
CL1867 | 2021-10-21 | Ramnad | G | Commissioning work | New Project | Prakash, Madhavan, Kathiresan & Dharmesh | 2021-10-25 | - | Unloading dispensing pump, ATG, and dispenser commissioned - Dispenser stamping completed - Automation installed and brought online - Outlet is open to public - Completed
CL1868 | 2021-10-21 | Vadivelan Nagar | C | Rule 18 work | Certification | Chandrasekar & Kamaraj | 2021-10-21 | - | Rule 18 completed - Ground earth regenerated - Unloading bypass valve cleaned - Attended
CL1869 | 2021-10-22 | Attur | C | Rule 18 work | Certification | Prabu, Vignesh & Nivas | 2021-10-22 | - | Rule 18 completed - Tank area liquid line ball valves leakage arrested by tightening the nut - Yenen dispenser offline UPS connected - Completed
CL1870 | 2021-10-22 | Kodungaiyur | C | Rule 18 work | Certification | Chandrasekar & Kamaraj | 2021-10-22 | - | Rule 18 completed - Dispenser calibration done A side old k factor- 10200 B side old k factor- 10200 A side new k factor-10000 B side new k factor-10000 A side 10Lit=10.00 B side 10Lit=10.01 A side opening reading=768206.38 A side closing reading=768462.40 A side testing=256.02lit B side opening reading=566017.48 B side closing reading=566136.95 B side testing=119.53 lit Total testing = 375.55 lit - Dispensing motor spider replaced - Dispenser filter replaced - PMR done - Rectified
CL1871 | 2021-10-22 | Avadi | G | Outlet visit | Preventive | Chandrasekar & Kamaraj | 2021-10-22 | - | Outlet general visit completed - PMR Done - Attended
CL1872 | 2021-10-23 | Velachery | C | Rule 18 work | Certification | Chandrasekar & Kamaraj | 2021-10-23 | - | Rule 18 completed - Ground earth regenerated - PMR Done - Attended
CL1873 | 2021-10-24 | Uthamasolapuram | T | Dispensing motor lov jaw coupling spider damaged | Breakdown | Prabu | 2021-10-24 | - | Dispensing motor lov jaw coupling spider replaced - Motor alignment checked - Rectified
CL1874 | 2021-10-25 | Avinashi | D | Batchen dispenser hose leakage due to hose joint damage | Breakdown | Gowtham | 2021-10-25 | - | Hose repaired by crimping - Leakage arrested - Testing : 0.80 Ltrs - Rectified
CL1875 | 2021-10-26 | Ariyalur | T | Nitrogen testing work | New Project | Chandrasekar & Kamaraj | 2021-10-26 | - | N2 testing completed - Testing pressure - 14.5kg/cm2 - Holding pressure 10 kg/cm^² - ALDS control panel testing work done - Attended
CL1876 | 2021-10-26 | Dharapuram | T | Unloading liquid line ball valve LPG lealage | Breakdown | Gowtham | 2021-10-26 | - | Unloading ballvalve leakage arrested by tightening the bolt - SRV mounting flange changed - Vent pipe alteration done - Resolved
CL1877 | 2021-10-26 | Bodi | A | Outlet going offline due to CPU issue | Breakdown | Madhavan & Kathiresan | 2021-11-02 | - | CPU fan replaced - Outlet back online - Testing : 10 Ltrs - Compressor air pressure switch serviced - Rectified
CL1878 | 2021-10-27 | Paramathivelur | G | Tyre inflator hose damaged | Breakdown | Thirumalaisamy | 2021-10-27 | - | Tyre inflator hose replaced - Working fine - Rectified
CL1879 | 2021-10-28 | Sankari | T | Unloading liquid line ACME adapter leakage | Breakdown | Prabu | 2021-10-28 | - | ACME adapter replaced - Unloading done - Rectified
CL1880 | 2021-10-28 | Vellakovil | C | Yenen dispenser stamping | Certification | Thirumalaisamy | 2021-10-28 | - | Stamping completed - Attended
CL1881 | 2021-10-28 | Ramnad | D | Metering unit DP valve teflon membrane punctured | Breakdown | Dharmesh | 2021-10-28 | - | Metering unit DP valve teflon membrane changed - Rectified
CL1882 | 2021-10-28 | Cantonment | T | Unloading pump abnormal noise | Breakdown | Prakash | 2021-10-28 | - | Pump carbon blade and seal kit replaced - Kept under observation - Resolved
CL1883 | 2021-10-29 | Bathlagundu | T | Tank installation | New Project | Kathiresan | 2021-10-29 | - | Tank installation completed - Attended
CL1884 | 2021-10-29 | Dharmapuri | D | Dispenser B side display not working & Tank area ROV leakage | Breakdown | Prabu | 2021-10-29 | - | Display cables cleaned and reconnected - ROV leakage arrested by tightening the bolt - Rectified
CL1885 | 2021-10-29 | Virudhunagar | A | Outlet going offline due to CPU issue | Breakdown | Kathiresan | 2021-10-29 | - | CPU connections corrected - System updation done - Dispenser back online - Rectified
CL1886 | 2021-10-29 | Palladam | D | Batchen dispenser hose skin peeled | Breakdown | Gowtham | 2021-10-29 | - | Dispenser hose skin covered - Nozzle serviced - Testing : 2 Ltrs - Rectified
CL1887 | 2021-10-29 | Ariyamangalam | G | Generator service | Preventive | Nepolean | 2021-10-29 | - | Oil, Oil filter and diesel filter replaced - Resolved
CL1888 | 2021-10-30 | Kumbakonam | C | Rule 18 work | Certification | Chandrasekar & Vignesh | 2021-10-30 | - | Rule 18 completed - Ground earth regenerated - Emergency switch NC element changed - PMR done - Resolved
CL1889 | 2021-10-30 | Perambalur | G | Welding work | New Project | Dharmesh | 2021-10-30 | - | GI pipe (Electrical earth) installation completed - Attended
CL1890 | 2021-10-31 | Virudhunagar | A | Outlet going offline due to CPU issue | Breakdown | Kathiresan | 2021-11-01 | - | CPU maintenance done - Outlet back online - Rectified
CL1891 | 2021-11-01 | Perambalur | G | Rule 33 data collection | New Project | Dharmesh | 2021-11-01 | - | Rule 33 data collected - Pipe line installation in process - Attended
CL1892 | 2021-11-01 | Cantonment | D | Nozzle not working properly | Breakdown | Kamaraj | 2021-11-01 | - | C side Yenen nozzle replaced with a new one - Working fine - Testing : 1 Ltr - Rectified
CL1893 | 2021-11-01 | T.V.Kovil | G | Offline UPS battery problem | Breakdown | Vigneshwaran | 2021-11-01 | - | New battery replaced - Rectified
CL1894 | 2021-11-02 | Namakkal 2 | T | Unloading liquid line ballvalve leakage | Breakdown | Prabu | 2021-11-02 | - | Ballvalve leakage arrested by tightening the nut and teflon applied - Rectified
CL1895 | 2021-11-02 | Perambalur | D | Dispenser installation | New Project | Dharmesh | 2021-11-02 | - | Dispenser installation completed - Working fine - Attended
CL1896 | 2021-11-02 | Paramathivelur | T | Dispensing liquid line ballvalve with ROV not working | Breakdown | Thirumalaisamy | 2021-11-02 | - | Ballvalve with ROV replaced - Working fine - Rectified
CL1897 | 2021-11-02 | Namakkal 1 | R | Control panel noise and vibration | Breakdown | Prabu | 2021-11-02 | - | Air solenoid coil cleaned and reconnected - Noise arrested - Rectified
CL1898 | 2021-11-04 | Kangeyam | T | Dispensing liquid line ballvalve with ROV not working | Breakdown | Gowtham | 2021-11-04 | - | Ball valve with ROV replaced - Rectified
CL1899 | 2021-11-04 | Uthamasolapuram | D | Dispenser A side nozzle leakage | Breakdown | Prabu | 2021-11-04 | - | Nozzle leakage arrested by replacing the nozzle teeth - Rectified
CL1900 | 2021-11-04 | Kangeyam | D | Yenen dispenser one side not working | Breakdown | Gowtham | 2021-11-04 | 1 Hour | Dispenser C side solenoid coil 1.5 amps fuse replaced - Working fine - Rectified
CL1901 | 2021-11-05 | Ayothiyapattinam | A | Outlet going offline due to EB power fluctuation issue | Breakdown | Prabu | 2021-11-05 | - | EB fluctuation resolved - Outlet back online - Rectified
CL1902 | 2021-11-05 | Tharamangalam | R | Control panel not working & FRL unit leakage | Breakdown | Prabu | 2021-11-05 | 30 Minutes | Control panel change over link refitted - FRL unit leakage air fitting replaced - B side nozzle teeth replaced - Working fine - Rectified
CL1903 | 2021-11-06 | Hosur | T | Unloading cant be done | Breakdown | Prabu | 2021-11-06 | - | RYB line wires changed - 3 pole 32 amp MCB changed - Unloading finished - Tank area ROV leakage arrested by applying teflon and tightening the nut - Rectified
CL1904 | 2021-11-06 | Kangeyam | T | Dispensing pump ROV leakage | Breakdown | Gowtham | 2021-11-06 | - | ROV replaced with new one - Dispensing pump spider replaced - PMR done - Rectified
CL1905 | 2021-11-06 | Musiri | T | Unloading cant be done in genset mode | Breakdown | Chandrasekar | 2021-11-06 | - | Control panel isolation transformer input power increased - Motor working normally - Rectified
CL1906 | 2021-11-07 | Vadivelan Nagar | D | C side nozzle lock pin damaged | Breakdown | Suneel Sagar | 2021-11-07 | - | Nozzle lock pin replaced - Working fine - Rectified
CL1907 | 2021-11-07 | Dharapuram | G | Unloading training | Preventive | Gowtham | 2021-11-07 | - | Unloading training completed - Compressor oil changed - Attended
CL1908 | 2021-11-08 | Cantonment | A | Automation testing | Preventive | Kamaraj | 2021-11-08 | - | C side testing done - Testing : 1 Ltr - Completed
CL1909 | 2021-11-08 | Ariyamangalam | A | Automation testing | Preventive | Nepolean | 2021-11-08 | - | D side testing done - Testing : 1.56 Ltrs - Completed
CL1910 | 2021-11-08 | T.V.Kovil | A | Automation testing | Preventive | Vignesh | 2021-11-08 | - | B & C side testing done - Testing : 2 Ltrs - Completed
CL1911 | 2021-11-08 | Hosur | A | Automation testing | Preventive | Madhavan | 2021-11-08 | - | A side testing done - Testing : 1.74 Ltrs - Completed
CL1912 | 2021-11-08 | Ramnad | T | Dispenser running continuosly | Breakdown | Kathiresan | 2021-11-08 | - | Dispensing motor running time alteration completed - Equalizer and ballvalve adjustment done - Working fine - Rectified
CL1913 | 2021-11-09 | Perambalur | G | Site visit | New Project | Dharmesh | 2021-11-09 | - | Welding work in process - Attended
CL1914 | 2021-11-09 | Attur | D | Dispenser pressure adjustment | Breakdown | Prabu | 2021-11-09 | - | Dispensing bypass valve adjusted - Pressure developed - Liquid line ballvalve leakage arrested by tightening the bolt - Unloading training completed - Batchen dispenser display LED 2 Nos replaced - Rectified
CL1915 | 2021-11-10 | Ariyamangalam | D | Batchen dispenser D side on/off switch not working | Breakdown | Vigneshwaran | 2021-11-10 | - | New on/off switch replaced - Working good - Rectified
CL1916 | 2021-11-11 | Udumalpet | C | Stamping work | Certification | Gowtham & Nivas | 2021-11-11 | - | Stamping completed - Unloading ROV LPG leakage arrested by tightening the bolt by applying the teflon - B and C side nozzles serviced - Nozzle teeth replaced at C side - Rectified
CL1917 | 2021-11-11 | Mettupalayam | C | Stamping work | Certification | Thirumalaisamy, Nivas & Gowtham | 2021-11-12 | - | Stamping completed - A side old k factor- 10200 B side old k factor- 10200 A side new k factor-10200 B side new k factor-10200 A side 10Lit=9.87 B side 10Lit=9.91 A side opening reading=315014.33 A side closing reading=315140.72 A side testing=126.39lit B side opening reading=584538.98 B side closing reading=584648.63 B side testing=109.65lit - Completed
CL1918 | 2021-11-11 | Ayothiyapattinam | T | Unloading pressure gauge not working | Breakdown | Prabu | 2021-11-11 | - | Pressure gauge replaced with new - Working fine - Rectified
CL1919 | 2021-11-12 | Namakkal 1 | D | Dispenser B side breakaway leakage | Breakdown | Prabu | 2021-11-12 | - | Breakaway leakage arrested by reassembling - Nozzle ropes changed both the sides - DOL starter stuck up released - Rectified
CL1920 | 2021-11-12 | Madurai | D | A side nozzle leakage | Breakdown | Kathiresan | 2021-11-12 | - | Nozzle teeth 4 nos replaced - Rectified
CL1921 | 2021-11-12 | Mettupalayam | T | Dispensing ROV pneumatic hose damaged & Electrical chamber from tank area to dispenser area conduit bulged | Breakdown | Thirumalaisamy, Nivas & Gowtham | 2021-11-12 | - | New pneumatic hose replaced - Spare line provided - Electrical chamber new conduit provided - Resolved
CL1922 | 2021-11-13 | Kodumudi | C | Stamping work | Certification | Thirumalaisamy, Nivas & Gowtham | 2021-11-13 | - | Stamping completed - A side old k factor- 10300 B side old k factor- 10300 A side new k factor-10300 B side new k factor-10300 A side 10Lit=9.84 B side 10Lit=9.85 A side opening reading=205287.16 A side closing reading=205650.02 A side testing=362.86lit B side opening reading=204903.60 B side closing reading=205574.93 B side testing=671.33lit Attended
CL1923 | 2021-11-13 | Perambalur | G | Welding work | New Project | Dharmesh | 2021-11-13 | - | Dispensing and decanting line welding work completed - Attended
CL1924 | 2021-11-14 | Perambalur | G | Pipeline hydro test | New Project | Dharmesh | 2021-11-15 | - | Pipeline hydro test completed at 48kg/cm2 - Attended
CL1925 | 2021-11-14 | Vedachandur | G | Online UPS not working properly | Breakdown | Kathiresan | 2021-11-21 | - | Sent to Mothish - Mother board short circuited - New mother board replaced - Rectified
CL1926 | 2021-11-14 | Ramnad | C | PESO inspection | Certification | Venkatesh & Kathiresan | 2021-11-15 | - | Inspection completed - Attended
CL1927 | 2021-11-15 | Kodungaiyur | D | A side nozzle problem | Breakdown | Suneel Sagar | 2021-11-15 | - | Nozzle replaced by new one - Rectified
CL1928 | 2021-11-16 | Avadi | G | Earthing problem | Breakdown | Suneel Sagar | 2021-11-16 | - | Connected a new earthing wire from Bus bar to isolation transformer - Earthing problem resolved - Rectified
CL1929 | 2021-11-17 | Velachery | R | Compressor cutoff problem and D side display not working | Breakdown | Suneel Sagar | 2021-11-17 | - | Dispenser pneumatic line replaced - Compressor cutoff is normal - D side display board replaced by new - Rectified
CL1930 | 2021-11-17 | Perundurai | T | Dispensing motor running only in test mode | Breakdown | Thirumalaisamy | 2021-11-17 | - | W1 conductor new NO terminal connected - Working fine - A side low flow solenoid coil fuse replaced - Testing : 0.65 Ltrs - Rectified
CL1931 | 2021-11-17 | Sankari | T | dispensing motor not running in EB mode at nights due to high voltage | Breakdown | Prabu | 2021-11-18 | - | Stabilizer parameters changed for EB RYB line 250,255,250 - Working fine - Resolved
CL1932 | 2021-11-18 | Thuraiyur | D | Dispenser bottom liquid line ballvalve with ROV leakage | Breakdown | Dharmesh | 2021-11-18 | - | ROV leakage arrested by tughtening the nut by applying teflon - Rectified
CL1933 | 2021-11-18 | Kumbakonam | D | Dispenser A side nozzle leakage | Breakdown | Vignesh | 2021-11-18 | - | Nozzle teeth replaced - Nozzle O ring replaced - Testing: 0.86 Ltrs - Rectified
CL1934 | 2021-11-18 | Dharapuram | D | Dispenser A side keypad not working properly | Breakdown | Gowtham | 2021-11-18 | - | A side keypad replaced with spare - Working fine - Rectified
CL1935 | 2021-11-18 | Perundurai | T | Dispensing motor not working in run mode | Breakdown | Thirumalaisamy | 2021-11-19 | - | Isolation transformer input supply changed(440V to 400V) output:220V=220V 24V=22.5V - Dispensing motor now working in run mode - PMR done - Rectified
CL1936 | 2021-11-19 | Bhavani | C | Calibration & stamping work | Breakdown | Prabu, Kamaraj & Adhithyan | 2021-11-20 | - | Calibration & stamping completed - A side old k factor- 10150 B side old k factor- 10150 A side new k factor-10050 B side new k factor-10050 A side 10Lit=9.98 B side 10Lit=9.99 A side opening reading=1476430.86 A side closing reading=1476690.86 A side testing=260.lit B side opening reading=1679882.38 B side closing reading=1680126.82 B side testing=244.44lit Total testing 504.44 - Attended
CL1937 | 2021-11-20 | Bathlagundu | T | Tank hydro test | New Project | Chandrasekar | 2021-11-20 | - | Hydro test completed - 29kg/cm^2 holding pressure - Completed
CL1938 | 2021-11-20 | Attur | D | Batchen dispenser A side error 11 | Breakdown | Prabu | 2021-11-20 | - | Pulsar cable adjusted - Working fine - Rectified
CL1939 | 2021-11-20 | Dharmapuri | A | Outlet going offline due to CPU issue | Breakdown | Madhavan & Prabu | 2021-11-24 | - | CPU serviced and connected - Outlet back to online - Resolved
CL1940 | 2021-11-20 | Chengalpattu | D | B side keypad is not working properly | Breakdown | Suneel Sagar | 2021-11-20 | - | Keypad replaced - Working good - Rectified
CL1941 | 2021-11-21 | Paramathivelur | R | Compressor running continuously due to the damage in the pneumatic fittings | Breakdown | Thirumalaisamy | 2021-11-21 | - | New pneumatic fittings replaced - Unloading motor V belt tension adjusted - PMR done - Rectified
CL1942 | 2021-11-21 | T.V.Kovil | A | Yenen dispenser going offline for automation maintenance | Preventive | Madhavan | 2021-11-21 | - | Dispenser back online - Maintenance completed - Resolved
CL1943 | 2021-11-22 | Thuraiyur | D | Filling point liquid and vapour ball valve stem leakage | Breakdown | Dharmesh | 2021-11-22 | - | Filling point vapour line ROV replaced - Leakage arrested - Decanding liquid line Ball valve with ROV & insulation gasket replaced - Decanting area pneumatic hose changed for 10mtrs - Rectified
CL1944 | 2021-11-22 | Kodungaiyur | G | Online UPS battery problem | Breakdown | Suneel Sagar | 2021-11-22 | - | Battery replaced with a new one - Rectified
CL1945 | 2021-11-22 | Uthamasolapuram | T | Dispensing motor pressure drop | Breakdown | Prabu | 2021-11-22 | - | Bypass valve cleaned - Tank to dispersing motor emergency pipe line changed - pressure developed - Rectified
CL1946 | 2021-11-22 | Perundurai | R | Dispensing motor nor working properly in run mode | Breakdown | Thirumalaisamy | 2021-11-22 | - | Isolation transformer voltage changed (440V to 400V) - W1 conductor replaced - W1 and W2 conductor circuit reconnected - Kept under observation - Working fine - Rectified
CL1947 | 2021-11-23 | Thirunelveli | D | Dispenser neutral problem - not working | Breakdown | Kathiresan | 2021-11-23 | 15 days | Dispenser parameter changed - Working fine - Yenen dispenser emergency switch wiring reconnection done - working fine - Rectified
CL1948 | 2021-11-23 | Namakkal 1 | T | Dispensing motor DG mode running problem | Breakdown | Prabu | 2021-11-23 | - | Isolation transformer input supply changed (440V to 450V) - Rectified
CL1949 | 2021-11-23 | Dindigul | D | Yenen nozzle swivel joint broken | Breakdown | Kamaraj | 2021-11-23 | - | Yenen nozzle replaced - Testing : 0.940 Ltrs - Working fine - Recitifed
CL1950 | 2021-11-24 | Devakottai | G | Site visit | New Project | Prakash & Vignesh | 2021-11-24 | - | Site visit completed - Attended
CL1951 | 2021-11-24 | Bathlagundu | T | CP Installation | New Project | Kamaraj | 2021-11-24 | - | CP installation completed - Attended
CL1952 | 2021-11-24 | Chengalpattu | T | Unloading line ROV with ballvalves leakage | Breakdown | Suneel Sagar | 2021-11-24 | - | Unloading line ROV with ballvalves - 25 NB, 40 NB & 50 NB - each one replaced - No leakage found - Rectified
CL1953 | 2021-11-25 | Rasipuram | G | Compressor not running due to DOL starter 18 and 19 line wire loose connection | Breakdown | Prabu | 2021-11-25 | - | Wiring reconnected - Dispenser display glasses replaced - Resolved
CL1954 | 2021-11-25 | Bathlagundu | G | Canopy and Tottem board foundation work | New Project | Kamaraj | 2021-11-25 | - | Canopy foundation bolt fixing and tottem foundation bolt fixing completed - Dispensing and decanting motor concrete bed work completed - Attended
CL1955 | 2021-11-25 | Cantonment | D | B side nozzle LPG leakage | Breakdown | Chandrasekar | 2021-11-25 | - | Nozzle teeth 4 nos replaced - Rectified
CL1956 | 2021-11-25 | T.V.Kovil | D | Yenen dispenser C side nozzle leakage | Breakdown | Vigneshwaran | 2021-11-25 | - | Nozzle teeth 4 nos replaced - Rectified
CL1957 | 2021-11-25 | Vadivelan Nagar | T | Tank 1 unloading solenoid problem | Breakdown | Suneel Sagar | 2021-11-25 | - | Unloading solenoid valve body cleaned - ROV working satisfactory - Resolved
CL1958 | 2021-11-25 | Madurai | G | Oil dispenser and Tyre inflator position alteration | Preventive | Kathiresan | 2021-11-25 | - | Oil dispenser and Tyre inflator position alteration completed - Oil dispenser testing: 1 Ltrs - Attended
CL1959 | 2021-11-26 | Udumalpet | D | Amount reversing due to over filling | Breakdown | Gowtham | 2021-11-26 | - | Advised not to fill over the capacity of fuel tank - Attended
CL1960 | 2021-11-27 | Uthamapalayam | G | CPU not working properly | Breakdown | Kamaraj | 2021-11-27 | - | CPU serviced - Power strip replaced - PMR done - Resolved
CL1961 | 2021-11-27 | Ariyamangalam | D | B side nozzle leakage | Breakdown | Nepolean | 2021-11-27 | - | Nozzle teeth 4 nos replaced - Rectified
CL1962 | 2021-11-27 | Udumalpet | T | Tank 2 pressure dropped while dispensing | Breakdown | Gowtham | 2021-11-27 | - | Bypass valve cleaned - Pressure drop controlled - Rectified
CL1963 | 2021-11-27 | Theni | G | Unloading training | Preventive | Kamaraj | 2021-11-27 | - | Unloading training completed - Fire extinguisher refillings done for 75 Kg and 9 Kg - Attended
CL1964 | 2021-11-27 | Rasipuram | D | Dispenser cut off problem & Dispesing motor not running properly | Breakdown | Prabu | 2021-11-27 | - | On/off switch element reconnected - LPG flow valve adjusted - Dispenser cutoff working fine - Isolation transformer input supply changed (440 V to 400 V) - Working fine - Rectified
CL1965 | 2021-11-27 | Namakkal 2 | T | Tank area liquid line ROV leakage | Breakdown | Prabu | 2021-11-27 | - | ROV leakage arrested by tightening the nut by applying teflon - Rectified
CL1966 | 2021-11-27 | Palayam | G | Fire extinguisher power released automatically | Breakdown | Thirumalaisamy | 2021-11-27 | - | 75Kg fire refill done by Prevention pro - Rectified
CL1967 | 2021-11-29 | Namakkal 1 | C | Stamping work | Certification | Dharmesh & Prabu | 2021-11-29 | - | Calibration and stamping completed - A side old k factor- 10150 B side old k factor- 10150 A side new k factor-10150 B side new k factor-10150 A side 10Lit=10.03 B side 10Lit=9.96 A side testing= 140.26lit B side testing= 170.23lit Total testing 310.49 - Compressor belt replaced - Rectified
CL1968 | 2021-11-29 | Rasipuram | C | Stamping work | Certification | Dharmesh & Prabu | 2021-11-29 | - | Calibration and stamping completed - A side k factor- 10050 B side k factor- 10100 A side 10Lit=10.06 B side 10Lit=9.91 A side testing= 182.86lit B side testing= 121.51lit Total testing 395.37 lit - Attended
CL1969 | 2021-11-29 | T.V.Kovil | A | Outlet going offline for earth checking | Preventive | Madhavan | 2021-11-29 | - | Earth regenerated - Outlet back online - Completed
CL1970 | 2021-11-30 | Melur | D | Dispenser pressure problem | Breakdown | Kathiresan | 2021-11-30 | - | Dispensing motor bypass valve and equalizer ball valve adjusted - Dispensing pressure developed - Resolved
CL1971 | 2021-11-30 | Aravakurichi | A | Outlet running offline due to coverter board damage | Breakdown | Thirumalaisamy | 2021-12-28 | - | Dispenser requires separate chemical earth - Chemical earth installed - RS485 to USB converter board changed newly - Automation maintenance done - Dispenser bottom ROV with ballvalve LPG leakage arrested by tightening the bolt - Neutral to Earth 1.7volt - Rectified
CL1972 | 2021-11-30 | Bhavani | D | Dispenser display is not clear | Preventive | Prabu | 2021-11-30 | - | Display fiber glass replaced for dispenser A and B side - Rectified
CL1973 | 2021-11-30 | Chengalpattu | T | Unloading line PRV is not working properly | Breakdown | Suneel Sagar | 2021-11-30 | - | PRV replaced 2 nos and 3/4" stud replaced 4 nos - Resolved
CL1974 | 2021-12-01 | Theni | C | Calibration & Stamping work | Certification | Dharmesh & Nivas | 2021-12-01 | - | Calibration and stamping completed - A side old k factor- 106700 B side old k factor- 108500 A side new k factor-106700 B side new k factor-108500 A side opening reading=615944.39 A side closing reading=616093.90 A side testing=149.51 B side opening reading=509408.60 B side closing reading=509595.89 B side testing=187.24 lit Total testing = 336.75 lit - Rectified
CL1975 | 2021-12-01 | Bodi | C | Stamping work | Certification | Dharmesh & Nivas | 2021-12-01 | - | Stamping completed - N2 machine pressure gauge Pneumatic tube spare replaced - Resolved
CL1976 | 2021-12-01 | Uthamapalayam | C | Stamping work | Certification | Dharmesh & Nivas | 2021-12-01 | - | Stamping completed - Attended
CL1977 | 2021-12-01 | Avinashi | T | Leakage at tank 1 equalizer teflon bush | Breakdown | Gowtham | 2021-12-01 | - | Leakage arrested by applying anabond in teflon bush - Rectified
CL1978 | 2021-12-06 | Rasipuram | T | Unloading liquid line ROV leakage | Breakdown | Prabu | 2021-12-06 | - | Unloading ROV with ball valve leakage arrested by tightening the stem and applied teflon - Rectified
CL1979 | 2021-12-07 | Virudhachalam | C | Rule 18 and stamping work | Certification | Dharmesh & Chandrasekar | 2021-12-07 | - | Rule 18 completed - Ground earth regenerated - Dispensing and decanting line ROV LPG leakage arrested - Dispensing bypass valve and equalizer valve adjusted - Stamping and calibration completed - PMR done A side k factor - 10100 B side k factor - 10200 Both side K factor no change A side testing litre - 188.55 B side testing litre - 172.19 Total litre - 360.74 A side 10 ltr - 9.98 B side 10 ltr - 9.97 - Resolved
CL1980 | 2021-12-07 | Attur | D | Batchen dispenser B side error 11 | Breakdown | Prabu | 2021-12-07 | - | Dispenser pulsar box and cables replaced - Working fine - Rectified
CL1981 | 2021-12-07 | Chengalpattu | G | Emergency switch NC element worn out | Breakdown | Suneel Sagar | 2021-12-07 | - | Fill point emergency push button replaced with new one - Emergency switch performance found satisfactory - Rectified
CL1982 | 2021-12-08 | Manapparai | G | Online UPS not working properly | Breakdown | Nivas | 2021-12-23 | - | Online UPS serviced by Mothish - B side nozzle teeth 4 nos replaced - - Rectified
CL1983 | 2021-12-08 | Kodungaiyur | C | Stamping work | Certification | Suneel Sagar | 2021-12-08 | - | Stamping completed - Attended
CL1984 | 2021-12-08 | Velachery | T | Unloading venting ball valve and dispensing pneumatic connector damaged | Breakdown | Suneel Sagar | 2021-12-08 | - | Venting ball valve replaced - Tank 2 dispensing pneumatic connector replaced - Rectified
CL1985 | 2021-12-08 | Vadivelan Nagar | D | C side nozzle not working properly | Breakdown | Suneel Sagar | 2021-12-08 | - | Nozzle cleaned and serviced - Working fine - Rectified
CL1986 | 2021-12-08 | Bathlagundu | T | Material receipt and tank inside liquid line and vapour line pipes alteration | New Project | Kamaraj | 2021-12-10 | - | Materials received and tank inside pipe alteration done - Excess flow valve fixed for both flanges - Completed
CL1987 | 2021-12-09 | Neelambur | D | Dispenser pressure problem | Breakdown | Gowtham | 2021-12-09 | - | DP valve plunger tension adjusted - Operation found satisfactory - Rectified
CL1988 | 2021-12-11 | Bathlagundu | G | Dispensing decanting motors placing | New Project | Kamaraj | 2021-12-11 | - | Dispensing decanting motors placed - Tank to dispensing motor liquid line and vapour lines connected - Completed
CL1989 | 2021-12-11 | Ayothiyapattinam | G | Unloading training | Preventive | Prabu | 2021-12-11 | - | Unloading training completed - Attended
CL1990 | 2021-12-11 | Uthamasolapuram | T | Dispensing motor spider damaged | Breakdown | Prabu | 2021-12-11 | - | Spider replaced - Motor alignment checked- Working fine - Rectified
CL1991 | 2021-12-11 | Palladam | D | Dispenser C side excess flow valve broken | Breakdown | Gowtham | 2021-12-12 | - | Excess flow valve 3/4" repalced with new one - Working satisfactory - Rectified
CL1992 | 2021-12-11 | Ariyamangalam | A | C and D nozzle going offline for automation maintenance | Preventive | Madhavan | 2021-12-11 | - | Maintenance completed - C and D nozzles back online - Resolved
CL1993 | 2021-12-12 | Bathlagundu | T | Welding work | New Project | Kamaraj | 2021-12-12 | - | Decanting motor to tank inlet welding completed - Cable and Earth flat measurement done - Attended
CL1994 | 2021-12-12 | Palakkad | G | Mass flow meter calibration - FCRI | Preventive | Dharmesh & Gowtham | 2021-12-14 | - | Mass flow meter calibrated at FCRI - Completed
CL1995 | 2021-12-12 | T.V.Kovil | T | Unloading motor belt damaged | Breakdown | Vignesh | 2021-12-12 | - | Motor belt replaced with new - Working fine - Rectified
CL1996 | 2021-12-13 | Madurai | G | PMR work | Preventive | Kathiresan | 2021-12-13 | - | Compressor oil changed - Total leakage checked - PMR done - Attended
CL1997 | 2021-12-13 | Dindigul | C | Stamping work | Certification | Kamaraj | 2021-12-13 | - | Stamping compelted - Attended
CL1998 | 2021-12-14 | Bathlagundu | G | GI earth pipe welding work | New Project | Kamaraj | 2021-12-14 | - | GI Earth pipe welding completed - Tank to dispensing motor liquid line welding completed - Rectified
CL1999 | 2021-12-14 | Melur | A | Outlet going offline due to automation CPU problem | Breakdown | Kathiresan | 2021-12-16 | - | Dispensing bypass valve cleaned - CPU replaced with new one - Outlet back online - Working good - Rectified
CL2000 | 2021-12-14 | Vadivelan Nagar | T | Dispensing motor with pump not working | Breakdown | Suneel Sagar, Vignesh & Nivas | 2021-12-18 | 10 Hours | Dispensing motor with pump replaced by standby pump - Rectified temporarily - Dispensing motor coil rewinded - Pump serviced - Working fine - Rectified
CL2001 | 2021-12-15 | Bathlagundu | G | Pipeline hydro test | New Project | Kamaraj | 2021-12-15 | - | Dispensing motor to dispenser pipeline hydro test completed - Testing pessure 48kg/cm^2 - Dispeser bottom frame installed - Completed
CL2002 | 2021-12-15 | Dharmapuri | G | Genset servicing | Preventive | Prabu | 2021-12-15 | - | Genset filter and oil changed - Total leakage tested - PMR done - Working fine - Completed
CL2003 | 2021-12-15 | Thiruvaiyaru | G | Site visit | New Project | Prakash & Prasath | 2021-12-15 | - | Site visit completed - Attended
CL2004 | 2021-12-15 | Pudukkottai | D | Dispensing air solenoid coil air leakage | Breakdown | Nepolean | 2021-12-15 | - | Air solenoid coil replaced - Working fine - Rectified
CL2005 | 2021-12-15 | Avinashi | T | Tank 2 dispensing problem due to air hose damage | Breakdown | Gowtham | 2021-12-15 | - | New air hose replaced - D side nozzle teeth 4 nos replaced - Working fine - Rectified
CL2006 | 2021-12-15 | Madurai | T | Circuit installation for Dispensing and unloading at the same for Tank1 and Tank 2 respectively | Preventive | Kathiresan | 2021-12-15 | - | Circuit installed - Working properly - ATG cut off at 84% - found satisfactory - Completed
CL2007 | 2021-12-16 | Palayam | C | Calibration work | Certification | Dharmesh & Thirumalaisamy | 2021-12-16 | - | Calibration completed A side k factor- 10000 B side k factor- 10000 A side 10Lit=10.03 B side 10Lit=10.04 A side opening reading=75650.97 A side closing reading=75783.38 A side testing=132.41lit B side opening reading=66215.34 B side closing reading=66354.87 B side testing=139.53lit Dispensing line bypass valve adjusted and Equalizer line ball valve adjusted - Resolved
CL2008 | 2021-12-17 | Velachery | C | Calibration work | Certification | Dharmesh & Pandi Durai | 2021-12-17 | - | Calibration completed A side 10Lit=10.08 B side 10Lit=10.04 C side 10Lit=10.12 D side 10Lit=10.13 A side opening reading=1644495.92 A side closing reading=1644596.12 A side testing=100.2Lit B side opening reading=1079344.04 B side closing reading=1079466.00 B side testing=121.96Lit C side opening reading=918025.81 C side closing reading=918122.04 C side testing=96.24Lit D side opening reading=363893.43 D side closing reading=363984.68 D side testing=91.25Lit Total Testing Lit= 409.64 - Attended
CL2009 | 2021-12-17 | Bathlagundu | D | Dispenser installation | New Project | Kamaraj | 2021-12-17 | - | Dispenser installation completed - Attended
CL2010 | 2021-12-17 | Vadivelan Nagar | C | Calibration work | Certification | Dharmesh & Pandi Durai | 2021-12-17 | - | Calibration completed A side old k factor- 10070 B side old k factor- 10060 C side old k factor- 10060 D side old k factor- 10100 A side new k factor- 10110 B side new k factor- 10160 C side new k factor- 10060 D side new k factor- 10100 A side 10Lit=10.07 B side 10Lit=10.04 C side 10Lit=10.13 D side 10Lit=10.08 A side opening reading=1325651.94 A side closing reading=1325864.12 A side testing=212.18Lit B side opening reading=316127.86 B side closing reading=316329.73 B side testing=201.87Lit C side opening reading=842371.32 C side closing reading=842475.11 C side testing=103.79Lit D side opening reading=71325.26 D side closing reading=71452.19 D side testing=126.93Lit Total Testing Lit= 644.77 - Attended
CL2011 | 2021-12-18 | Velachery | C | Stamping work | Certification | Dharmesh & Pandi Durai | 2021-12-18 | - | Stamping completed - Attended
CL2012 | 2021-12-18 | Vadivelan Nagar | C | Stamping work | Certification | Dharmesh & Pandi Durai | 2021-12-18 | - | Stamping completed - Attended
CL2013 | 2021-12-18 | Namakkal 2 | D | Dispenser B side breakaway leakage | Breakdown | Prabu | 2021-12-18 | - | Leakage arrested - Nozzle rope changed - Testing : 1.42 Ltrs - Rectified
CL2014 | 2021-12-18 | Bathlagundu | G | Welding work | New Project | Kamaraj | 2021-12-18 | - | Tank area liquid line vapour line welding completed - Fill point to tank inlet pipe line hydro test done - Testing pressure : 48kg/cm^2 - No leakage - Found satisfactory - Completed
CL2015 | 2021-12-19 | Perambalur | T | Tank Nitrogen testing | New Project | Avinash | 2021-12-19 | - | N2 test completed - Tested at 14.5kg/ cm^2 - Holding pressure - 10 kg / cm^2 - Resolved
CL2016 | 2021-12-20 | Uthamapalayam | D | Dispenser A side LPG slow delivery | Breakdown | Kamaraj | 2021-12-20 | - | Equalizer bypass valve adjusted - High flow low flow solenoid coil cleaned - Slow delivery arrested - Rectified
CL2017 | 2021-12-20 | Thiruvaiyaru | G | Pipeline hydro test | New Project | Vignesh & Pandi Durai | 2021-12-20 | - | Pipeline hydro test completed - Testing Pressure : 48 kg/cm^² - No leakage - Attended
CL2018 | 2021-12-20 | Ramnad | T | Dispenser pressure problem | Breakdown | Kathiresan | 2021-12-20 | - | Dispensing pump bypass valve and equalizer valve adjusted - Pressure developed - Dispenser bottom ROV leakage arrested by tightening the nut - Tank to ATG configuration completed - Working fine - Rectified
CL2019 | 2021-12-20 | Kumbakonam | D | Dispenser B side keypad not working | Breakdown | Vignesh | 2021-12-20 | - | Keypad replaced - Unloading ROV leakage arrested by tightening the nut and applied teflon - Working fine - Rectified
CL2020 | 2021-12-21 | Tharamangalam | D | Dispenser bottom liquid line ballvalve leakage - Dispenser run mode not working | Breakdown | Prabu | 2021-12-21 | - | Ball valve leakage arrested by tightening the nut - Dispenser glass fuse changed - A side nozzle teeth replaced - Rectified
CL2021 | 2021-12-21 | Bathlagundu | C | Rule 33 data collection | New Project | Kamaraj | 2021-12-21 | - | Rule 33 data collected - Dispensing pipe line hydro test completed - Trench work in process - Attended
CL2022 | 2021-12-21 | Thiruvaiyaru | T | STP motor testing | New Project | Prakash, Prasath & Dharmesh | In process | - | In process
CL2023 | 2021-12-21 | Virudhunagar | D | Dispenser A side nozzle leakage | Breakdown | Kathiresan | 2021-12-21 | - | A side nozzle teeth replaced - Working fine - Rectified
CL2024 | 2021-12-21 | Palladam | D | Dispenser D side excess flow valve not working properly as its stud broken | Breakdown | Gowtham | 2021-12-21 | - | Excess flow valve stud and nut replaced - Working fine - Testing : 2 Ltrs - Rectified
CL2025 | 2021-12-21 | Sankari | R | Compresssor not running properly | Breakdown | Prabu | 2021-12-21 | - | Compressor starter damaged to be replaced from frank - Compressor line directed - Rectified temporarily
CL2026 | 2021-12-21 | Dindigul | D | Dispenser B side nozzle teeth damaged | Breakdown | Kamaraj | 2021-12-21 | - | B side nozzle teeth replaced - Working fine - Rectified
CL2027 | 2021-12-22 | Thiruvaiyaru | G | Electrical work | New Project | Dharmesh | 2021-12-25 | - | Electrical work completed - Attended
CL2028 | 2021-12-22 | Bathlagundu | G | Dispensing motor to dispenser liquid and vapour pipe line welding work | New Project | Kamaraj | 2021-12-22 | - | Welding work completed - Earth flat welding in process - Attended
CL2029 | 2021-12-22 | Theni | R | Servo stabilizer control panel board short circuited | Breakdown | Kamaraj | 2021-12-27 | - | Servo stabilizer serviced - Dispenser liquid line LPG leakage arrested - Rectified
CL2030 | 2021-12-23 | Tirunelveli | C | Stamping work | Certification | Kathiresan & Vignesh | 2021-12-24 | - | Stamping completed - Calibration report = 'A' side 10 ltrs = 10.04 'B' side 10 ltrs = 10.08 'C' side 10 ltrs = 9.99 'D' side 10 ltrs = 9.98 "K" factor report= "A" side Old 'K' =103000 "A" side New 'K'=101700 "B " side old 'K'= 102000 "B" side New 'K' =101400 "C" side old 'K' =10000 "C" side New 'K'=10341 "D" side old 'K'= 10000 "D" side New 'K' =10330 Total testing ltrs= 676.51 EB room to tank area T1 unloading air hose 30mtrs changed - Rectified
CL2031 | 2021-12-24 | Virudhunagar | A | Automation CPU software updation | Preventive | Kathiresan & Vignesh | 2021-12-24 | - | Software updated - Kept under observation for 2 hours - working fine - New 10 kg fire extinguishers 2 nos replaced - Recitife
CL2032 | 2021-12-24 | Bathlagundu | T | Dispensing motor to dispenser liquid and vapour pipe line work | New Project | Kamaraj | 2021-12-24 | - | Dispensing motor to dispenser liquid and vapour pipe line work completed - Cables chamber to tank area hose measurement done - Completed
CL2033 | 2021-12-24 | Palladam 2 | T | Tank 2 pit marking | New Project | Gowtham | 2021-12-24 | - | Tank pit marking done - Civil work in process - Completed
CL2034 | 2021-12-24 | Perambalur | G | Site visit | New Project | Prakash, Chandrasekar & Avinash | 2021-12-24 | - | EB line, Pavor blocks and pipeline connections instruction given - Attended
CL2035 | 2021-12-25 | Namakkal 2 | G | Diesel genset servicing | Preventive | Prabu | 2021-12-25 | - | Genset fuel filter, oil filter and oil changed - TP link fixed outside the office room - Completed
CL2036 | 2021-12-25 | Paramathivelur | D | Dispenser display housing faded & Dispensing motor spider damaged | Preventive | Thirumalaisamy | 2021-12-25 | - | Display housing glass changed - Dispensing motor spider replaced - Automation and online UPS maintenance done - Rectified
CL2037 | 2021-12-25 | Bathlagundu | G | Trench and motor bed shed work | New Project | Kamaraj | 2021-12-25 | - | Trench and Motor bed shed work completed - Dispensing pipeline covered with tarfelt sheet - Attended
CL2038 | 2021-12-26 | Neelambur | T | Bypass valve top mount replacement | Breakdown | Gowtham | 2021-12-26 | - | Bypass valve top mount along adjustable bolt replaced - Unloading completed - Found satisfactory - Rectified
CL2039 | 2021-12-26 | Palayam | D | Dispenser slow delivery dut to dispensing motor suction problem | Breakdown | Thirumalaisamy | 2021-12-26 | - | Dispensing bypass valve cleaned and equalizer line ball valve adjusted - Pressure developed - Slow delivery Rectified
CL2040 | 2021-12-27 | Bathlagundu | G | Cable conduit pipe line connection | New Project | Kamaraj | 2021-12-27 | - | Chamber to chamber Cable conduit pipe line connected - Attended
CL2041 | 2021-12-27 | Madurai | D | A side keypad not working | Breakdown | Kathiresan | 2021-12-27 | - | Keypad interchanged from B side for programming access - B side keypad to be replaced - Temporarily Rectified
CL2042 | 2021-12-28 | Thiruvaiyaru | G | Welding work | New Project | Dharmesh | 2021-12-29 | - | above ground motor pipe line welding completed - Pipeline water hydro test completed - Testing pressure 48 Kg/Cm^2 - Batchen dispenser B side meaturing unit seal kit & bearing changed - Rectified
CL2043 | 2021-12-28 | Velachery | T | Tank 1 dispensing liquid line ball valve stem leakage | Breakdown | Suneel Sagar | 2021-12-28 | - | Dispensing liquid line ball valve stem leakage arrested by tightening the bolt and applying the teflong - Rectified
CL2044 | 2021-12-28 | Sankari | G | Compressor not working | Breakdown | Prabu | 2021-12-29 | - | Air compressor starter and oil changed - Air pressure switch and safety relief valve adjusted - Working fine - Rectified
CL2045 | 2021-12-29 | Bathlagundu | G | Site visit | New Project | Kamaraj | 2021-12-29 | - | Canopy and fencing line work in process - Attended
CL2046 | 2021-12-31 | Ariyalur | G | Dispensing and Decanting pump and motor & Dispenser commissioning | New Project | Prakash & Prabu | 2021-12-31 | - | Pump Motor and Dispenser commissioning completed - Attended
CL2047 | 2021-12-31 | Virudhunagar | T | Unloading side 50 NB ball valve stem leakage | Breakdown | Kathiresan | 2021-12-31 | - | Unloading side 50 NB ball valve stem leakage arrested by tightening the bolt and teflon applied - Rectified
CL2048 | 2021-12-31 | Perambalur | T | Dispensing pump and motor commissioning & Dispenser stamping | New Project | Dharmesh, Chandrasekar & Pandi Durai | 2021-12-31 | - | Dispensing pump and motor commissioning & Dispenser stamping completed - Unloading completed - Attended
CL2049 | 2021-12-31 | Chengalpattu | D | Yenen dispenser keypad not working properly | Breakdown | Suneel Sagar | 2021-12-31 | - | Dispenser keypad changed - Resolved