## All
Service Logs - Jan' 2022 to Dec' 2022
ticket_no | date | name_of_the_outlet | code | nature_of_the_complaint | breakdown__ preventive | service_engineer | rectified_on | interruption_of_sales_if_any__time_duration | details_of_work_done
CL2050 | 2022-01-01 | Perambalur | A | Commissioning work | New Project | Madhavan, Chandrasekar & Dharmesh | 2022-01-02 | - | Commissioning and inauguration work completed - Attended
CL2051 | 2022-01-01 | Ariyalur | A | Commissioning work | New Project | Madhavan, Chandrasekar & Dharmesh | 2022-01-02 | - | Commissioning and inauguration work completed - Attended
CL2052 | 2022-01-01 | Palladam | D | C side nozzle teeth damaged | Breakdown | Gowtham | 2022-01-01 | - | Nozzle teeth 4 nos replaced - Rectified
CL2053 | 2022-01-01 | Bathlagundu | G | Canopy installation and fencing work | New Project | Kamaraj | 2022-01-01 | - | Canopy installation and fencing work completed - Attended
CL2054 | 2022-01-02 | Neelambur | T | Unloading training and Dispenser pressure drop | Breakdown | Gowtham | 2022-01-02 | - | Unloading training completed - Pressure drop adjusted by cleaning dispensing bypass valve - Rectified
CL2055 | 2022-01-03 | Thanjavur | D | Dispenser B side keypad and rochester not working properly | Breakdown | Nepolean & Dharmesh | 2022-01-06 | - | Rochester gauge adjusted and dial cleaned - Working fine - Rectified
CL2056 | 2022-01-04 | Devakottai | G | Site visit | New Project | Prakash &Vignesh | 2022-01-04 | - | Site visit completed - Attended
CL2057 | 2022-01-05 | Musiri | T | Ballvalve with ROV stem LPG leakage, printer relocation and PMR | Breakdown | Dharmesh & Nivas | 2022-01-05 | - | Ballvalve with ROV stem tightened - Leakage arrested - Printer relocated - PMR done - Resolved
CL2058 | 2022-01-05 | Palayam | D | Dispenser slow delivery due suction problem | Breakdown | Thirumalaisamy | 2022-01-05 | - | Bypass valve cleaned - Equalizer ball valve adjusted - Suction pressure developed - Rectified
CL2059 | 2022-01-05 | Mettupalayam | D | Dispenser slow delivery due suction problem | Breakdown | Gowtham | 2022-01-05 | - | Bypass valve cleaned - PMR done - Suction pressure developed - Rectified
CL2060 | 2022-01-05 | Vedachandur | C | Calibration work | Certification | Kamaraj & Pandi Durai | 2022-01-05 | - | Calibration completed - A side old k factor- 10000 B side old k factor- 10000 A side new k factor-10080 B side new k factor-10100 A side 10Lit=9.99 B side 10Lit=9.98 A side opening reading=75740.91 A side closing reading=76298.60 A side testing=512.16lit B side opening reading=63964.91 B side closing reading=64431.57 B side testing=482.26lit Total testing litre= 994.42 lit - Attended
CL2061 | 2022-01-05 | Villapuram | D | B side nozzle teeth problem | Breakdown | Kathiresan | 2022-01-05 | - | Nozzle teeth 4 nos replaced - Rectified
CL2062 | 2022-01-06 | Pudukkottai | D | Dispenser slow delivery due suction problem | Breakdown | Nivas | 2022-01-06 | - | Bypass valve cleaned - Equalizer ball valve adjusted - Suction pressure developed - Rectified
CL2063 | 2022-01-06 | Thuraiyur | T | Unloading vapour hose leakage | Breakdown | Vignesh & Pandi Durai | 2022-01-06 | - | Vapour hose replaced - Tank area to EB room pneumatic hose replaced - PMR done - Rectified
CL2064 | 2022-01-06 | Kodumudi | T | Decanting pneumatic hose leakage | Breakdown | Thirumalaisamy | 2022-01-06 | - | Pneumatic hose replaced - Dispensing line ROV with ball valve LPG leakage arrested by tightening the bolt - PMR done - Rectified
CL2065 | 2022-01-06 | Ariyalur | C | Calibration work | Certification | Chandrasekar & Dharmesh | 2022-01-06 | - | Calibration completed - A side k factor- 10000 B side k factor- 10000 A side 10Lit=9.98 B side 10Lit=9.98 A side opening reading=729.76 A side closing reading=854.62 A side testing=124.86 lit B side opening reading=711.69 B side closing reading=839.95 B side testing=128.26 lit Total testing litre= 253.12 lit - Attended
CL2066 | 2022-01-06 | Perambalur | C | Calibration work | Certification | Chandrasekar & Dharmesh | 2022-01-06 | - | Calibration completed - A side k factor- 10000 B side k factor- 10000 A side opening reading=1663.17 A side closing reading=1769.41 A side testing=106.24 lit B side opening reading=1201.08 B side closing reading=1310.76 B side testing=109.68 lit Total testing litre= 215.92 lit - Attended
CL2067 | 2022-01-07 | Dharmapuri | D | Dispenser breakaway leakage | Breakdown | Prabu | 2022-01-07 | - | Breakaway leakage arrested - Hose ropes replaced - Rectified
CL2068 | 2022-01-07 | Bathlagundu | G | Cable laying and air hose laying | New Project | Kamaraj | 2022-01-07 | - | Cable and air hose laying completed - Control Panel and DP panel installation completed - Attended
CL2069 | 2022-01-10 | Ariyamangalam | D | A side nozzle teeth damaged | Breakdown | Nivas | 2022-01-10 | - | Nozzle teeth 4 nos replaced - Rectified
CL2070 | 2022-01-10 | Velachery | T | Veedor Root ATG output relay box power adapter defected | Breakdown | Suneel Sagar | 2022-01-10 | - | Relay box power adapter replaced - New switch board arranged to bypass ups supply if required - Resolved
CL2071 | 2022-01-10 | Villapuram | R | Office room emergency room switch position replacement | Preventive | Kathiresan | 2022-01-10 | - | Emergency switch position replaced - Working fine - Rectified
CL2072 | 2022-01-10 | Palladam - 2 | T | Tank installation | New Project | Gowtham | 2022-01-10 | - | Tank installation completed - Attended
CL2073 | 2022-01-11 | Kumbakonam | G | Fire extinguisher refilling | Preventive | Pandi Durai | 2022-01-11 | - | Fire extinguisher 75Kg and 9 kg refilling work done - Resolved
CL2074 | 2022-01-11 | Thiruvaiyaru | T | Tank N2 test | New Project | Chandrasekar & Dharmesh | 2022-01-11 | - | Nitrogen test completed - Testing pressure 14.5 Kg/cm2.Holding pressure 10 Kg/cm2 - Resolved
CL2075 | 2022-01-11 | Avadi | C | PMR work | Preventive | Suneel Sagar | 2022-01-11 | - | PMR done - Completed
CL2076 | 2022-01-12 | Hosur | R | Air compressor air leakage | Breakdown | Suresh | 2022-01-12 | - | Air leakage arrested by replacing a new ball valve - Working fine - Rectified
CL2077 | 2022-01-13 | Manapparai | R | Dispensing / unloading selector switch damaged | Breakdown | Nivas | 2022-01-13 | - | New selector switch replaced - Replaced
CL2078 | 2022-01-13 | Thiruvaiyaru | R | Control panel testing | New Project | Prakash & Chandrasekar | 2022-01-13 | - | Control panel testing done - ROV pneumatic line and dispenser tested - Completed
CL2079 | 2022-01-14 | T.V.Kovil | R | Compressor oil changing | Preventive | Vignesh | 2022-01-14 | - | Oil changed in both compressors - Rectified
CL2080 | 2022-01-15 | Avinashi | R | Compressor motor coil got short circuit | Breakdown | Gowtham | 2022-01-15 | - | Compressor motor replaced by spare motor - Working fine - Rectified
CL2081 | 2022-01-15 | Ariyamangalam | D | Dispenser B side on/off switch damaged | Breakdown | Nivas | 2022-01-15 | - | On/ Off switch replaced in B side - Working fine - Replaced
CL2082 | 2022-01-15 | Vadivelan Nagar | D | A side dispensing hose damaged | Breakdown | Suneel Sagar | 2022-01-15 | - | Dispensing hose replaced - Resolved
CL2083 | 2022-01-15 | Karur | D | B side low flow and cutoff problem | Breakdown | Thirumalaisamy | 2022-01-15 | - | High flow low flow solenoid coil cleaned - Working fine - Testing: 40.15 Ltrs - Rectified
CL2084 | 2022-01-17 | Sulur | T | Air hose leakage | Breakdown | Gowtham | 2022-01-17 | - | Dispensing pump air hose replaced - Working fine - PMR done - Rectified
CL2085 | 2022-01-17 | Namakkal 2 | R | Compressor oil drain line nut broken | Breakdown | Prabu | 2022-01-17 | - | Compressor oil changed - Oil drain nut fixed with araldite - No oil leakage - Resolved
CL2086 | 2022-01-17 | Avinashi | R | Stabilizer operation failed in servo mode due to surge arrester R phase fuse got damaged | Breakdown | Gowtham | 2022-01-17 | - | New fuse replaced - Panel working normally - Stabilizer under operation - Pressure gauge changed - Rectified
CL2087 | 2022-01-18 | Bathlagundu | G | Yard light post installation | New Project | Kamaraj | 2022-01-18 | - | Light post installed - Office room wiring done - Pavor blocks instruction given - Completed
CL2088 | 2022-01-19 | Cantonment | C | Canopy rework and Rule 19 | Certification | Prakash | 2022-01-29 | - | Tank 2 rule 19 completed on 21.01.2022 - N2 testing done - Tank 1 rule 19 completed on - 24.09.2022 Canopy work done on - 29.01.2022 - Resolved
CL2089 | 2022-01-19 | Pudukkottai | R | Control panel master solenoid coil not working | Breakdown | Vignesh | 2022-01-19 | - | Master solenoid coil replaced - Working fine - Rectified
CL2090 | 2022-01-20 | Theni | D | A side breakaway coupling LPG leakage | Breakdown | Kamaraj | 2022-01-20 | - | New breakaway coupling replaced - No leakage - Resolved
CL2091 | 2022-01-20 | Chengalpattu | C | PMR work | Preventive | Suneel Sagar | 2022-01-20 | - | PMR done - Completed
CL2092 | 2022-01-21 | Dharmapuri | C | Stamping work | Certification | Prabu | 2022-01-21 | - | Dispenser stamping completed - Attended
CL2093 | 2022-01-21 | Melur | R | Servo stabilizer makes noise and vibration & Dispenser pressure problem | Breakdown | Kathiresan | 2022-01-21 | - | Stabilizer "B"phase winding carbon bush refitmene done - Dispenser motor bypass valve cleaned.Pressure 10.5 kg. ALDS compressor (NRV) serviced by ELGI service persons. Dispenser working condition - Rectified
CL2094 | 2022-01-21 | Musiri | T | Dispenser slow delivery due suction problem | Breakdown | Dharmesh & Chandrasekar | 2022-01-21 | - | Tank to dispensing motor emergency spare pipe line changed - Dispensing motor bypass valve cleaned - Working fine - Rectified
CL2095 | 2022-01-21 | Hosur | T | Compressor not working | Breakdown | Prabu | 2022-01-23 | - | Compressor serviced by Frank service persons - Compressor oil changed - GI air line leakage arrested - PMR done - Completed
CL2096 | 2022-01-22 | Bathlagundu | G | Wiring connection and pipeline work | New Project | Kamaraj | 2022-01-22 | - | All equipment wiring connection completed - Tank area pipe line and office room painting work completed - Tottem board installed - Resolved
CL2097 | 2022-01-25 | Tharamangalam | T | Tank area air hose damaged | Breakdown | Prabu | 2022-01-25 | - | Tank area to EB Room new air hose changed - B side nozzle teeth 4 nos replaced - Rectified
CL2098 | 2022-01-25 | Thanjavur | T | Unloading process cant be done in Genset mode | Breakdown | Nepolean | 2022-01-25 | - | Transformer input voltage adjusted - Unloading can be done in Genset mode - Rectified
CL2099 | 2022-01-25 | Palladam 2 | T | Tank hydro test | New Project | Gowtham | 2022-01-25 | - | Hydro test completed at 28 kg/cm2 - Attended
CL2100 | 2022-01-26 | Villapuram | G | Genset engine vibrating and load unbalanced | Breakdown | Kathiresan | 2022-01-26 | - | Genset electic dynamo replaced with new one - Working fine - Rectified
CL2101 | 2022-01-26 | Cantonment | D | Batchen dispenser testing | Preventive | Nepolean | 2022-01-26 | - | Testing completed - 25/1/2022 _ night shift OFF line testing A side : 12.45 lit B side : 13.14 lit Total Testing : 25.59lit 26/1/2022 __ Day shift ON line testing A side : 162.57 lit B side : 326.97 lit Total Testing : 489.54 lit A side k factor: 100300 B side k factor : 100100 B side new k factor changed : 103000 - Completed
CL2102 | 2022-01-26 | T.V.Kovil | D | Batchen dispenser B side on / off switch not working properly | Breakdown | Vignesh | 2022-01-26 | - | New on / off switch replaced - Working fine - Rectified
CL2103 | 2022-01-27 | Bathlagundu | T | Nitrogen testing | New Project | Kamaraj | 2022-01-28 | - | Nitrogen test completed - Testing pressure 14.5 Kg/cm2.Holding pressure 10 Kg/cm2 - All pipe line purging done - No leakage - Found satisfactory - Resolved
CL2104 | 2022-01-27 | Virudhunagar | G | Electrical line problem | Breakdown | Kathiresan | 2022-01-27 | - | Electrical line checked - RS485 to USB converter board replaced - Earth regenerated - Working fine - Resolved
CL2105 | 2022-01-27 | Palladam 2 | T | CP installation | New Project | Gowtham | 2022-01-27 | - | CP installed - Completed
CL2106 | 2022-01-27 | Cantonment | D | Batchen dispenser testing | Preventive | Vignesh | 2022-01-27 | - | Testing completed - A side:43.00 lit B side:12.11 lit Total Testing :55.11 ltrs - Completed
CL2107 | 2022-01-27 | Tharamangalam | R | Control panel ESC contactor - NO wire loosened | Breakdown | Prabu | 2022-01-27 | - | Control panel ESC contactor - NO wire recorrected - Rectified
CL2108 | 2022-01-28 | Thuraiyur | T | Unloading problem and servo stablizer not working properly | New Project | Nepolean | 2022-01-28 | - | Unloading pump soft wheel key replaced - Kept under observation - Rectified
CL2109 | 2022-01-28 | Kattupakkam | G | Site visit | New Project | Suneel Sagar | 2022-01-28 | - | Site marking done for pit excavation- Attended
CL2110 | 2022-01-31 | Cantonment | C | Dispenser stamping | Certification | Prakash | 2022-01-31 | - | All 3 dispenser stamping completed A side testing: 117.26 lit B side testing : 111.81 lit "K " factor A side : 100300 B side : 103000 C side : 10170 D side :. 10150 E side: 100000 F side :. 100000 - Attended
CL2111 | 2022-01-31 | Bathlagundu | G | Genset, Yard light and canopy light cables connection | New Project | Kamaraj | 2022-01-31 | - | Genset, Yard light and canopy light cables connection completed - Attended
CL2112 | 2022-02-01 | Villapuram | D | Dispenser D side pulsar unit problem | Breakdown | Kathiresan | 2022-02-02 | - | Interchanged with C side - Now C side pulsar unit replaced on 02.02.2022 - Testing : 5 Ltrs - Rectified
CL2113 | 2022-02-01 | Cantonment | A | Yenen dispenser going offline for automation wiring correction | Preventive | Madhavan | 2022-02-01 | - | Wiring correction done - Dispenser back online - Resolved
CL2114 | 2022-02-02 | Bathlagundu | G | Site visit | New Project | Kamaraj | 2022-01-02 | - | Pavor block work in process - Hard stand making done - Attended
CL2115 | 2022-02-03 | Palladam | C | Dispenser calibration and stamping | Certification | Dharmesh & Gowtham | 2022-02-03 | - | Calibration and stamping done - A side op. reading - 774644.69 Cl.reading - 774755.55 B side Op.reading - 362917.63 Cl reading - 363022.14 C side Op. Reading - 1482750.32 - 1482875.42 D side Op. Reading - 1325807.63 Cl. Reading - 1325928.44 Total testing ltrs-461.39 ltr A side new k factor :101000 A - old K factor:101000 Flow rate : 9.99/10 ltr B- new K factor:101000 B - old K factor: 101000 Flow rate- 9.98/10 ltr C- new K factor:10050 C- old k factor: 10200 Flow rate:9.99/10 ltr D- new K factor:10050 D - old K factor: 10150 Flow rate: 9.99/10ltr. - Attended
CL2116 | 2022-02-03 | Renganathan Gas Bunk | T | Unloading pump LPG Leakage | Breakdown | Nepolean | 2022-02-03 | - | Oil seal 2 nos replaced newly - Unloading process can be done - Leakage arrested - Rectified
CL2117 | 2022-02-03 | Kangeyam | D | Cracked mother board replacement in yenen dispenser | Preventive | Thirumalaisamy & Dharmesh | 2022-02-03 | - | Cracked mother board replaced with new one - Working fine - Old motherboard closing reading: C-1854443.34 D-2087170.29 New motherboard opening reading: C-11.39 D-11.39 - Completed
CL2118 | 2022-02-04 | Velachery | D | Kalvacha dispenser a side keyboard not working properly | Breakdown | Suneel Sagar | 2022-02-04 | - | Keyboard dip switches replaced with new one - Working good - Rectified
CL2119 | 2022-02-04 | Uthamasolapuram | T | Tank area vapour line ball valve leakage | Breakdown | Prabu | 2022-02-04 | - | Ball valve leakage arrested by tightening the bolt nut and teflon applied - Nozzle serviced - Rectified
CL2120 | 2022-02-04 | Karur | C | Stamping and calibration work | Certification | Thirumalaisamy & Dharmesh | 2022-02-04 | - | Stamping and calibration completed - Calibration report: 'A' side 10 ltrs = 10.00 'B' side 10 ltrs = 10.05 'C' side 10 ltrs = 9.99 'D' side 10 ltrs = 10.00 "K" factor report: "A" side Old 'K' =102500 "A" side New 'K'=101500 "B " side old 'K'= 101500 "B" side New 'K' =101800 "C" side old 'K' =10250 "C" side New 'K'=10080 "D" side old 'K'= 10250 "D" side New 'K' =10080 Testing report: "A" side opening reading=8687840.24 "A" side closing reading=8688128.50 "A" side testing=288.26 "B" side opening reading=7281581.78 "B" side closing reading=7281861.75 "B" side testing=279.97 "C" side opening reading=623915.62 "C" side closing reading=624396.03 "C" side testing=480.41 "D" side opening reading=611851.73 "D" side closing reading=612345.57 "D" side testing=493.84 Total testing=1542.48litters. - completed
CL2121 | 2022-02-05 | Bhavani | R | Control panel not working | Breakdown | Prabu | 2022-02-05 | - | UPS battery dried out - EB supply directed - complaint registered with Consul - Rectified Temporarily
CL2122 | 2022-02-05 | Ariyamangalam | D | D side nozzle LPG leakage | Breakdown | Nepolean | 2022-02-05 | - | Nozzle teeth 4 nos replaced - Rectified
CL2123 | 2022-02-06 | Palladam 2 | T | Site visit | New Project | Suneel Sagar & Pandi Durai | 2022-02-06 | - | Tank flanges installed - Rochester gauge direction and HLA operation checked - Resolved
CL2124 | 2022-02-07 | Chinnasalem | T | Tank installation | New Project | Prabu | 2022-02-07 | - | Tank installation completed - Attended
CL2125 | 2022-02-07 | Perambalur | R | Unloading cant be done in Genset mode | Breakdown | Chandrasekar & Avinash | 2022-02-07 | - | Control panel output power increased - Unloading done - Rectified
CL2126 | 2022-02-07 | Aravakurichi | A | WIFI network issue | Breakdown | Kamaraj | 2022-02-07 | - | Network cable rewiring done - Issue resolved - Under observation - Dispenser working fine - Rectified
CL2127 | 2022-02-07 | Hosur | D | B side nozzle leakage | Breakdown | Suresh | 2022-02-07 | - | B side nozzle replaced - Working fine - Testing : 0.97 Ltrs - Rectified
CL2128 | 2022-02-07 | Palladam 2 | T | Motor bed construction | New Project | Gowtham | 2022-02-07 | - | Dispensing and decanting motor bed constructed - Dispensing motor placed on its foundation - Pipeline work in process - Attended
CL2129 | 2022-02-07 | Villapuram | D | C side dispenser Error 04 occurred | Breakdown | Kathiresan | 2022-02-12 | 4 days on C side | Pulsar box and dowel pin replaced with new one - Mother board refitted - Dispensing motor spider replaced and alignment checked - Kept under observation for 2 days - Testing : 5 Ltrs - Resolved
CL2130 | 2022-02-08 | Kumbakonam | R | Servo stabilizer not working properly - Outlet running in Genset mode | Breakdown | Nepolean | 2022-02-08 | 30 Mins | Servo stabilizer serviced by the instruction given by Service person - Kept under observation - Rectified
CL2131 | 2022-02-08 | Namakkal 2 | C | Calibration and stamping | Certification | Vignesh & Prabu | 2022-02-08 | - | Calibration and stamping completed - 'A' side 10 ltrs = 9.95 'B' side 10 ltrs = 9.97 "K" factor report: "A" side Old 'K' =10000 "A" side New 'K'=10100 "B " side old 'K'= 10000 "B" side New 'K' =10100 Testing report: "A" side opening reading=271559.32 "A" side closing reading=271659.32 "A side testing=100lit "B" side opening reading=253896.70 "B" side closing reading=254076.34 "B" side testing=179.64 Total testing=279.64litters - Attended
CL2132 | 2022-02-08 | Kattupakkam | G | Site visit | New Project | Suneel Sagar | 2022-02-08 | - | Tank pit work done - Attended
CL2133 | 2022-02-08 | Avadi | D | Dispenser D side nozzle teeth problem | Breakdown | Suneel Sagar | 2022-02-08 | - | Nozzle teeth 4 nos replaced - Rectified
CL2134 | 2022-02-08 | Palladam 2 | G | Dispenser pipeline trench and canopy foundation pit work | New Project | Gowtham | 2022-02-08 | - | Foundation pit dug - Attended
CL2135 | 2022-02-09 | Cantonment | D | Batchen dispenser power card problem | Breakdown | Prakash, Chandrasekar & Dharmesh | 2022-02-09 | - | IC and diode in the power card has been replaced in spare power card - Batchen dispenser working in run mode - Under observation - Testing litres A - 0.60 B - 17.16 C - 0.22 D - 0.06 E - 46.26 F - 0.12 Total testing - 64.42 litres - Rectified
CL2136 | 2022-02-09 | Vedachandur | G | Fire extinguisher operation training | Preventive | Kamaraj | 2022-02-09 | - | Fire extinguisher training completed - 9Kg fire extinguisher 1 no replaced done by chinmax team - Resolved
CL2137 | 2022-02-09 | Renganathan Gas Bunk | T | Unloading pump LPG Leakage | Breakdown | Nepolean | 2022-02-09 | - | Pump inner O ring replaced - Shaft bent - Informed to owner - Pump working fine - Rectified
CL2138 | 2022-02-10 | Krishnagiri | T | Differential Pressure Switch not working properly on run mode - Running in test mode | Breakdown | Nepolean | 2022-02-10 | 1 Hour | DPS bypassed - Connection reconnected - Working fine - Rectified
CL2139 | 2022-02-10 | Kattupakkam | G | Site marking | New Project | Suneel Sagar | 2022-02-10 | - | Unloading, hard stand, dispenser, earth pit and canopy marking has done - Completed
CL2140 | 2022-02-10 | T.V.Kovil | D | A and D side nozzle hammer teeth problem | Breakdown | Vignesh | 2022-02-10 | - | New nozzle teeth 4 nos each side replaced - Resolved
CL2141 | 2022-02-10 | Palladam 2 | T | Tank area pipeline welding work | New Project | Gowtham | 2022-02-10 | - | Pipeline welding work completed ank to dispenser pipeline provision will be done after island and trench marking - Attended
CL2142 | 2022-02-11 | Pudukkottai | T | Unloading vapour line ROV air leakage | Breakdown | Vignesh | 2022-02-11 | - | New ROV replaced - Working fine - Resolved
CL2143 | 2022-02-11 | Ariyamangalam | D | D side on/off switch problem | Breakdown | Nepolean | 2022-02-11 | - | New on/off switch replaced - Working fine - Rectified
CL2144 | 2022-02-12 | Thuraiyur | T | Unloading ROV with ballvalve LPG leakage | Breakdown | Nepolean & Pandi Durai | 2022-02-12 | - | ROV with ballvalve LPG leakage arrested by tightening the nut and teflon applied - Rectified
CL2145 | 2022-02-12 | Theni | D | Batchen dispenser bottom angle valve LPG leakage | Breakdown | Kamaraj | 2022-02-12 | - | Angle needle valve spindle seating position adjusted - Leakage arrested - Rectified
CL2146 | 2022-02-12 | Kodungaiyur | D | A side nozzle teeth damaged & PMR work | Breakdown | Suneel Sagar | 2022-02-12 | - | Nozzle teeth 4 nos replaced - PMR done - Unloading motor phase reverse problem on DG set solved - Rectified
CL2147 | 2022-02-14 | Chinnasalem | T | Tank hydro test | New Project | Prabu | 2022-02-14 | - | Tank hydro test completed at 29 kg/cm2 - Attended
CL2148 | 2022-02-14 | Uthamapalayam | T | Dispensing pneumatic hose air leakage | Breakdown | Kamaraj | 2022-02-14 | - | Pneumatic hose replaced with new one - Dispensing bypass valve cleaned to release suction problem - PMR done - Completed
CL2149 | 2022-02-15 | Namakkal 1 | T | Unloading vapour hose adapter leakage | Breakdown | Prabu | 2022-02-15 | - | Vapour hose adapter leakage arrested by appying teflon - Liquid line ball valve leakage arrested by tightening the nut - Tank area pneumatic air hose replaced to arrest leakage - Resolved
CL2150 | 2022-02-16 | Chinnasalem | T | CP installation | New Project | Prabu | 2022-02-16 | - | CP installed - Completed
CL2151 | 2022-02-16 | Uthamapalayam | T | Dispensing motor suction problem | Breakdown | Chandrasekar, Kamaraj & Nivas | 2022-02-16 | - | Tank alternate emergency line activated - Bypass valve cleaned - Kept under observation - Rectified
CL2152 | 2022-02-17 | Mulanur | G | Fire extinguisher service and Automation maintenance | Preventive | Thirumalaisamy | 2022-02-17 | - | Fire extinguisher service done by Prevention Pro - Operation training given to pump staff - PMR done - Automation maintenance done - Resolved
CL2153 | 2022-02-17 | Bathlagundu | G | Genset commissioning | New Project | Kamaraj | 2022-02-17 | - | Genset commissioned - Control panel charging, dispensing motor, decanting motor and dispenser testing done - Completed
CL2154 | 2022-02-17 | Kangeyam | G | Fire extinguisher refilling | Preventive | Gowtham | 2022-02-17 | - | Fire extinguisher refilling done by Prevention Pro - CO2 connecting hose replaced in both 75kg containers - Operation training given to pump staff - PMR done - Attended
CL2155 | 2022-02-17 | Tirunelveli | T | Unloading pump emergency ballvalve installation | Preventive | Kathiresan | 2022-02-17 | - | Emergency ballvalve installed in pump out - Pipeline hydro test done - C side nozzle teeth 4 nos replaced - Working fine - Rectified
CL2156 | 2022-02-19 | Thiruvaiyaru | R | Soft starter installation | New Project | Dharmesh | 2022-02-19 | - | Soft starter installation completed - EB mode Dispensing, Decanting motor & Dispenser Working checked - Attended
CL2157 | 2022-02-21 | Attur | D | Dispenser B side on/off switch damaged | Breakdown | Prabu | 2022-02-20 | - | On/ Off switch replaced in B side - Tank area ballvalve with ROV leakage arrested by tightening the bolt nut - C side nozzle damaged teeth replaced - Working fine - Resolved
CL2158 | 2022-02-21 | Ariyamangalam | D | B side nozzle LPG leakage | Breakdown | Nepolean | 2022-02-20 | - | Nozzle teeth 4 nos replaced with new - Rectified
CL2159 | 2022-02-22 | Velachery | C | PMR work | Preventive | Suneel Sagar | 2022-02-22 | - | PMR done - Completed
CL2160 | 2022-02-23 | Kodumudi | D | B side nozzle teeth problem | Breakdown | Thirumalaisamy | 2022-02-23 | - | Nozzle teeth 4 nos replaced - Automation maintenance done - Rectified
CL2161 | 2022-02-24 | Attur | D | Dispenser D side display not working | Breakdown | Prabu | 2022-02-24 | - | Display interchanged with C side - Display has to be changed another side - Temporarily Rectified
CL2162 | 2022-02-24 | Thiruvaiyaru | A | Final stage work and automation installation | New Project | Prakash, Madhavan, Chandrasekar & Dharmesh | 2022-02-25 | - | Automation installed and data available in KR admin app - Completed
CL2163 | 2022-02-24 | Palladam 2 | G | Pipeline welding | New Project | Gowtham | 2022-02-24 | - | Pipeline welding completed - Attended
CL2164 | 2022-02-25 | Palladam 2 | G | Pipeline hydro test | New Project | Gowtham | 2022-02-25 | - | Hydro test completed - Attended
CL2165 | 2022-02-26 | Thiruvaiyaru | T | Unloading pump leakage | Breakdown | Dharmesh | 2022-02-26 | - | Mechanical seal replaced - Leakage arrested - Batchen dispenser filter replaced - DOL starter relay replaced - Working fine - Rectified
CL2166 | 2022-02-27 | Rasipuram | R | Control panel voltage scanner burn out | Breakdown | Prabu | 2022-02-27 | - | Voltage scanner bypassed - Working fine - Rectified
CL2167 | 2022-02-28 | Udumalpet | T | Unloading pump emergency ballvalve installation | Preventive | Chandrasekar & Dharmesh | 2022-02-28 | - | Emergency ballvalve installed in pump out - Pipeline hydro test done - Working fine - Rectified
CL2168 | 2022-02-28 | Avinashi | T | Unloading pump emergency ballvalve installation | Preventive | Chandrasekar, Gowtham & Dharmesh | 2022-02-28 | - | Emergency ballvalve installed in pump out - Pipeline hydro test done - Working fine - Rectified
CL2169 | 2022-03-01 | Thiruvaiyaru | C | Stamping work | Certification | Nepolean | 2022-03-01 | - | Stamping work done - Attended
CL2170 | 2022-03-01 | Chromepet | G | Site visit | New Project | Suneel Sagar | 2022-03-01 | - | Site dimenstions noted - Completed
CL2171 | 2022-03-03 | Ramnad | T | Dispensing bypass valve adjustment | Preventive | Kathiresan | 2022-03-03 | - | Bypass valve adjusted - Motor bed alignment done - Unloading point and dispenser bottom ballvalve with ROV - LPG leakage arrested by tighting the stem nut - Unloading training done - Fire and safety training completed - Resolved
CL2172 | 2022-03-04 | Uthamapalayam | G | Unloading training | Preventive | Kamaraj | 2022-03-04 | - | Unloading training completed - Attended
CL2173 | 2022-03-04 | Chinnasalem | G | Site marking | New Project | Prabu | 2022-03-04 | - | Site marking done - Attended
CL2174 | 2022-03-06 | Chinnasalem | G | Site visit | New Project | Prabu | 2022-03-06 | - | Material unloading completed - Tank flanges removed and cleaning work in process - Attended
CL2175 | 2022-03-06 | Mettupalayam | R | Control panel dispensing solenoid coil not working | Breakdown | Gowtham | 2022-03-06 | - | Unloading solenoid coil interchanged with dispesing solenoid coil - Temporarily rectified
CL2176 | 2022-03-07 | Ariyamangalam | D | A nozzle LPG leakage | Breakdown | Nepolean | 2022-03-07 | - | Serviced nozzle replaced - Working fine - Testing : 1.17 Ltrs - Rectified
CL2177 | 2022-03-09 | Mulanur | G | Unloading and unloading training | Preventive | Thirumalaisamy | 2022-03-09 | - | Unloading and Unloading training completed - Attended
CL2178 | 2022-03-09 | Villapuram | D | A nozzle teeth damaged | Breakdown | Kathiresan | 2022-03-09 | - | Nozzle teeth 4 nos replaced - Oil dispenser air lock removed - Oil testing : 1.5 Ltrs - Working fine - Rectified
CL2179 | 2022-03-09 | Palayam | A | Outlet going offline due to yenen software automatically closed | Breakdown | Thirumalaisamy | 2022-03-10 | - | Earth regenerated - Outlet back online - PMR done - Automation maintenance completed - Resolved
CL2180 | 2022-03-10 | Attur | C | Stamping and calibration work | Certification | Vignesh & Prabu | 2022-03-10 | - | Calibration and stamping completed. Calibration report: 'A' side 10 ltrs = 9.95 'B' side 10 ltrs = 10.01 C side 10 ltrs= 10.05 D side 10 ltrs= 10.01 "K" factor report: "A" side Old 'K' =101000 "A" side New 'K'=101000 "B " side old 'K'= 103000 "B" side New 'K' =102000 C side Old K =10200 C side New K =9900 D side Old K =10200 D side New K =10000 Testing, A side =243.19 B side =739.90 C side=164.98 D side=200.00 Total testing=1248.07l - Completed
CL2181 | 2022-03-11 | T.V.Kovil | D | Dispenser C side on / off switch problem | Breakdown | Nivas | 2022-03-11 | - | On / off switch replaced with new - Working fine - Rectified
CL2182 | 2022-03-11 | Pudukkottai | D | Dispenser A side keypad not working | Breakdown | Pandi Durai | 2022-03-11 | - | New keypad replaced - Working fine - Rectified
CL2183 | 2022-03-11 | T.V.Kovil | D | Dispenser C nozzle teeth damaged | Breakdown | Nivas | 2022-03-11 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL2184 | 2022-03-11 | Salem | D | Stamping and calibration work | Certification | Prabu | 2022-03-11 | - | Calibration and stamping completed. Calibration report: 'A' side 10 ltrs = 9.99 'B' side 10 ltrs = 10.00 "K" factor report: "A" side Old 'K' =101000 "A" side New 'K'=101770 "B " side old 'K'= 103530 "B" side New 'K' =101770 Testing, A side =716.71 B side =183.48 Total testing=900.19litters - Completed
CL2185 | 2022-03-12 | Chinnasalem | G | Site visit | New Project | Prabu | 2022-03-12 | - | Welding work in process - Attended
CL2186 | 2022-03-13 | Namakkal 1 | R | Control panel noise | Breakdown | Prabu | 2022-03-13 | - | Air solenoid replaced - Noise arrested - Tank area air hose replaced - Rectified
CL2187 | 2022-03-13 | Rasipuram | D | Dispensing hose damaged | Breakdown | Prabu | 2022-03-13 | - | Nozzle serviced - Dispensing hose to be replaced newly - Attended
CL2188 | 2022-03-14 | Ariyamangalam | D | Dispenser A side preset keypad not working | Breakdown | Nepolean | 2022-03-14 | - | Preset keypad replaced - Working fine - Rectified
CL2189 | 2022-03-15 | Kumbakonam | C | Stamping work | Certification | Vignesh & Pandi Durai | 2022-03-15 | - | Calibration and stamping done - Calibration report: 'A' side 10 ltrs = 9.98 'B' side 10 ltrs = 9.97 "K" factor report: "A" side Old 'K' =10000 "A" side New 'K'=10100 "B " side old 'K'= 10000 "B" side New 'K' =10100 Total testing=499.64litres - Attended
CL2190 | 2022-03-16 | Theni | C | Rule 19 work | Certification | Prakash, Chandrasekar, Nivas & Pandidurai | 2022-03-19 | 2 Days | Vessel testing - Rule 19 completed - Control panel changed - Resolved
CL2191 | 2022-03-16 | Chinnasalem | D | Dispenser installation and pipeline hydrotest | New Project | Prabu | 2022-03-16 | - | Dispenser installed - Pipeline hydro test completed - Resolved
CL2192 | 2022-03-17 | Kodungaiyur | R | Control panel dispensing solenoid body damaged | Breakdown | Suneel Sagar | 2022-03-17 | - | Solenoid body replaced with new - Rectified
CL2193 | 2022-03-17 | Thuraiyur | D | B side metering unit LPG leakage | Breakdown | Nepolean | 2022-03-17 | - | Metering unit bearing and oil seal kit replaced by new - Leakage arrested - Working fine - Rectified
CL2194 | 2022-03-17 | Erode | R | Outlet running in offline mode due to online UPS not working | Breakdown | Thirumalaisamy | 2022-03-18 | - | Online UPS input supply wire terminal adjusted - UPS service done - Outlet back online - Compressor oil changed for both - PMR done - Rectified
CL2195 | 2022-03-18 | Avadi | D | B side display card segment failure | Breakdown | Suneel Sagar | 2022-03-18 | - | New display card replaced - Working fine - Resolved
CL2196 | 2022-03-18 | Manapparai | T | Tank 1 run mode not working due to low voltage | Breakdown | Vignesh | 2022-03-18 | - | Tank 1 and 2 terminal looping done - Working fine - Rectified
CL2197 | 2022-03-19 | Tirunelveli | D | Batchen dispenser not working | Breakdown | Kathiresan | 2022-03-20 | 10 Hours | Batchen dispenser power card PCB not working - New power board replaced - B side high flow low flow solenoid coil cleaned - Working fine Testing "A" side =10 ltrs "B" side =177.22 ltrs. Total =187.22 ltrs - Rectified
CL2198 | 2022-03-19 | Uthamapalayam | T | Unloading pump out emergency ballvalve installation | Preventive | Kamaraj | 2022-03-19 | - | Emergency ballvalve installation done - Pipeline hydro test done - Completed
CL2199 | 2022-03-19 | Theni | D | Batchen dispenser metering unit leakage | Breakdown | Kamaraj | 2022-03-19 | - | Metering unit stem leakage arrested by applying teflon at the O ring - Rectified
CL2200 | 2022-03-23 | Avinashi | T | Tank 1 STP equalizer line LPG leakage | Breakdown | Gowtham | 2022-03-23 | - | Leakage arrested by teflon bush and new ferrule fittings replaced - Found satisfactory - Rectified
CL2201 | 2022-03-23 | Salem | C | Rule 19 work | Certification | Chandrasekar | 2022-03-25 | 36 Hours | Rule 19 completed - Vessel hydrotest, NDT test and N2 test completed - Sales started - Resolved
CL2202 | 2022-03-23 | Cantonment | A | Yenen dispenser going offline for automation maintenance | Preventive | Madhavan | 2022-03-23 | - | Automation maintenance done - Dispenser back online - Completed
CL2203 | 2022-03-23 | Villapuram | R | EB line Phase B - fuse worn out | Breakdown | Kathiresan | 2022-03-23 | - | Fuse replaced - Working fine - Resolved
CL2204 | 2022-03-24 | Perundurai | G | Fire extinguisher refilling and operation training | Preventive | Thirumalaisamy | 2022-03-24 | - | Fire extinguisher 75Kg and 9 kg refilling done - Fire extinguisher operation training given - Resolved
CL2205 | 2022-03-24 | Thanjavur | R | Control panel tripping due to voltage problem | Breakdown | Nepolean | 2022-03-24 | - | Input voltage reduced from 400 to 380 - Tripping issue resolved - Completed
CL2206 | 2022-03-24 | Manapparai | C | Dispenser calibration and stamping | Certification | Dharmesh & Pandi Durai | 2022-03-24 | - | Calibration and stamping completed - Calibration report: 'A' side 10 ltrs = 9.99 'B' side 10 ltrs = 9.98 "K" factor report: "A" side Old 'K' =10280 "A" side New 'K'=10190 "B " side old 'K'= 10280 "B" side New 'K' =10280 Total testing=351.29litters. Automation "CPU" new one replaced - working fine - Completed
CL2207 | 2022-03-24 | Velachery | C | Preventive Maintenance | Certification | Suneel Sagar | 2022-03-24 | - | Preventive maintenance done - Completed
CL2208 | 2022-03-24 | Bhavani | G | Fire extinguisher refilling and operation training | Preventive | Thirumalaisamy | 2022-03-24 | - | Fire extinguisher 75Kg and 9 kg refilling done - Fire extinguisher operation training given - Resolved
CL2209 | 2022-03-25 | Vadivelan Nagar | C | Preventive Maintenance | Certification | Suneel Sagar | 2022-03-25 | - | Preventive maintenance Report done - Completed
CL2210 | 2022-03-26 | Rasipuram | R | Control panel Electric line one phase not coming properly | Breakdown | Prabu | 2022-03-25 | - | Fuses reassembled - EB line adjusted - Rectified
CL2211 | 2022-03-26 | T.V.Kovil | D | B side nozzle teeth damaged | Breakdown | Nepolean | 2022-03-26 | - | B nozzle teeth replaced - Working fine - Rectified
CL2212 | 2022-03-26 | Namakkal 1 | C | Preventive Maintenance | Certification | Prabu | 2022-03-26 | - | Preventive maintenance Report done - Completed
CL2213 | 2022-03-27 | Bhavani | D | A nozzle hose leakage | Breakdown | Prabu | 2022-03-27 | - | A side dispensing hose replaced - Testing : 1.68 Ltrs - Rectified
CL2214 | 2022-03-27 | Mulanur | C | Calibration work | Certification | Vignesh & Thirumalaisamy | 2022-03-27 | - | Calibration report: 'A' side 10 ltrs =10.06 'B' side 10 ltrs =10.05 "K" factor report: "A" side Old 'K' =10000 "A" side New 'K'=10000 "B" side old 'K'= 10000 "B" side New 'K' =10000 Total testing=251.07litres - Completed
CL2215 | 2022-03-28 | Perundurai | C | Calibration and stamping | Certification | Vignesh & Thirumalaisamy | 2022-03-28 | - | Calibration and stamping completed - Calibration report: 'A' side 10 ltrs = 9.93 'B' side 10 ltrs = 9.93 "K" factor report: "A" side Old 'K' =10300 "A" side New 'K'=10300 "B " side old 'K'= 10250 "B" side New 'K' =10250 Total testing=324.90litters Automation maintenance completed - Attended
CL2216 | 2022-03-28 | Puliyur | T | Tank installation | New Project | Chandrasekar | 2022-03-28 | - | Tank installation and foundation concrete work completed - Attended
CL2217 | 2022-03-28 | Avinashi | C | Calibration work | Certification | Gowtham & Vignesh | 2022-03-28 | - | Calibration done - Calibration report: 'A' side 10 ltrs = 9.99 'B' side 10 ltrs = 9.98 'C' side 10 ltrs = 10.05 'D' side 10 ltrs = 10.01 "K" factor report: "A" side Old 'K' =100660 "A" side New 'K'=103500 "B " side old 'K'= 100000 "B" side New 'K' =100000 'C' and 'D' side no changes in K = 10000 Total testing= 1451.02 litres - Completed
CL2218 | 2022-03-28 | Kumbakonam | R | Air compressir relay not working | Breakdown | Nepolean | 2022-03-28 | - | New relay released - Working fine - Resolved
CL2219 | 2022-03-29 | Kangeyam | C | Calibration work | Certification | Gowtham & Vignesh | 2022-03-29 | - | Calibration done - Calibration report: 'A' side 10 ltrs = 10.05 'B' side 10 ltrs = 10.05 'C' side 10 ltrs = 10.03 'D' side 10 ltrs = 10.04 "K" factor report: "C" side Old 'K' =10100 "C" side New 'K'=10200 "D " side old 'K'= 10080 "D" side New 'K' =10300 'A' and 'B' side no K factor (Kalvacha) Total testing= 676.86 litres - Completed
CL2220 | 2022-03-29 | Aravakurichi | C | Calibration work | Certification | Vignesh & Thirumalaisamy | 2022-03-29 | - | Calibration done - Calibration report: 'A' side 10 ltrs = 9.95 'B' side 10 ltrs = 9.96 "K" factor report: "A" side Old 'K' =10050 "A" side New 'K'=10100 "B " side old 'K'= 10050 "B" side New 'K' =10100 Total testing=324.90litres - Completed
CL2221 | 2022-03-30 | Namakkal 1 | D | B side dispensing hose damaged | Breakdown | Prabu | 2022-03-30 | - | 5m dispensing hose replaced - RS485 to USB converter board and CPU replaced - Outlet back online - Testing : 0.84 Ltrs - Rectified
CL2222 | 2022-03-30 | Melur | T | Dispensing motor not working properly | Breakdown | Kathiresan | 2022-03-30 | - | Control panel transformer power increased - Working fine - Kept under observation - Resolved
CL2223 | 2022-03-31 | T.V.Kovil | D | Batchen dispenser 5m hose damaged | Breakdown | Vignesh | 2022-03-31 | - | 5m dispensing hose replaced - Testing: 1.070 Ltrs - Rectified
CL2224 | 2022-04-01 | Dharapuram | R | Control panel is not booting up due to emergency switch stuck up | Breakdown | Gowtham | 2022-04-01 | - | Emergency switch stuck up released - Panel working properly - Resolved
CL2225 | 2022-04-02 | Uthamapalayam | T | Dispensing motor run mode not working | Breakdown | Kamaraj | 2022-04-02 | - | Tank 1 and 2 terminal looping done - Working fine - Rectified
CL2226 | 2022-04-02 | Chinnasalem | G | Electrical pipeline, wire and air line laying | New Project | Prabu | 2022-04-02 | - | Pipeline laying work completed - Rule 33 data collected - Attended
CL2227 | 2022-04-03 | Dindigul | D | Dispenser B side nozzle not working properly | Breakdown | Kamaraj | 2022-04-03 | - | B side nozzle replaced - Working fine - Testing : 0.98 Ltrs - Rectified
CL2228 | 2022-04-03 | Villapuram | C | Calibration work | Certification | Dharmesh & Kathiresan | 2022-04-04 | - | Calibration done - A" side 10 ltrs = 10.06 "B" side 10 ltrs = 10.08 "C" side 10 ltrs = 10.22 "D" side 10 ltrs = 10.04 " A" side 'K' = 10000 " B" side 'K' = 10000 " C" side old 'K' = 10350 " C " side new 'K' =10400 " D" side old ' K' = 10200 " D " side new 'K '= 10000 Total testing = 1510.37 ltrs - Completed
CL2229 | 2022-04-04 | Melur | C | Calibration work | Certification | Dharmesh & Kathiresan | 2022-04-04 | - | Calibration done - A' side 10 ltrs = 9.99 'B' side 10 ltrs = 10.02 "K" factor report: "A" side Old 'K' =10000 "A" side New 'K'=10100 "B " side old 'K'= 10000 "B" side New 'K' =10070 Total testing=758.51 ltrs - Completed
CL2230 | 2022-04-05 | Ariyamangalam | D | Dispenser D side nozzle teeth problem | Breakdown | Nepolean | 2022-04-05 | - | Nozzle teeth replaced - Working fine - Compressor oil changed - Resolved
CL2231 | 2022-04-05 | T.V.Kovil | A | Dispenser going offline due to automation maintenance | Preventive | Madhavan | 2022-04-05 | - | Automation maintenance done - Dispenser back online - Completed
CL2232 | 2022-04-05 | Chengalpattu | D | Dispensing solenoid coil problem | Breakdown | Suneel Sagar | 2022-04-05 | - | Dispensing solenoid body replaced - Dispenser nozzle retraction rope adjusted - Rectified
CL2233 | 2022-04-06 | Thuraiyur | G | Fire extinguisher refilling and operation training | Preventive | Vignesh | 2022-04-06 | - | Fire extinguisher refilling done by Prevention Pro - CO2 connecting hose replaced in both 75kg containers and a 9Kg container - Operation training given to pump staff - PMR done - Attended
CL2234 | 2022-04-07 | Kumbakonam | C | PMR work and compressor oil changing | Certification | Nivas | 2022-04-07 | - | PMR done - Compressor oil changed - Completed
CL2235 | 2022-04-07 | Attur | T | Tank area LPG leakage | Breakdown | Prabu | 2022-04-07 | - | LPG leakage arrested by changing Liquid ballvalve to ACME adapter 2" gasket - FRL leakage arrested - Resolved
CL2236 | 2022-04-07 | Thuraiyur | T | Unloading liquid ballvalve LPG leakage | Breakdown | Vignesh | 2022-04-07 | - | Liquid ballvalve LPG leakage arrested by tightening the nut - Rectified
CL2237 | 2022-04-08 | Namakkal 2 | D | Dispenser B side nozzle hose retraction rope broken - Ball valve leakage | Breakdown | Prabu | 2022-04-08 | - | Retraction rope replaced - Breakaway leakage arrested - Display cleaned and fixed - Ballvalve leakage arrested by tightening the nut and applied teflon - Resolved
CL2238 | 2022-04-08 | Udumalpet | C | PMR and unloading training | Certification | Gowtham | 2022-04-08 | - | PMR done - Unloading training completed - Attended
CL2239 | 2022-04-09 | Melur | R | Servo stablizer spark and vibrating | Breakdown | Kathiresan | 2022-04-09 | - | Carbon bush refit done - Spring tension adjusted - Working fine - Resolved
CL2240 | 2022-04-09 | Hosur | G | Fire extinguisher refilling | Preventive | Suresh | 2022-04-09 | - | Fire extinguisher refilling done - 75kg container hose replaced - Completed
CL2241 | 2022-04-09 | Aravakurichi | T | Dispensing motor spider broken | Breakdown | Thirumalaisamy | 2022-04-09 | - | Spider newly replaced - Tank area to EB room pneumatic hose changed - Dispensing motor W1 and W2 contactor interchanged - Under observation - Resolved
CL2242 | 2022-04-11 | Perundurai | D | Dispenser Error 05 occurred - Servo stabilizer voltage output contactor problem | Breakdown | Thirumalaisamy | 2022-04-11 | - | Communication cable reconnected - Voltage output contactor replaced - Working fine - Rectified
CL2243 | 2022-04-11 | Kumbakonam | T | Unloading pump pressure gauge not working properly | Preventive | Pandi Durai | 2022-04-11 | - | Unloading pump pressure gauge replaced with new one - Fire Extinguisher 75kg nozzle replaced - Rectified
CL2244 | 2022-04-12 | Virudhunagar | C | Stamping and calibration work | Certification | Vignesh & Kathiresan | 2022-04-12 | - | Stamping and calibration done - Calibration report: 'A' side 10 ltrs = 9.96 'B' side 10 ltrs = 9.97 "K" Factor Report: "A" side 'K' factor =10200 "B" side 'K' factor =10200 Total testing=300.19 ltrs B nozzle teeth 4 Nos replaced - PMR done - Completed
CL2245 | 2022-04-12 | Namakkal 1 | A | Automation going offline due to earthing issue | Breakdown | Madhavan & Prabu | 2022-04-14 | - | New earthing provided - RS485 to USB converter board replaced - Dispenser back online - Resolved
CL2246 | 2022-04-12 | Virudhunagar | A | Dispenser going offline dut to thunderstorm - CPU problem - RS485 to USB converter not working due to earthing defect | Breakdown | Kathiresan | 2022-05-09 | - | USB hub port changed - CPU serviced - Dispenser on/off switch changed - Dispenser back online - Rectified
CL2247 | 2022-04-13 | T.V.Kovil | C | PMR Work | Certification | Vignesh | 2022-04-13 | - | PMR done - Attended
CL2248 | 2022-04-14 | Bathlagundu | G | Commissioning and inauguration work | New Project | Prakash, Dharmesh & Nivas | 2022-04-18 | - | Commissioning and inauguration work completed - Outlet opened to public - Attended
CL2249 | 2022-04-15 | Hosur | C | Rule 19 work | Certification | Chandrasekar, Prabu & Avinash | 2022-04-17 | 2 Days | Rule 19 completed - Vessel hydrotest, NDT test and N2 test completed - Dispenser & DG painting work completed - Sales started - Resolved
CL2250 | 2022-04-15 | Avadi | G | Fire extinguisher renewal | Preventive | Suneel Sagar | 2022-04-15 | - | Fire extinguisher renewal completed - Attended
CL2251 | 2022-04-15 | Namakkal 1 | D | Dispenser motherboard defected | Breakdown | Thirumalaisamy & Nepolean | 2022-04-16 | 8 Hours | New motherboard replaced - Opening Reading(16.04.2022) A Nozzle-560.62 B Nozzle-7.95. Display and display card replaced - Outlet running in offline mode - Working fine - Rectified
CL2252 | 2022-04-16 | Bathlagundu | C | Calibration work | Certification | Kamaraj | 2022-04-16 | - | Dispenser calibration completed - Calibration report: 'A' side 10 ltrs = 9.96 'B' side 10 ltrs = 9.98 "K" Factor Report: "A" side 'K' factor =10000 "B" side 'K' factor =10000 Calibration report: 'A' side 10 ltrs = 9.96 'B' side 10 ltrs = 9.98 "K" Factor Report: "A" side 'K' factor =10000 "B" side 'K' factor =10000 Dispenser opening Reading "A"side = 292.140 "B"side = 274.110 Automation work completed - Attended
CL2253 | 2022-04-17 | Kattupakkam | T | Tank erection | New Project | Suneel sagar | 2022-04-17 | - | Tank erection completed - Attended
CL2254 | 2022-04-17 | Namakkal 1 | D | B side display preset board not working properly | Breakdown | Thirumalaisamy | 2022-04-17 | - | B side new display changed - Display working properly both side - Rectified
CL2255 | 2022-04-17 | Namakkal 1 | A | Automation going offline due to CPU not working | Breakdown | Thirumalaisamy | 2022-05-11 | - | Mother board box replaced - RS485 to USB converter replaced - Dispenser back online - Working fine - Rectified
CL2256 | 2022-04-18 | Bathlagundu | A | Automation installation | New Project | Madhavan | 2022-04-18 | - | Dispenser brought online and data available in KR admin app - Completed
CL2257 | 2022-04-18 | Hosur | T | Complete leakage checking and dispenser to breakaway LPG hose replacing | Preventive | Prabu | 2022-04-18 | - | Leakage testing completed - dispenser to breakaway LPG hose replaced - Testing : 0.94 Ltrs - Resolved
CL2258 | 2022-04-19 | Udumalpet | T | DOL starter control cable damaged | Breakdown | Gowtham | 2022-04-19 | - | Control cable replaced - Batchen dispenser display cable replaced newly as a preventive action - Resolved
CL2259 | 2022-04-20 | Vadivelan Nagar | T | Dispensing liquid line ball valve manual gland leakage | Breakdown | Suneel Sagar | 2022-04-20 | - | Gland leakage arrested by tightening the nut and teflon applied - Rectified
CL2260 | 2022-04-20 | Dindigul | D | Dispenser A side on/off switch damaged | Breakdown | Kamaraj | 2022-04-20 | - | On / off switch replaced with new - Working fine - Rectified
CL2261 | 2022-04-20 | Kattupakkam | T | Tank hydro test | New Project | Suneel Sagar | 2022-04-20 | - | Tank hydro test completed for 2 tanks and found satisfactory - Completed
CL2262 | 2022-04-21 | Thuraiyur | C | Stamping work | Certification | Nepolean & Avinash | 2022-04-21 | - | Stamping completed - PMR done - Attended
CL2263 | 2022-04-21 | Kattupakkam | T | CP installation | New Project | Suneel Sagar | 2022-04-21 | - | CP installed - Completed
CL2264 | 2022-04-22 | Bathlagundu | C | PESO inspection | Certification | Kamaraj | 2022-04-22 | - | PESO Inspection completed - TP Link installed - Signal problem resolved - Found satisfactory - Rectified
CL2265 | 2022-04-23 | T.V.Kovil | D | A side nozzle teeth damaged | Breakdown | Avinash | 2022-04-23 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL2266 | 2022-04-24 | Kodumudi | R | Dispensing motor MOL problem due to EB low voltage | Breakdown | Thirumalaisamy | 2022-04-24 | - | Dispensing motor contactor relay automatically changed to manual mode - Changed into auto mode - Checked input EB supply - Working fine - Rectified
CL2267 | 2022-04-25 | Paramathivelur | D | A & B side nozzle teeth damaged | Breakdown | Thirumalaisamy | 2022-04-25 | - | Nozzle teeth changed for both sides - Working fine - 5m hose to be changed in A side - Rectified
CL2268 | 2022-04-25 | Kattupakkam | G | Site visit | New Project | Prakash | 2022-04-25 | - | Site visit completed - Attended
CL2269 | 2022-04-26 | Bathlagundu | G | Decanting and safety training | Preventive | Kamaraj | 2022-04-26 | - | Unloading training completed and safety instructions given - Unloadind done properly - Attended
CL2270 | 2022-04-27 | Ellis Nagar | G | Tank area pit marking | New Project | Kathiresan | 2022-04-27 | - | Tank pit marking completed - Attended
CL2271 | 2022-04-28 | Cantonment | T | Tank 1 CP reference electrode failure | Breakdown | Chandrasekar | 2022-04-28 | - | CP Reference electrode replaced - Working fine - Resolved
CL2272 | 2022-04-28 | Namakkal 1 | R | Online UPS not working | Breakdown | Prabu | 2022-04-28 | - | Online UPS mother board and cooling fan changed - Stabilizer serviced - Completed
CL2273 | 2022-04-28 | Kodumudi | G | ALDS basic operation training | Preventive | Thirumalaisamy | 2022-04-28 | - | ALDS operation training completed - All equipments working fine - Attended
CL2274 | 2022-04-29 | Musiri | C | Stamping work | Certification | Vigneshwaran | 2022-04-29 | - | Stamping completed - Calibration report: 'A' side 10 ltrs = 9.94 'B' side 10 ltrs = 9.93 "K" Factor Report: Old; "A" side 'K' factor =10350 "B" side 'K' factor =10350 New; "A" side 'K' factor =10200 "B" side 'K' factor =10200 Total testing=886.77 ltrs - Resolved
CL2275 | 2022-04-29 | Chinnasalem | C | Rule 33 third party inspection | Certification | Prakash | 2022-04-29 | - | Third party inspection completed - Attended
CL2276 | 2022-04-29 | Namakkal 2 | T | ATG not working properly | Breakdown | Prabu | 2022-04-29 | - | Control room to ATG damaged wire replaced - ATG working fine - Resolved
CL2277 | 2022-04-29 | Ellis Nagar | G | Office room and EB room civil marking | New Project | Kathiresan | 2022-04-29 | - | Civil marking completed - Attended
CL2278 | 2022-04-30 | Pudukkottai | D | Dispenser B side not working | Breakdown | Nepolean & Pandi Durai | 2022-04-30 | - | B side on/off switch element NO problem - New element replaced - Working fine - Rectified
CL2279 | 2022-05-01 | Hosur | D | B side excess flow valve repair | Breakdown | Suresh | 2022-05-01 | - | Excess flow valve replaced - Working fine - Testing : 0.95 Ltrs - Rectified
CL2280 | 2022-05-02 | Sulur | R | Compressor running continuously because of the damage in the air hose | Breakdown | Gowtham | 2022-05-02 | - | Power room to dispenser air hose changed - Compressor works fine - Resolved
CL2281 | 2022-05-02 | Bathlagundu | D | DP valve teflon membrane punctured | Breakdown | Kamaraj | 2022-05-02 | - | New teflon membrane replaced - Working fine - Rectified
CL2282 | 2022-05-03 | Krishnagiri | D | Dispenser both side nozzle hose, keypad and nozzle problem - solenoid coil leakage and heating issue | Breakdown | Prabu | 2022-05-03 | - | Keypad, Nozzle hoses replaced - Nozzle serviced - Both unloading and dispensing Solenoid coils replaced - PMR completed - Total testing 1.76 litres - Rectified
CL2283 | 2022-05-03 | Udumalpet | R | Emergency switch element loose contact | Breakdown | Gowtham | 2022-05-03 | - | Emergency switch element reconnected - Panel working fine - Resolved
CL2284 | 2022-05-03 | Villapuram | D | Dispenser D nozzle slow delivery | Breakdown | Kathiresan | 2022-05-03 | - | 3/4" excess flow valve refitted - Slow delivery resolved - Working fine - Rectified
CL2285 | 2022-05-04 | Kodungaiyur | D | Dispenser not running in run mode - Yenen going offline | Breakdown | Dharmesh | 2022-05-10 | - | RS485 to USB converter board newly replaced - Outlet back online - Unloading ballvalve leakage arrested by tightening the nut and teflon applied - PMR done - Completed
CL2286 | 2022-05-04 | Sulur | C | Calibration work | Certification | Gowtham | 2022-05-04 | - | Calibration done - A side old K fac. - 10035 A side new K fac. - 10075 B side old K fac.- 10025 B side new K fac - 10075 A side - 9.96/10.00 B side - 9.99/ 10.00 Testing ltr A side - 1455.42 B side - 1525.88 Total - 2981.30 - Completed
CL2287 | 2022-05-05 | Avinashi | R | R phase surge arrester fuse damage | Breakdown | Gowtham | 2022-05-05 | - | R phase surge arrester fuse replaced - Working fine - Resolved
CL2288 | 2022-05-05 | Perambalur | G | Dispenser going offline - RS485 - USB converter short due to earthing problem | Breakdown | Avinash | 2022-05-05 | - | RS485 - USB converter board replaced with a new one - Earth regenerated - Rectified
CL2289 | 2022-05-05 | Theni | C | Calibration work | Certification | Kamaraj | 2022-05-05 | - | Calibration done - Testing litre. A side =1159.54 liter. B side = 513.66 liter. Total testing litre = 1673.20 litre.
CL2290 | 2022-05-05 | Kattupakkam | T | Tank area pipeline welding work & Hydro test | New Project | Dharmesh | 2022-05-05 | - | Pipeline welding work and hydro test completed - Hydro test done at 48kg /cm2 testing pressure - Found satisfactory - Completed
CL2291 | 2022-05-06 | Ariyamangalam | D | A nozzle LPG leakage | Breakdown | Nepolean | 2022-05-06 | - | Nozzle replaced with a serviced nozzle - Working good - Testing : 1.15 Ltrs - Resolved
CL2292 | 2022-05-07 | Kodumudi | R | Unloading solnoid coil problem & Unloading training | Breakdown | Thirumalaisamy | 2022-05-07 | - | Solenoid coil cleaned and refit done -Unloading training provided - Rectified
CL2293 | 2022-05-07 | T.V.Kovil | C | Calibration work | Certification | Nepolean | 2022-05-07 | - | Calibration done - A side testing : 88.79 B side testing: 88.57 C side testing: 89.97 D side testing : 88.19 Total : 355.52 litres New k factors: A side : 100360 B side : 100840 A side testing: 213.66 B side testing: 128.34 Total: 342.00 litres - Completed
CL2294 | 2022-05-07 | Ariyamangalam | C | Calibration work | Certification | Nepolean | 2022-05-07 | - | Calibration done - A side testing : 89.26 B side testing : 90.65 C side testing: 89.15 D side testing : 109.96 Total : 379.02 litre - Completed
CL2295 | 2022-05-07 | Kattupakkam | G | Cable conduit and cable laying | New Project | Dharmesh | 2022-05-07 | - | Cable conduit and laying work completed - Resolved
CL2296 | 2022-05-08 | Cantonment | C | Calibration work | Certification | Nepolean | 2022-05-08 | - | Calibration done - A side testing: 89.90 B side testing: 62.04 C side testing: 70.13 D side testing: 70.27 E side testing: 70.22 F side testing: 80.19 Total: 442.75 lit. K factor not changed - Completed
CL2297 | 2022-05-08 | Avadi | T | Dispensing motor lovejoy coupling damaged | Breakdown | Dharmesh | 2022-05-08 | - | Lovejoy coupling replaced with new - PMR done - Completed
CL2298 | 2022-05-09 | Cantonment | C | Calibration work | Certification | Nepolean | 2022-05-09 | - | Calibration done on E side - Testing : 190.38 Ltrs - Rectified
CL2299 | 2022-05-09 | Attur | T | Tank pressure not maintained | Breakdown | Prabu | 2022-05-09 | - | Bypass valve cleaned and O ring replaced - Kept under observation for a week - Resolved
CL2300 | 2022-05-09 | Palayam | A | Yenen software closed automatically | Breakdown | Thirumalaisamy | 2022-05-09 | - | Software opened - Separate earthing should be provided - Temporaily rectified
CL2301 | 2022-05-09 | Cantonment | D | EF dispenser "SE Switch on" error occurred | Breakdown | Nepolean | 2022-05-09 | - | Dispenser mother board replaced with new E side k factor: 09950 F side k factor : 10000 E side testing: 228.84 lit F side testing : 90.21 lit - Resolved
CL2302 | 2022-05-10 | Pudukkottai | R | Compressor continuous running problem | Breakdown | Nivas | 2022-05-10 | - | Power room to tank area dispensing pneumatic hose changed - DOL starter contactor one no changed - Rectified
CL2303 | 2022-05-10 | Ariyamangalam | D | A side both nozzles servicing | Preventive | Nepolean | 2022-05-10 | - | Both nozzles serviced and tested - Testing : 1.16 Ltrs - Completed
CL2304 | 2022-05-10 | Kodumudi | G | Fire and safety training program | Preventive | Thirumalaisamy | 2022-05-10 | - | Fire and safety training program given to pump staffs - Attended
CL2305 | 2022-05-11 | T.V.Kovil | C | Calibration work | Certification | Nepolean | 2022-05-11 | - | Calibration done A side: 80.17 B side : 80.15 C side: 95.11 D side: 81.00 Total : 336.43 litres - Completed
CL2306 | 2022-05-11 | Cantonment | C | Calibration work | Certification | Nepolean | 2022-05-11 | - | Calibration done A side : 109.70 B side : 81.60 E side: 125.05 F side: 125.17 Total: 441.52 litres - Completed
CL2307 | 2022-05-11 | Ariyamangalam | C | Calibration work | Certification | Nepolean | 2022-05-11 | - | Calibration done A side: 89.02 B side: 92.90 C side: 100.51 D side: 108.23 Total: 390.66 litres- Completed
CL2308 | 2022-05-12 | T.V.Kovil | D | C side dispenser on/off switch not working properly | Breakdown | Vignesh | 2022-05-12 | - | On/off switch replaced newly - Working fine - Rectified
CL2309 | 2022-05-12 | Ellis Nagar | T | Tank installation | New Project | Kathiresan | 2022-05-12 | - | Tank installation and concrete work completed - Attended
CL2310 | 2022-05-13 | Chinnasalem | T | Tank & Pipeline nitrogen test | New Project | Prabu | 2022-05-14 | - | Tank & Pipeline nitrogen test done - Holding pressure 10 bar - Completed
CL2311 | 2022-05-13 | T.V.Kovil | G | Air inflator on/off switch damaged | Breakdown | Vignesh | 2022-05-13 | - | Air inflator on/off switch replaced with new - Working fine - Resolved
CL2312 | 2022-05-14 | Tirunelveli | C | Calibration work | Certification | Kathiresan & Pandi Durai | 2022-05-14 | - | Calibration done A' side 10 ltrs = 9.99 'B' side 10 ltrs = 9.97 'C' side 10 ltrs = 9.99 'D' side 10 ltrs = 10.00 "K" factor report= "A" side Old 'K' =101700 "A" side New 'K'=102300 "B " side old 'K'= 101400 "B" side New 'K' =102000 "C" side 'K' =10341 "D" side 'K' =10330 Testing Report : "A" Testing= 272.05 "B" Testing= 266.52 "C" Testing= 347.12 "D" Testing= 380.72 - Completed
CL2313 | 2022-05-14 | Kattupakkam | D | Dispenser installation | New Project | Dharmesh | 2022-05-14 | - | Dispenser installation completed - Tank area to dispenser welding work completed - Attended
CL2314 | 2022-05-15 | Kattupakkam | T | Tank area to dispenser pipe line hydro test | New Project | Dharmesh | 2022-05-15 | - | Tank area to dispenser pipe line hydro test done - Testing pressure 48Kg/cm2 - Completed
CL2315 | 2022-05-15 | Villapuram | A | C and D side dispenser automation cable damaged and D side Error 04 occurred | Breakdown | Kathiresan | 2022-05-16 | 1.5 Days on D side | Automation cable replaced - D side pulsar box replaced - esting report 15/5/22= 0.41 ltrs 16/5/22= 1 ltrs Total= 1.41 ltrs - D" side Totalizer =282869.910 Working fine - Rectified
CL2316 | 2022-05-16 | Puliyur | T | CP installation | New Project | Thirumalaisamy | 2022-05-16 | - | CP installation done - Kept under observation - Completed
CL2317 | 2022-05-17 | Mettupalayam | R | Control panel not booting up & complete wiring short circuit | Breakdown | Gowtham & Prabu | 2022-05-18 | 10 Hours | Input cable and MNX 22 relay replaced - DG AVR contactor replaced - ATG high - high alarm reset - Dispenser display glass replaced - EB room to tank area pneumatic hose replaced - Stabilizer to be serviced - Control panel directed without stabilizer - Resolved
CL2318 | 2022-05-17 | T.V.Kovil | D | Dispenser C side nozzle teeth damaged | Breakdown | Vignesh | 2022-05-17 | - | Nozzle teeth 4 nos replaced at C side - Working fine - Resolved
CL2319 | 2022-05-17 | Ellis Nagar | T | Both tank hydro test | New Project | Kathiresan | 2022-05-17 | - | Tank hydro test completed for both tanks - Found satisfactory - Holding pressure 28.73 kg/ cm² - Completed
CL2320 | 2022-05-18 | Vedachandur | G | Leakage test and PMR | Preventive | Kamaraj | 2022-05-18 | - | Leakage test done - PMR done - Completed
CL2321 | 2022-05-18 | Kodungaiyur | A | Internet signal issue | Preventive | Dharmesh | 2022-05-18 | - | TP link installed - Automation training provided to pump staff - A side serviced nozzle replaced - B side nozzle teeth replaced - Working fine - Rectified
CL2322 | 2022-05-18 | Hosur | D | B side nozzle leakage | Breakdown | Suresh | 2022-05-18 | - | Nozzle replaced with a serviced nozzle - Working good - Testing : 0.98 Ltrs - Resolved
CL2323 | 2022-05-19 | Namakkal 3 | T | Tank installation and foundation concrete work | New Project | Chandrasekar & Prabu | 2022-05-19 | - | Tank installed and foundation concrete work completed - attended
CL2324 | 2022-05-19 | T.V.Kovil | G | N2 machine not working | Breakdown | Nepolean | 2022-05-19 | - | Valve & Solenoid coil serviced - N2 machine working fine - Rectified
CL2325 | 2022-05-19 | Cantonment | G | N2 machine keypad not working | Breakdown | Nepolean | 2022-05-19 | - | Keypad replaced - Valve & Solenoid coil serviced - N2 machine working fine - Rectified
CL2326 | 2022-05-19 | Thanjavur | G | N2 machine slow air dispensing | Breakdown | Pandi Durai | 2022-05-19 | - | Valve & Solenoid coil serviced - Temperature sensor cleaned - N2 machine working fine - Rectified
CL2327 | 2022-05-19 | Ellis Nagar | T | CP installation | New Project | Kathiresan | 2022-05-19 | - | CP installation done - found satisfactory - Tank 1's R1 and Tank 2's R1 looping terminal connection installed - Completed
CL2328 | 2022-05-20 | Devakottai | G | Site visit | New Project | Prakash | 2022-05-20 | - | Site visit completed - Attended
CL2329 | 2022-05-20 | Ellis Nagar | G | Site visit | New Project | Prakash | 2022-05-20 | - | Site visit completed - Attended
CL2330 | 2022-05-20 | Cantonment | D | C and D side nozzle replacement | Breakdown | Chandrasekar | 2022-05-20 | - | Both side nozzles replaced - C, side testing. 0.97 litre D, side testing. 0.89 litre Sales. C-Open reading.2382516.21 C-close reading. 3085017.81 C-side sales. 702501.60 D-open reading. 2368496.15 D-close reading. 3007289.92 D-side sales. 638793.77 - Completed
CL2331 | 2022-05-20 | Velachery | D | B side keypad not working properly | Breakdown | Suneel Sagar | 2022-05-20 | - | Keypad replaced - Nozzle NC element replaced - Kept under observation - Resolved
CL2332 | 2022-05-21 | Avinashi | R | Compressor continuous running problem | Breakdown | Gowtham | 2022-05-21 | - | Pneumatic hose replaced - Working fine - Rectified
CL2333 | 2022-05-21 | Cantonment | D | A side nozzle servicing and testing | Preventive | Nepolean | 2022-05-21 | - | C and D side nozzle teeth replaced - NRV O ring replaced - Working fine - Testing : 4.58 Ltrs - Resolved
CL2334 | 2022-05-21 | Chengalpattu | C | PMR Work | Certification | Suneel Sagar | 2022-05-21 | - | PMR completed - Attended
CL2335 | 2022-05-21 | Mettupalayam | D | Servo stabilizer problem and dispenser nozzle problem | Breakdown | Gowtham | 2022-05-21 | - | Stabilizer serviced by service person - Nozzle teeth 4 nos replaced - Rectified
CL2336 | 2022-05-22 | Ariyamangalam | D | Dispenser D side nozzle not working properly | Breakdown | Nivas | 2022-05-22 | - | Serviced nozzle replaced - Working fine - Testing : 0.76 Ltrs - Rectified
CL2337 | 2022-05-22 | Villapuram | R | EB room water motor panel short circuited and smoking | Breakdown | Kathiresan | 2022-05-22 | - | Fire extinguisher used - Smoking arrested - Training will be given to use CO2 extinguisher - Resolved
CL2338 | 2022-05-23 | Ellis Nagar | T | Decanting and dispensing motor bed marking | New Project | Kathiresan | 2022-05-23 | - | Decanting and dispensing motor bed marking done - Completed
CL2339 | 2022-05-23 | Uthamasolapuram | T | Dispensing motor spider broken | Breakdown | Prabu | 2022-05-23 | - | Dispensing motor spider changed - Working fine - Rectified
CL2340 | 2022-05-24 | Sulur | D | Dispenser B side, preset operation automatically comes to zero(reset) at end of the transaction while fueling | Breakdown | Gowtham | 2022-05-24 | - | Dispenser on/off switch assembly replaced - Working good - Resolved
CL2341 | 2022-05-24 | Chinnasalem | G | Fire and safety training program | Preventive | Prabu | 2022-05-24 | - | Fire and safety training program given to pump staffs - Attended
CL2342 | 2022-05-24 | Puliyur | T | Tank cleaning, Excess flow valve fixing, tank inside pipeline welding and hydro test | New Project | Thirumalaisamy | 2022-05-24 | - | Tank cleaning completed - Excess flow valve fixed - Tank inside dispensing liquid pipe line welding and hydro test done - Pressure held at 48kg/cm^2 - Both flanges fixed to tank - Completed
CL2343 | 2022-05-25 | T.V.Kovil | C | DIL visit and stamping | Certification | Nepolean | 2022-05-25 | - | Stamping and DIL visit completed - Attended
CL2344 | 2022-05-25 | Ellis Nagar | T | Tank 1 and tank 2 excess flow valve fitting and Dispensing liquid pipe line hydro test | New Project | Kathiresan | 2022-05-25 | - | Excess flow valve fitting done - Dispensing pipeline hydro test done - Dispenser and trench marking done - Completed
CL2345 | 2022-05-26 | Chengalpattu | c | DIL Stamping | Certification | Chandrasekar & Vignesh | 2022-05-26 | - | DIL stamping done - 'C' side 10 ltrs = 9.98 'D' side 10 ltrs = 9.97 "K" factor report "C" side Old 'K' =09950 "C" side New 'K'=10010 "D " side old 'K'= 09950 "D" side New 'K' =10040 Testing Report "C" Testing= 327.07 "D" Testing=322.03 Total testing =649.10 - FRL replaced - Compressor pressure switch adjusted - Completed
CL2346 | 2022-05-26 | Nasiyanur | T | Tank installation | New Project | Thirumalaisamy | 2022-05-26 | - | Tank installation done - Completed
CL2347 | 2022-05-26 | Sankari | T | ATG not working properly | Breakdown | Prabu | 2022-05-26 | - | ATG wires reconnected - Working fine - ATG went live - Rectified
CL2348 | 2022-05-26 | Bhavani | D | Dispenser A side keypad not working | Breakdown | Prabu | 2022-05-26 | - | A side keypad replaced - PMR done - Completed
CL2349 | 2022-05-27 | Dharapuram | D | B side 1/2 Mtr dispensing hose damaged | Breakdown | Gowtham | 2022-05-27 | - | 1/2" dispensing hose replaced - Decanting liquid line ROV air fitting T joint replaced - Testing : 2 Ltrs - Resolved
CL2350 | 2022-05-27 | Nasiyanur | T | Tank foundation work | New Project | Thirumalaisamy | 2022-05-27 | - | Tank foundation work done - Site boundary marking and dispenser island marking done - Completed
CL2351 | 2022-05-27 | Kodungaiyur | D | B side DP valve diaphragm damaged | Breakdown | Suneel Sagar | 2022-05-27 | - | DP valve diaphragm replaced - Working fine - Rectified
CL2352 | 2022-05-28 | Musiri | G | Fire and safety training program | Preventive | Avinash | 2022-05-28 | - | Fire and safety training program given to pump staffs - Attended
CL2353 | 2022-05-28 | Velachery | C | Calibration work | Certification | Chandrasekar | 2022-05-28 | - | Calibration done A, side 10 ltrs=10.09 B, side 10 ltrs=10.00 C, side 10 ltrs = 10.11 D, side 10 ltrs = 10.12 Testing Report A, Testing =227.59 B, Testing =591.62 C,Testing= 81.13 D, Testing=79.57 Total testing =979.91 - Completed
CL2354 | 2022-05-28 | Vadivelan Nagar | C | Calibration work | Certification | Chandrasekar | 2022-05-28 | - | Calibration report A, side 10 ltrs=10.07 B, side 10 ltrs=10.04 C, side 10 ltrs = 10.06 D, side 10 ltrs = 10.11 Testing Report A, Testing =119.80 B, Testing =121.78 C,Testing= 349.56 D, Testing=101.93 Total testing =693.07 A, side k-factor=10110 B, side k-factor =10160 C.side old k-factor =10060 C, side newk- factor =10160 D, side k-factor=10100 - Completed
CL2355 | 2022-05-28 | Ariyamangalam | D | D side nozzle testing and servicing | Preventive | Nepolean | 2022-05-28 | - | Hosur nozzles 2 mos serviced and tested - Testing : 1.54 Ltrs - Completed
CL2356 | 2022-05-28 | Palladam 2 | T | Tank and pipeline nitrogen testing | New Project | Gowtham | 2022-05-28 | - | ank and pipe line tested and purged by Nitrogen at 15 kg/sqr.cm - Tank holding nitrogen with 11 kg/sqr.cm - Found satisfactory - Painting completed - Rectified
CL2357 | 2022-05-28 | Ellis Nagar | T | Tank area pipeline work | New Project | Kathiresan | 2022-05-28 | - | Pipeline work completed - Rule 33 data collected - Fencing and decanting point marking done - Completed
CL2358 | 2022-05-29 | Bathlagundu | D | Yenen nozzle mount loosened | Breakdown | Kamaraj | 2022-05-29 | - | Nozzle mount reassembled - Working fine - Rectified
CL2359 | 2022-05-29 | Velachery | D | A side relays not working | Breakdown | Suneel Sagar | 2022-05-29 | - | Relay replaced by new one - Working good - Resolved
CL2360 | 2022-05-29 | Ariyamangalam | G | EB input phase problem | Breakdown | Nivas | 2022-05-29 | - | Input adjusted by EB service man - Rectified
CL2361 | 2022-05-31 | Ariyamangalam | D | B and C side nozzle teeth problem | Breakdown | Nivas | 2022-05-31 | - | Both nozzles hammer teeth replaced - Working fine - Replaced
CL2362 | 2022-05-31 | Ariyamangalam | R | 1 Kva online UPS not working | Breakdown | Nivas | 2022-05-31 | - | Standby offline UPS replaced - Rectified temporarily
CL2363 | 2022-05-31 | Perambalur | R | VFD CPF02 error occurred | Breakdown | Avinash | 2022-05-31 | - | Dispensing motor connection given through soft starter - Working fine - Resolved
CL2364 | 2022-06-01 | Krishnagiri | A | System heating issue | Breakdown | Prabu | 2022-06-01 | - | Spare CPU replaced - Working fine - Rectified
CL2365 | 2022-06-01 | Vellakovil | T | Tank area ROV LPG leakage | Breakdown | Thirumalaisamy | 2022-06-01 | - | Leakage arrested by applying teflon and tightening the nut - Dispenser retraction rope tightened - Completed
CL2366 | 2022-06-01 | Perambalur | R | VFD CPF02 error occurred due to control card and gate drive board damaged of dust | Breakdown | Dharmesh | 2022-06-01 | - | VFD control card and gate drive board replaced - Working fine - Resolved
CL2367 | 2022-06-02 | Saravanampatty | T | Rochester gauge stuck up | Breakdown | Gowtham | 2022-06-02 | - | Rochester gauge adjusted and dial cleaned - ROV link serviced - Working fine - PMR done - Rectified
CL2368 | 2022-06-02 | Vadivelan Nagar | D | A nozzle problem and compressor continuous running | Breakdown | Suneel Sagar | 2022-06-02 | - | Nozzle replaced with new one - Dispenser pneumatic hose replaced - Rectified
CL2369 | 2022-06-02 | Velachery | T | Tank 2 dispensing line pneumatic connector damaged | Breakdown | Suneel Sagar | 2022-06-02 | - | Dispensing line pneumatic connector replaced - Working fine - Resolved
CL2370 | 2022-06-02 | Ellis Nagar | T | Dispensing and decanting pipe line hydro test | New Project | Kathiresan | 2022-06-02 | - | All pipe line hydro test done - Testing pressure 48 Kg/cm^2 - Dispenser installed - Completed
CL2371 | 2022-06-04 | Palayam | R | Control panel not working | Breakdown | Thirumalaisamy | 2022-06-04 | - | Dispensing solenoid coil replaced - Pneumatic fittings changed - 1 Kva transformer 2 amps fuse changed - Working fine - Unloading training given - Rectified
CL2372 | 2022-06-04 | Vadivelan Nagar | R | Control panel not working | Breakdown | Suneel Sagar | 2022-06-04 | - | Master solenoid coil replaced - Control Panel working - PMR done - Resolved
CL2373 | 2022-06-04 | Velachery | R | Compressor motor belt damaged | Breakdown | Suneel Sagar | 2022-06-04 | - | Compressor motor belt replaced - PMR done - Rectified
CL2374 | 2022-06-06 | Attur | D | Dispenser B side display not working properly | Breakdown | Prabu | 2022-06-06 | - | Spare display replaced - Working fine - Rectified
CL2375 | 2022-06-06 | Thuraiyur | D | Batchen dispenser error 23 occurred | Breakdown | Vignesh | 2022-06-06 | - | Temperature wire reconnected - Error solved - Rectified
CL2376 | 2022-06-06 | Aravakurichi | G | Fire and safety training program | Preventive | Thirumalaisamy | 2022-06-06 | - | Fire and safety training program given to pump staffs - Fire extinguisher service done - Automation maintenance done - Attended
CL2377 | 2022-06-06 | Chengalpattu | D | Dispensing hose damaged | Breakdown | Suneel Sagar | 2022-06-06 | - | Spare hoses replaced - Working fine - Resolved
CL2378 | 2022-06-06 | T.V.Kovil | D | D side nozzle teeth damaged | Breakdown | Vignesh | 2022-06-06 | - | Hammer teeth 4 nos replaced - Rectified
CL2379 | 2022-06-07 | Rasipuram | A | Servo stablizer and RS485 to UXB converter short circuited due to thunderstorm - Dispenser went offline | Breakdown | Prabu | 2022-06-07 | - | Stabilizer fuse, MCB replaced - Wiring corrected - RS485 to USB converter board and cable replaced - Dispenser back online - Working fine - Resovled
CL2380 | 2022-06-07 | Namakkal 3 | T | Tank hydro test | New Project | Prabu | 2022-06-07 | - | Hydro test done at pressure 29kg/cm2- Completed
CL2381 | 2022-06-08 | Kangeyam | C | PMR Work | Certification | Gowtham | 2022-06-08 | - | PMR done - Completed
CL2382 | 2022-06-08 | Puliyur | G | Site visit | New Project | Thirumalaisamy | 2022-06-08 | - | Material unloading completed - Mechanical work in process - Attended
CL2383 | 2022-06-08 | Palayam | G | New earth provision for dispenser due to automatic closing of yenen program | Preventive | Thirumalaisamy | 2022-06-08 | - | Separate earth provided for Dispenser - Kept under observation for 2 days - Dispenser Earth - 2.9Ohms; Control panel earth - 1.80 ohms - Completed
CL2384 | 2022-06-08 | Ariyamangalam | R | 1 Kva online UPS not working | Breakdown | Nivas | 2022-06-08 | - | UPS settings tuned - Working fine - Rectified
CL2385 | 2022-06-08 | Villapuram | A | Dispenser going offline due to automation cable damage | Breakdown | Kathiresan | 2022-06-08 | - | Cable replaced with new - Resolved
CL2386 | 2022-06-09 | KR Gases | T | Ammonia plant tank testing and Rule 19 | Certification | Prabu | 2022-06-09 | - | Tank, SRV & Unloading hose testing done - Rule19 done - completed
CL2387 | 2022-06-10 | Devakottai | T | Tank installation | New Project | Chandrasekar & Nivas | 2022-06-10 | - | Tank installation done - Foundation bolt concrete completed - Resolved
CL2388 | 2022-06-11 | Ellis Nagar | G | Canopy measurement | New Project | Dharmesh | 2022-06-11 | - | Measurement taken for canopy - Attended
CL2389 | 2022-06-11 | Tiruchengode | T | Tank installation | New Project | Prabu | 2022-06-11 | - | Tank installation done - Foundation bolt concrete completed - Resolved
CL2390 | 2022-06-11 | Namakkal 3 | T | CP installation | New Project | Prabu | 2022-06-11 | - | CP installed - Completed
CL2391 | 2022-06-11 | Puliyur | T | Site visit | New Project | Thirumalaisamy | 2022-06-11 | - | Trench marking done - Pipeline welding in process - Attended
CL2392 | 2022-06-13 | Mettupalayam | A | Automation system service | Preventive | Gowtham | 2022-06-13 | - | New CPU replaced as old CPU fan was not working - PMR done - Kept under observation - Attended
CL2393 | 2022-06-13 | Kattupakkam | T | N2 test for 2 tanks | New Project | Suneel Sagar | 2022-06-13 | - | N2 test completed for both tanks - Filled & tested at 15 kg pressure and hold at 10 kg pressure - Completed
CL2394 | 2022-06-14 | Attur | D | Batchen dispenser B side slow delivery | Breakdown | Prabu | 2022-06-14 | - | High flow low flow solenoid coil cleaned - Working fine - Testing: 0.91 Ltrs - Rectified
CL2395 | 2022-06-16 | Kattupakkam | A | Automation work | New Project | Chandrasekar & Dharmesh | 2022-06-17 | - | Control panel testing done - Dispensing & decanting motor work done - Automation work partially done - Completed
CL2396 | 2022-06-16 | Rasipuram | D | B side nozzle not working properly | Breakdown | Prabu | 2022-06-16 | - | Spare nozzle replaced - Testing : 0.91 Ltrs - Rectified
CL2397 | 2022-06-16 | Avadi | C | Calibration and stamping | Certification | Chandrasekar & Dharmesh | 2022-06-16 | - | Calibration and stamping done - Calibration report A side 10 ltrs=10.02 B side 10 ltrs=10.03 C side 10 ltrs = 9.99 D side 10 ltrs = 10.00 Testing Report A Testing = 180.61 B Testing = 115.11 C Testing= 173.00 D Testing= 110.83 Total testing = 579.55 All side k factor - 10000 no change - Completed
CL2398 | 2022-06-17 | Vellakovil | T | Dispensing motor fan broken | Breakdown | Thirumalaisamy | 2022-06-17 | - | Fan needs to be replaced - Attended
CL2399 | 2022-06-17 | KR Gases | C | Rule 19 Tank hydro test | Preventive | Prakash & Prabu | 2022-06-19 | - | Tank Rule 19 completed - Resolved
CL2400 | 2022-06-20 | Tiruchengode | T | Tank hydro test | New Project | Prabu | 2022-06-20 | - | Hydro test completed at 29 kg/cm2 - Completed
CL2401 | 2022-06-20 | Villapuram | G | Fire extinguisher and training for pump staff | Preventive | Kathiresan | 2022-06-20 | - | Renewal and training completed - Attended
CL2402 | 2022-06-20 | Mettupalayam | R | Stabilizer R phase coil burnt | Breakdown | Gowtham | 2022-06-21 | - | Stabilizer bypass done - New stabilizer replaced on 24-06-2022 - Voltage scanner serviced - Working good - Resovled
CL2403 | 2022-06-21 | Paramathivelur | C | Calibration and stamping | Certification | Vigneshwaran & Thirumalaisamy | 2022-06-21 | - | Calibration and stamping done - Calibration report: 'A' side 10 ltrs = 10.00 'B' side 10 ltrs = 9.99 "K" factor report: "A" side Old 'K' =10000 "A" side New 'K'=10000 "B " side old 'K'= 10000 "B" side New 'K' =10000 Testing: A Nozzle-185.67litters B Nozzle-110.10litters Total Testing-295.77litres - Completed
CL2404 | 2022-06-21 | Ellis Nagar | T | Both tank Nitrogen test | New Project | Chandrasekar | 2022-06-21 | - | Nitrogen testing completed - Testing pressure 15 kg/cm2 - Completed
CL2405 | 2022-06-21 | Chinnasalem | G | Generator, compressor, UPS, stabilizer and control panel commissioning | New Project | Prabu | 2022-06-21 | - | Generator, compressor, UPS, stabilizer and control panel commissioning done - Completed
CL2406 | 2022-06-21 | Ariyamangalam | D | D side nozzle LPG hose leakage | Breakdown | Nepolean | 2022-06-21 | - | New 5m LPG hose replaced - Nozzle serviced and tested - Testing : 2.93 Ltrs - Rectified
CL2407 | 2022-06-21 | Vadivelan Nagar | G | Generator battery expired | Breakdown | Suneel Sagar | 2022-06-21 | - | DG battery replaced with new one - Resolved
CL2408 | 2022-06-21 | Avadi | G | Phase reverse complaint | Breakdown | Suneel Sagar | 2022-06-21 | - | Phase sequence chaged - ALDS operating in EB power - Rectified
CL2409 | 2022-06-21 | Palayam | C | Calibration and stamping | Certification | Vigneshwaran & Thirumalaisamy | 2022-06-21 | - | Calibration and stamping done - Calibration report: 'A' side 10 ltrs = 10.03 'B' side 10 ltrs = 10.04 "K" factor report: "A" side Old 'K' =10000 "A" side New 'K'=10000 "B " side old 'K'= 10000 "B" side New 'K' =10000 Testing: A Nozzle-110.13litters B Nozzle-120.28litters Total Testing-230.41litres - Completed
CL2410 | 2022-06-21 | Karur | C | Recalibration | Certification | Vigneshwaran & Thirumalaisamy | 2022-06-21 | - | Calibration and stamping done - Calibration report: 'A' side 10 ltrs = 9.98 'B' side 10 ltrs = 10.02 'C' side 10 ltrs = 10.00 'D' side 10ltrs = 9.99 "K" factor report: "A" side Old 'K' =101500 "A" side New 'K'=101500 "B " side old 'K'= 101800 "B" side New 'K' =101800 "C" side old 'K' =10080 "C" side New 'K'=10080 "D" side old 'K' =10080 "D"side New 'K'=10080 Testing: A Nozzle-130.30litters B Nozzle-113.09litters C Nozzle- 161.28litters D Nozzle- 241.11 litters Total Testing-645.78litres - Completed
CL2411 | 2022-06-22 | Pudukkottai | T | Dispensing motor noise due spider broken | Breakdown | Nepolean, Dharmesh & Pandi Durai | 2022-06-22 | - | Dispensing motor spider changed - Working fine - Dispensing solenoid coil in control panel replaced with new - Unloading ACME adapter replaced - Working fine - Rectified
CL2412 | 2022-06-22 | Palladam | G | Fire extinguisher servicing, refilling and operation training | Preventive | Gowtham | 2022-06-22 | - | Fire extinguisher servicing, refilling and operation training conducted - Completed
CL2413 | 2022-06-22 | Avinashi | G | Fire extinguisher servicing, refilling and operation training | Preventive | Gowtham | 2022-06-22 | - | Fire extinguisher servicing, refilling and operation training conducted - Completed
CL2414 | 2022-06-22 | Villapuram | D | A nozzle leakage | Breakdown | Kathiresan | 2022-06-22 | - | Nozzle teeth 4 nos changed - Working fine - Rectified
CL2415 | 2022-06-22 | Tiruchengode | T | CP installation | New Project | Prabu | 2022-06-22 | - | Cathotic protection installed - Completed
CL2416 | 2022-06-22 | Sankari | D | B side nozzle lock damaged | Breakdown | Prabu | 2022-06-22 | - | Nozzle lock 1 set replaced - Working fine - Resolved
CL2417 | 2022-06-23 | Chinnasalem | G | All equipment commissioning | New Project | Chandrasekar, Nivas, Prabu & Avinash | 2022-06-23 | - | ATG configured - Dispenser connected online - All equipments commissioned - Attended
CL2418 | 2022-06-23 | Pudukkottai | R | Compressor continuous running due to dispensing air hose line damaged | Breakdown | Nepolean | 2022-06-24 | - | Dispensing air hose line replaced with new one - Outlet working normally - Rectified
CL2419 | 2022-06-24 | Rasipuram | D | A side dispensing hose damaged | Breakdown | Prabu | 2022-06-24 | - | New 5m LPG hose replaced - Nozzle serviced - Air compressor oil changed - UPS battery water top up done - PMR done - Testing : 0.77 Ltrs - Rectified
CL2420 | 2022-06-24 | Ariyamangalam | G | Mass flow meter testing | Preventive | Nepolean | 2022-06-24 | - | Mass flow meter testing done on D side - Testing 1 : 422.54 Ltrs Testing 2 : 361.27 Ltrs - Completed
CL2421 | 2022-06-24 | Puliyur | G | Earth pipe installation | New Project | Thirumalaisamy | 2022-06-24 | - | Earth pipe installed - Rule 33 data collected - Cable measurement taken - Completed
CL2422 | 2022-06-25 | Udumalpet | D | Point jumping | Breakdown | Gowtham | 2022-06-25 | - | Both side high flow low flow coil and filter cleaned - A side on/off switch replaced - 5m hose replaced - Testing : A : 25.08 Ltrs; B : 47.51 Ltrs - Resolved
CL2423 | 2022-06-25 | Attur | G | Fire extinguisher servicing, refilling and operation training | Preventive | Prabu | 2022-06-25 | - | Fire extinguisher servicing, refilling and operation training conducted - Completed
CL2424 | 2022-06-25 | Ariyamangalam | D | B side nozzle servicing and testing | Preventive | Nepolean | 2022-06-25 | - | Nozzle serviced and tested - One serviced nozzle replaced - Working fine - Testing : 3.34 Ltrs - Rectified
CL2425 | 2022-06-25 | Puliyur | G | Pipe line welding and hydro test | New Project | Thirumalaisamy | 2022-06-25 | - | Pipe line welding and hydro test completed - Pressure held at 48kg/cm^2 - Completed
CL2426 | 2022-06-26 | Ariyamangalam | D | B nozzle leakage | Breakdown | Nivas | 2022-06-26 | - | Serviced nozzle replaced - Working fine - Testing : 1.12 Ltrs - Resolved
CL2427 | 2022-06-26 | Puliyur | C | Rule 33 third party inspection | New Project | Thirumalaisamy | 2022-06-26 | - | Rule 33 third party inspection done - Attended
CL2428 | 2022-06-27 | Kattupakkam | C | Stamping, calibration and all equipment commissioning | New Project | Dharmesh & Avinash | 2022-06-29 | - | All equipment commissioned - Stamping and calibration done - Calibrated quantity 'A' side 10 ltrs = 10.14 'B' side 10 ltrs = 10.15 'C' side 10 ltrs = 10.16 'D' side 10 ltrs = 10.16 "K" factor A' side K = 9842 'B' side K = 9842 'C' side K = 9820 'D' side K = 9820 - Rectified
CL2429 | 2022-06-27 | Namakkal 3 | G | Dispensing liquid line welding and hydro test | New Project | Thirumalaisamy | 2022-06-27 | - | Dispensing liquid line welding and hydro test done - Excess flow valves and flanges fitting done - Testing pressure : 48kg/cm^2 - Completed
CL2430 | 2022-06-27 | Tirunelveli | A | Automation installation | New Project | Chandrasekar, Kathiresan & Nivas | 2022-06-29 | - | Automation installed and outlet brought online - Completed
CL2431 | 2022-06-27 | Chinnasalem | C | All equipement commissioning & Stamping | New Project | Prakash | 2022-06-29 | - | Stamping completed - Opening reading A side 388.30lit B side 329.94lit K factors A side 10000 B side 10000 A side 9.97lit B side 9.95lit - Attended
CL2432 | 2022-06-27 | Kattupakkam | C | PESO Inspection | New Project | Suneel Sagar | 2022-06-27 | - | PESO inspection completed - Attended
CL2433 | 2022-06-27 | Eral | T | Tank installation | New Project | Kathiresan | 2022-06-27 | - | Tank installed - Completed
CL2434 | 2022-06-28 | Eral | T | Tank foundation concrete work | New Project | Kathiresan | 2022-06-28 | - | Tank foundation concrete work done - Completed
CL2435 | 2022-06-28 | Tirunelveli | A | Automation installation | New Project | Madhavan | 2022-06-28 | - | Automation installed and data available in KR admin app - Completed
CL2436 | 2022-06-28 | Namakkal 2 | R | Compressor running continuously because of the damage in the air hose | Breakdown | Prabu | 2022-06-28 | - | EB room to tank area air hose replaced - N2 machine air hose nipple changed - Resolved
CL2437 | 2022-06-29 | Theni | T | Dispensing motor spider broken | Breakdown | Kamaraj | 2022-07-01 | - | Lovejoy coupling spider replaced with new - PMR done - Completed
CL2438 | 2022-06-30 | Palayam | G | Fire extinguisher servicing, refilling and operation training | Preventive | Thirumalaisamy | 2022-06-30 | - | Fire extinguisher servicing, refilling and operation training conducted - PMR done - Completed
CL2439 | 2022-06-30 | Theni | A | Automation installation | New Project | Madhavan | 2022-06-30 | - | Automation installed and data available in KR admin app - Completed
CL2440 | 2022-06-30 | Kattupakkam | A | Automation installation | New Project | Madhavan | 2022-06-30 | - | Automation installed and data available in KR admin app - Completed
CL2441 | 2022-06-30 | Ariyamangalam | D | D side nozzle service and testing | Preventive | Nepolean | 2022-06-30 | - | D side nozzle serviced and tested - Testing : 2.25 Ltrs - Attended
CL2442 | 2022-07-01 | Chinnasalem | A | Automation installation | New Project | Madhavan | 2022-07-01 | - | Automation installed and data available in KR admin app - Completed
CL2443 | 2022-07-01 | Tiruchengode | T | Tank cleaning, Excess flow valve and flanges fixing | New Project | Thirumalaisamy | 2022-07-01 | - | Tank cleaned - EFV working fine - Completed
CL2444 | 2022-07-01 | Uthamapalayam | R | Compressor running continuously because of the damage in the air hose | Breakdown | Kamaraj | 2022-06-28 | - | Control panel to tank area air hose replaced - Resolved
CL2445 | 2022-07-01 | Kodungaiyur | T | Emergency line gasket leakage | Breakdown | Suneel Sagar | 2022-07-01 | - | 3/4" stud and gasket replaced - Leakage arrested - Rectified
CL2446 | 2022-07-02 | Kattupakkam | D | Differential pressure valve diaphragm punctured | Breakdown | Suneel Sagar | 2022-07-02 | - | Differential pressure valve diaphragm replaced in C side - Working fine - Resolved
CL2447 | 2022-07-03 | Ammapettai | T | Tank installation | New Project | Prabu | 2022-07-03 | - | Tank installed - Completed
CL2448 | 2022-07-03 | Puliyur | G | GI flat welding and cable laying | New Project | Thirumalaisamy | 2022-07-03 | - | GI flat welding done - Tank area to EB room cable laying done - Rectified
CL2449 | 2022-07-04 | Neelambur | C | Preventive Maintenance | Preventive | Gowtham | 2022-07-04 | - | PMR done - Found satisfactory - Attended
CL2450 | 2022-07-04 | Kattupakkam | D | D side keypad not working | Breakdown | Suneel Sagar | 2022-07-08 | - | D side display card replaced - keypad working fine - Rectified
CL2451 | 2022-07-05 | Palladam 2 | G | Commissioning, Automation, Configuration and inauguration work | New Project | Prakash, Dharmesh, Vignesh & Pandi Durai | 2022-07-08 | - | Tank purging, Unloading pump and motor, Dispensing pump and motor installed - ATG configured - Calibration done - Commissioning done - Completed
CL2452 | 2022-07-08 | Palladam 2 | C | Stamping work | Certification | Nepolean & Gowtham | 2022-07-08 | - | Calibration done - A side K. Fact-103500 B side K. Fact-100000 D side K. Fact-10000 C side old K fact- 10000 C side new K fact- 10100 Nozzle wise rate of flow for 10 lts. A side- 10.01 lts./10.00 B side - 9.97 lts./10.00 C side - 9.99 lts. / 10.00 D side - 10.05 lts / 10.00 Nozzle wise total testing lts. A side- 139.97 lts. B side - 151.41 lts. C side - 437.21 lts. D side - 150.84 lts - Completed
CL2453 | 2022-07-08 | Theni | A | Batchen converter board cable damaged | Breakdown | Kamaraj | 2022-07-08 | - | Cable recorrected - Working fine - Under observation - Resolved
CL2454 | 2022-07-09 | Palayam | R | Stablizer contactor problem | Breakdown | Thirumalaisamy | 2022-07-13 | - | Working in bypass mode - Contactor replaced by Mothish service person - Working fine - Resolved
CL2455 | 2022-07-09 | Palladam 2 | A | Automation installation | New Project | Madhavan | 2022-07-09 | - | Automation installed and data available in KR admin app - Completed
CL2456 | 2022-07-09 | Renganathan Gas Bunk | T | Unloading problem | Breakdown | Chandrasekar | 2022-07-09 | - | Tank 2 HLA level adjusted - Unloading done - Resolved
CL2457 | 2022-07-09 | Tiruchengode | G | Liquid and vapour pipeline welding and Hydro test | New Project | Prabu | 2022-07-09 | - | Liquid and vapour pipeline welding and Hydro test done - Completed
CL2458 | 2022-07-10 | Chinnasalem | T | Unloading process and training | New Project | Prabu | 2022-07-10 | - | Unloading and Unloading training completed - Tank area leakage checked - Attended
CL2459 | 2022-07-10 | Ayothiyapattinam | R | Control panel unloading solenoid coil leakage | Breakdown | Prabu | 2022-07-10 | - | Solenoid coil replaced - Working fine - Rectified
CL2460 | 2022-07-14 | Udumalpet | T | Tank 1 STP motor not working due to impeller damage | Breakdown | Nepolean & Gowtham | 16-07-2022 | - | STB motor direct line is running 44sec only Amps : R - 5.74, Y - 6.19, B - 5.40
CL2461 | 2022-07-14 | Ellis Nagar | G | Automation and Control panel testing | New Project | Dharmesh & Pandi Durai | 2022-07-18 | - | Automation installed, Control panel testing done working fine - Completed
CL2462 | 2022-07-14 | Namakkal 3 | G | Site visit | New Project | Prakash & Vignesh | 2022-07-14 | - | Liquid and vapour pipeline welding and Hydro test done - Rule 33 data collected - Completed
CL2463 | 2022-07-14 | Tiruchengode | G | Site visit | New Project | Prakash & Vignesh | 2022-07-15 | - | Rule 33 data collected - Site visit done - Attended
CL2464 | 2022-07-15 | T.V.Kovil | A | Automation maintenance | Preventive | Madhavan | 2022-07-15 | - | Maintenance done - Outlet back online - Completed
CL2465 | 2022-07-15 | Palayam | R | Control panel not working | Breakdown | Thirumalaisamy | 2022-07-16 | 1.30 Hours | Problamatic master solenoid coil replaced with unloading solenoid - New solenoid coil replaced for unloading - PMR Completed- Resolved
CL2466 | 2022-07-15 | Devakottai | G | Site visit | New Project | Prakash & Vignesh | 2022-07-15 | - | Site visit completed - Attended
CL2467 | 2022-07-15 | Ellis Nagar | G | Site visit | New Project | Prakash & Vignesh | 2022-07-15 | - | Site visit completed - Attended
CL2468 | 2022-07-16 | Tiruchengode | C | Third party inspection ( Rule 33 ) | Certification | Prakash & Vignesh | 2022-07-16 | - | Third party inspection ( Rule 33 ) done - Completed
CL2469 | 2022-07-16 | Namakkal 3 | C | Third party inspection ( Rule 33 ) | Certification | Prakash & Vignesh | 2022-07-16 | - | Third party inspection ( Rule 33 ) done - Completed
CL2470 | 2022-07-16 | Dharapuram | D | B side dispensing hose breakaway to change - Bypass valve cleaning - Emergency switch fitting | Breakdown | Gowtham & Nepolean | 2022-07-17 | - | Office room emergency switch new 1no changed, Dispenser EFV and breakaway changed, Dispensing and decanting motor bypass valve cleaned & leakage arrested, PMR completed, A side testing ltr 17.74 - Rectified
CL2471 | 2022-07-16 | Villapuram | C | Stamping and calibration work | Certification | Kathiresan | 2022-07-16 | - | Stamping and calibration done - Calibration report: "A" side 10 ltrs = 10.00 "B" side 10 ltrs = 10.00 "C" side 10 ltrs = 10.03 "D" side 10 ltrs = 10.00 "K" factor report; ' A ' side old K = 10000 ' A ' side new K = 10100 ' B ' side old K. = 10000 ' B ' side new K = 10100 ' C ' side old K = 10200 ' C ' side new K = 10400 ' D ' side old K = 10000 ' D ' side new K = 10080 - Completed
CL2472 | 2022-07-16 | Devakottai | T | Tank hydro test | New Project | Dharmesh | 16-07-2022 | - | Hydro test completed at 27 kg/cm2 - Completed
CL2473 | 2022-07-16 | Paramathivelur | G | EB shutdown & DG engine oil hose damaged | Breakdown | Thirumalaisamy | 16-07-2022 | 4 Hours | EB problem solved - DG oil hose replaced by service person - Rectified
CL2474 | 2022-07-17 | Vellakoil | T | Decanting motor leakage | Breakdown | Gowtham, Nepolean & Thirumalaisamy | 2022-07-18 | - | Decanting motor LPG leakage arrested by change the O - ring in both side and 1no bearing changed - Rectified
CL2475 | 2022-07-17 | Eral | T | Tank hydro test | New Project | Kathiresan | 2022-07-17 | - | Hydro test completed at 28 kg/cm2 - Completed
CL2476 | 2022-07-17 | T.V.Kovil | D | Nozzle leakage | Breakdown | Vigneshvaran | 2022-07-17 | - | A side nozzle teeth 4 Nos replaced - Leakage arrested - Rectified
CL2477 | 2022-07-18 | Kattupakkam | R | VFD parameter adjusting and ATG configuration | Breakdown | Suneel Sagar | 2022-07-18 | - | VFD keypad parameter adjusted, 2HP compressor OLR adjusted to 3.5A to 4 A, ATG cut off reconfigured - Rectifed
CL2478 | 2022-07-18 | Velacherry | D | Keypad issue | Breakdown | Suneel Sagar | 2022-07-18 | - | A side new keypad changed - Rectified
CL2479 | 2022-07-19 | Avinashi | C | Stamping work | Certification | Gowtham | 2022-07-19 | - | Stamping and PMR done - Completed
CL2480 | 2022-07-19 | Vellakoil | T | Unloading work | Breakdown | Thirumalaisamy | 2022-07-19 | - | Unloading completed. Unloading pump working fine.Tank 19% to 57% - Completed
CL2481 | 2022-07-19 | Tiruchengode | R | Electrical work | New Project | Chandrasekar & Nivas | 2022-07-20 | - | Electrical work partially completed - Civil and canopy instruction done - Attended
CL2482 | 2022-07-19 | Melur | T | Dispenser slow delivery | Breakdown | Kathiresan | 2022-07-20 | - | Dispensing bypass valve cleaned and dispensing emergency spare liquid line changed - Working fine. Pressure 11.5 kg /cm² - Rectified
CL2483 | 2022-07-19 | Kodumudi | R | Air compressor conductor damage | Breakdown | Thirumalaisamy | 2022-07-19 | - | Air compressor conductor damage. New conductor changed working fine - rectified
CL2484 | 2022-07-19 | Cantonment | D | Yenen dispenser swith issue and EB Y phase issue | Breakdown | Vigneshvaran | 2022-07-20 | - | Yenen dispenser D side nozzle switch new 1no changed and complaint has been filed in EB due to Y phase supply not working at the pump running only in genset mode - Working in EB mode rectified
CL2485 | 2022-07-20 | Cantonment | A | EF nozzle's automation power supply unit problem. | Breakdown | Madhavan & Vigneshwaran | 2022-07-20 | 4 Hours (EF Nozzle Only) | Power supply unit replaced - Rectified
CL2486 | 2022-07-20 | Uthamapalayam | D | EB neutral problem | Breakdown | Kamaraj | 2022-07-21 | - | EB service perspn resolved the problem - Rectified
CL2487 | 2022-07-20 | Palladam | D | Dispenser breakaway failure | Breakdown | Gowtham | 2022-07-19 | - | Batchen dispenser B side breakaway coupling refitted after service, need to be change new one. Testing - 6 Ltrs - Resolved
CL2488 | 2022-07-21 | Eral | T | CP installation | New Project | Dharmesh | 2022-07-21 | - | Cp installed R1 C1 = -0.534 R1 C2 = -0.530 R1 A1 = -1.530 R1 A2 = -1.500 R1 A3 = -1.580 R1 A4 = -1.550 After loop reading = -1.19 VDC Found satisfactory - Completed
CL2489 | 2022-07-21 | Namakkal 3 | T | Pipeline hydro | New Project | Nivas | 2022-07-21 | - | Dispensing liquid and vapour pipe line welding and hydro test done. Tested pressure 48 kg/cm2.Earth installation work partially done - Completed
CL2490 | 2022-07-21 | Ellis Nagar | C | Commissioning work, Stamping and Calibration | Certification | Prakash, Dharmesh & Kathiresan | 2022-07-22 | - | Commissiong work completed. All equipment working fine - Dispenser calibration and stamping done Calibration report: "A" side 10 ltrs = 10.02 "B" side 10 ltrs = 10.00 "C" side 10 ltrs = 10.03 "D" side 10 ltrs = 10.02 "K" factor report; ' A ' side K = 10000 ' B ' side K. = 10000 ' C ' side K = 10000 ' D ' side K = 10000- Completed
CL2491 | 2022-07-21 | Vellakoil | T | Unloading work | Breakdown | Thirumalaisamy | 2022-07-21 | - | Unloading work completed. pump working fine no leakage
CL2492 | 2022-07-22 | Namakkal 3 | T | Pipeline work | New Project | Nivas | 2022-07-22 | - | Electrical pipeline work done - GI flat work in process - Attended
CL2493 | 2022-07-22 | Bhavani | G | 70 Kg fire extinguisher CO2 hose damaged | Breakdown | Prabu | 2022-07-22 | - | 70 kg fire extinguisher CO2 hose replaced - Control panel solenoid air leakage arrested by applying teflon - Completed
CL2494 | 2022-07-22 | Devakottai | T | CP installation | New Project | Avinash | 2022-07-22 | - | CP installation work completed R1 C1 =-0.452 R1 C2 = 0.450 R1 A1 = 1.504 R1 A2 = 1.458 R1 A3 = 1.510 R1 A4 = 1.438 After looping reading = -1.124 completed
CL2495 | 2022-07-22 | Udumalpet | T | Site visit for above ground motor installation | Preventive | Gowtham | 2022-07-22 | - | Material list collected for above ground motor installation - Attended
CL2496 | 2022-07-22 | Vadivelan nagar | C | Preventive Maintenance | Certification | Suneel Sagar | 2022-07-22 | - | Preventinve maintenance done - Completed
CL2497 | 2022-07-22 | Sankari | C | PMR work | Certification | Prabu | 2022-07-22 | - | PMR done - Found satisfactory - Attended
CL2498 | 2022-07-23 | Namakkal 1 | R | Control panel solenoid air leakage | Breakdown | Prabu | 2022-07-23 | - | Solenoid coil replaced - Working fine - Rectified
CL2499 | 2022-07-23 | Ariyamangalam | D | Nozzle servicing | Preventive | Nepolean | 2022-07-23 | - | Nozzle from dindigul tested at D side - Testing : 4.5 Ltrs - Completed
CL2500 | 2022-07-24 | Ellis Nagar | A | Automation and outlet opening | New Project | Madhavan & Kathiresan | 2022-07-24 | - | Automation data available online and outlet opened to public - Attended
CL2501 | 2022-07-24 | Cantonment | A | Dispenser going offline due to USB converter board changing to network board | Preventive | Prasath | 2022-07-25 | - | All dispensers connected with network board - Working fine - Outlet back online - Resolved
CL2502 | 2022-07-25 | Namakkal 3 | G | Electrical work | New Project | Prabu | 2022-07-25 | - | Electrical and air hose laying work completed - Attended
CL2503 | 2022-07-26 | Cantonment | D | A and B side nozzle changed | Preventive | Chandrasekar | 2022-07-26 | - | Nozzles changed at A and B side - Working fine - A, side testing =1.11 litre B, side testing =1.13 litre A, side opening=9536945.44 A, side closing=9968806.05 A, side sales=431860.61 B, side opening =7932200.19 B, side closing =8395405.85 B, side sales=463205.66 - Completed
CL2504 | 2022-07-26 | Ariyamangalam | D | D side on/off switch not working properly | Breakdown | Nepolean | 2022-07-26 | - | New on/off switch replaced - D and C side nozzle serviced and tested - D side testing: 4.05 lit C side testing: 5.22 lit - Completed
CL2505 | 2022-07-26 | Villapuram | T | C and D side dispensing air hose damaged | Breakdown | Kathiresan | 2022-07-26 | - | EB room to dispenser air hose 26 mtrs changed - Working fine - Resolved
CL2506 | 2022-07-26 | Ammapettai | T | Tank hydro test | New Project | Prabu | 2022-07-26 | - | Hydro test done - Tested pressure 29 kg/cm² - Dispensing motor and decanting motor marking done - Completed
CL2507 | 2022-07-27 | Nasiyanur | T | Tank hydro test | New Project | Prabu | 2022-07-27 | - | Hydro test done - Tested pressure 29 kg/cm² - Dispensing motor and decanting motor marking done - Completed
CL2508 | 2022-07-27 | Vellakoil | G | Fire extinguisher service and training | Preventive | Thirumalaisamy | 2022-07-27 | - | 75 kg and 9 kg fire extinguishers tested and found satisfactory - Training provided - Completed
CL2509 | 2022-07-27 | Palladam | D | Yenen dispenser D side keypad failure | Breakdown | Gowtham | 2022-07-27 | - | New keypad replaced - Working fine - Rectified
CL2510 | 2022-07-27 | T.V.Kovil | G | Compressor oil changing | Preventive | Vigneshvaran | 2022-07-27 | - | Oil changed for both compressors - Attended
CL2511 | 2022-07-27 | Neelambur | G | Fire extinguisher service and training | Preventive | Gowtham | 2022-07-27 | - | 75 kg and 9 kg fire extinguishers tested and found satisfactory - Training provided - Completed
CL2512 | 2022-07-28 | Ramnad | T | Dispensing motor leakage | Breakdown | Kathiresan | 2022-07-28 | - | Bypass valve cleaned and leakage arrested - Motor alignment adjusted - Entire outlet leakage test done - Working normal - Resolved
CL2513 | 2022-07-29 | Neelambur | G | Dispenser power problem | Breakdown | Gowtham | 2022-07-29 | - | Transformer fuse (6.3A) replaced and then it's input voltage regulated to 400V - W1 contactor neutral wire loose contact it's automatically resolved while , cables disconnect and then re-assembling - Working fine - Testing : 1 Ltr - Rectified
CL2514 | 2022-07-29 | Eral | G | Pipeline trench and ALDS earth point marking | New Project | Kathiresan | 2022-07-29 | - | Pipeline trench and ALDS earth point marking done - Cable measurement done - Completed
CL2515 | 2022-07-30 | Eral | T | Dispensing liquid pipe line welding and hydro test | New Project | Avinash | 2022-07-30 | - | Dispensing liquid pipe line welding and hydro test done - Excess flow valves and flanges fitted - Completed
CL2516 | 2022-08-01 | Dharmapuri | D | Display B side hanging | Breakdown | Prabu | 2022-08-01 | - | Displays interchanged - Working fine - Dispensing motor spider 1 no replaced - Compressor air fitting 1 no changed to arrest air leakage - Testing : 4.83 Ltrs - Resolved
CL2517 | 2022-08-01 | Udumalpet | C | Rule 18 work tank 1 new dispensing motor installation and old RX 10 STP testing | Certification | Prakash, Nepolean, Gowtham & Dharmesh | 2022-08-03 | - | Above ground dispensing motor and pump commissioned - Working fine - Old RX10 STP failed - Rule 18 completed on 04.08.2022 - Resolved
CL2518 | 2022-08-01 | T.V.Kovil | G | Sales stopped due to product dry out | Breakdown | Vigneshvaran | 2022-08-01 | 1.40 Hours | Product unloaded - Sales stopped - Resolved
CL2519 | 2022-08-02 | Dindigul | A | Dispenser going offline due to CPU issue | Breakdown | Kamaraj | 2022-08-02 | - | CPU replaced - Dispenser back online - Rectified
CL2520 | 2022-08-02 | Mulanur | G | High voltage issue in EB supply | Breakdown | Thirumalaisamy | 2022-08-06 | - | Voltage reduced from EB supply - Resolved
CL2521 | 2022-08-02 | Kattupakkam | R | "Auto On" is not working in compressor due to low voltage | Breakdown | Suneel Sagar | 2022-08-02 | - | Compressor is connected with stabilizer - Working fine - Rectified
CL2522 | 2022-08-03 | Vedachandur | G | Fire extinguisher service and training | Preventive | Kamaraj | 2022-08-03 | - | Fire extinguisher checked and found satisfactory - Training provided to all staffs - Completed
CL2523 | 2022-08-03 | Eral | D | Dispenser installation | New Project | Avinash | 2022-08-03 | - | Dispenser installation done - Completed
CL2524 | 2022-08-03 | Rasipuram | G | Fire extinguisher service and training | Preventive | Prabu | 2022-08-03 | - | Fire extinguisher checked and found satisfactory - Training provided to all staffs - Completed
CL2525 | 2022-08-03 | Sankari | G | Fire extinguisher service and training | Preventive | Prabu | 2022-08-03 | - | Fire extinguisher checked and found satisfactory - Training provided to all staffs - Completed
CL2526 | 2022-08-03 | Theni | A | Outlet going offline due to automation converter board problem | Breakdown | Kamaraj | 2022-08-04 | - | Converter board connector replaced - Dispenser back online Before offline Reading : A side - 17612.14 B side - 11238.82 Before online Reading: A side - 17724.20 B side- 11449.11 - Rectified
CL2527 | 2022-08-04 | Tiruchengode | G | DG chemical earthing installation | New Project | Prabu | 2022-08-04 | - | Chemical earth installed - Completed
CL2528 | 2022-08-04 | Mulanur | C | Rule 18 work | Certification | Nepolean & Thirumalaisamy | 2022-08-04 | - | Rule 18 done - Completed
CL2529 | 2022-08-04 | Vellakoil | C | Rule 18 work | Certification | Nepolean & Thirumalaisamy | 2022-08-04 | - | Rule 18 done - Completed
CL2530 | 2022-08-04 | Eral | T | Tank area pipeline welding | New Project | Avinash | 2022-08-04 | - | Pipeline welding work completed - Attended
CL2531 | 2022-08-04 | Namakkal 3 | G | DG chemical earthing installation | New Project | Prabu | 2022-08-04 | - | Chemical earth installed - Completed
CL2532 | 2022-08-05 | Chinnasalem | R | Dispensing motor VFD installation | New Project | Chandrasekar & Prabu | 2022-08-05 | - | VFD installation completed - Working fine - Kept under observation for a day and it is satisfactory - Completed
CL2533 | 2022-08-05 | Uthamapalayam | D | Dispenser not running due to fuse damage because of voltage fluctuation | Breakdown | Kamaraj | 2022-08-05 | 1 Hour | Dispenser input power supply fuse changed - Working fine - Rectified
CL2534 | 2022-08-05 | Namakkal 3 | G | Site visit | New Project | Prakash | 2022-08-05 | - | Site visit completed - Attended
CL2535 | 2022-08-05 | Tiruchengode | G | Site visit | New Project | Prakash | 2022-08-05 | - | Site visit completed - Attended
CL2536 | 2022-08-05 | Kangayam | C | Rule 18 work | Certification | Nepolean | 2022-08-05 | - | Rule 18 done - Completed
CL2537 | 2022-08-05 | Palladam | C | Rule 18 work | Certification | Nepolean | 2022-08-05 | - | Rule 18 done - Completed
CL2538 | 2022-08-05 | Neelambur | C | Rule 18 work | Certification | Nepolean | 2022-08-05 | - | Rule 18 done - Completed
CL2539 | 2022-08-05 | Saravanampatti | C | Rule 18 work | Certification | Nepolean | 2022-08-05 | - | Rule 18 done - Completed
CL2540 | 2022-08-05 | Sulur | C | Rule 18 work | Certification | Nepolean | 2022-08-05 | - | Rule 18 done - Completed
CL2541 | 2022-08-05 | Theni | A | Batchen dispenser going offline due to converter board problem | Breakdown | Kamaraj | 2022-08-06 | - | Converter board replaced - Outlet back online - Resolved
CL2542 | 2022-08-06 | Thuraiyur | D | Batchen A side nozzle leakage | Breakdown | Nivas | 2022-08-06 | - | Nozzle serviced - NRV spring replaced - Leakage arrested - Working fine - Rectified
CL2543 | 2022-08-06 | Paramathivelur | D | Dispensing 5m hose damaged | Breakdown | Thirumalaisamy | 2022-08-06 | - | 5m dispensing hose replaced - Automation maintenance done - PMR done - Testing : 0.58 Ltrs - Resolved
CL2544 | 2022-08-06 | Mettupalayam | C | Rule 18 work | Certification | Nepolean | 2022-08-06 | - | Rule 18 done - Completed
CL2545 | 2022-08-06 | Avinashi | C | Rule 18 work | Certification | Nepolean | 2022-08-06 | - | Rule 18 done - Completed
CL2546 | 2022-08-06 | Avadi | R | Unloading solenoid plunger problem | Breakdown | Suneel Sagar | 2022-08-06 | - | Solenoid plunger cleaned - PMR done - Rectified
CL2547 | 2022-08-06 | T.V.Kovil | G | Fire extinguisher service and training | Preventive | Vigneshvaran | 2022-08-06 | - | Fire extinguisher refilling done - 75kg fire exinguisher damaged hose replaced - Training provided - Resolved
CL2548 | 2022-08-06 | Palayam | R | Control panel working improperly due to two phase supply | Breakdown | Thirumalaisamy | 2022-08-07 | - | Control panel working in two phase supply with VFD - Online UPS connection provided due to high supply - Panel working fine - Under observation - Rectified
CL2549 | 2022-08-07 | Eral | G | Dispensing and decanding pipe line welding and hydro test | New Project | Avinash | 2022-08-07 | - | Dispensing and decanding pipe line welding and hydro test done - pressure holding at 48 kg/cm² - Completed
CL2550 | 2022-08-08 | Kattupakkam | R | ATG signal interference due to VFD | Breakdown | Suneel Sagar | 2022-08-09 | - | VFD service engineers visited and adjusted perimeters to lose ATG signal interference - Kept under observation - Resolved
CL2551 | 2022-08-08 | Velacherry | D | Kalvacha dispenser display card and communication cable testing | Preventive | Suneel Sagar | 2022-08-08 | - | Display card and communication cable testing done - Found satisfactory - Completed
CL2552 | 2022-08-08 | Vadivelan nagar | T | ACME adapter and flange threading worn out | Breakdown | Suneel Sagar | 2022-08-19 | - | ACME flange and adapter replaced - Resolved
CL2553 | 2022-08-09 | Devakottai | T | Pipeline welding and hydro test | New Project | Nivas | 2022-08-09 | - | Dispensing liquid pipe line welding and hydro test done - Pressure holding at 48 kg/cm^2 - Excess flow valve fitted and flanges refitted - Rule 33 data collected - Completed
CL2554 | 2022-08-09 | Ariyamangalam | G | Fire extinguisher service and training | Preventive | Nepolean | 2022-08-09 | - | Fire extinguisher serviced and refillings done - Completed
CL2555 | 2022-08-10 | Vedachandur | D | Yenen dispenser motherboard problem | Breakdown | Kamaraj | 2022-08-10 | 7 Hours | New motherboard replaced - Working fine - Rectified
CL2556 | 2022-08-10 | Sankari | T | Dispensing motor noise | Breakdown | Prabu | 2022-08-10 | - | Dispensing motor spider replaced - Motor alignment checked - Working fine - Resolved
CL2557 | 2022-08-10 | Rasipuram | R | Control panel voltage scanner defect | Breakdown | Prabu | 2022-08-10 | - | Defective voltage scanner replaced with new - Working fine - Rectified
CL2558 | 2022-08-10 | Thuraiyur | D | Dispensing hose damaged and nozzle servicing | Breakdown | Nepolean | 2022-08-10 | - | 5m dispensing hose replaced - A side nozzle serviced - Working fine - Resolved
CL2559 | 2022-08-10 | Palladam 2 | D | Nozzle mount problem | Breakdown | Gowtham | 2022-08-10 | - | Nozzle mount refitted - Working fine - Testing : 0.800 Ltrs - Rectified
CL2560 | 2022-08-10 | Eral | G | Earth installation | New Project | Avinash | 2022-08-10 | - | Earth installed - Cable laying started - Attended
CL2561 | 2022-08-11 | Vadivelan nagar | T | Dispensing motor is not properly running due to run signal | Breakdown | Suneel Sagar | 2022-08-11 | - | Control panel auxiliary contact spare NO connected - Addon block replaced with new - Kept under observation - Resolved
CL2562 | 2022-08-12 | Ammapet | T | CP installation | New Project | Prabu | 2022-08-12 | - | CP installed - R-C1=0.610 R-C2=0.610 R-A1=1.730 R-A2=1.720 R-A3=1.710 R-A3=1.720 Total =1.220 - Completed
CL2563 | 2022-08-12 | Ramnad | R | Servo stabilizer not working - R phase winding coil vibrating | Breakdown | Kathiresan | 2022-08-12 | - | Stabilizer voltage settings adjusted - R phase winding coil alignment adjusted - Working fine - Resolved
CL2564 | 2022-08-12 | Nasiyanur | T | CP installation | New Project | Thirumalaisamy | 2022-08-12 | - | CP installation work done. R-C1=0.590 R-C2=0.590 R-A1=1.780 R-A2=1.780 R-A3=1.770 R-A4=1.760 Looped=1.228 Fencing area marking done - Completed
CL2565 | 2022-08-12 | Vedachandur | D | Mother board servicing and testing | Preventive | Kamaraj | 2022-08-12 | - | Old mother board repaired and tested - Working fine - Kept under observation - Resolved
CL2566 | 2022-08-12 | Eral | G | Electrical cable laying | New Project | Avinash | 2022-08-12 | - | Cable laying done - Completed
CL2567 | 2022-08-12 | Devakottai | T | Tank area welding work | New Project | Nivas | 2022-08-12 | - | Tank area welding done - Earth installation done - Completed
CL2568 | 2022-08-13 | Devakottai | C | Rule 33 third party visit | Certification | Prakash & Vignesh | 2022-08-13 | - | Rule 33 third party inspection done - Attended
CL2569 | 2022-08-13 | Virudhunagar | T | Dispensing liquid line and vapour line ROV not working | Breakdown | Kathiresan | 2022-08-13 | - | Dispensing solenoid coil replaced - Working fine - Resolved
CL2570 | 2022-08-13 | Velachery | C | PMR work | Preventive | Suneel Sagar | 2022-08-13 | - | PMR done - Completed
CL2571 | 2022-08-16 | Erode | T | Dispensing motor running only in test mode - Offline UPS input supply phase reversing | Breakdown | Thirumalaisamy | 2022-08-16 | - | Supply phase neutral interchanged - Dispensing motor working in run mode - Tank area Ball valve with ROV LPG leakage arrested by applying teflon and tightening the nut - Online UPS and automation maintenance done - PMR done - Safety training and fire extinguishers operation training given to Pump staffs - Completed
CL2572 | 2022-08-17 | Sulur | C | PMR work | Certification | Gowtham | 2022-08-17 | - | PMR done - Unloading vent line serviced - Completed
CL2573 | 2022-08-17 | Cantonment | C | Rule 18 work | Certification | Nepolean | 2022-08-17 | - | Rule 18 done - Completed
CL2574 | 2022-08-17 | Ariyamangalam | C | Rule 18 work | Certification | Nepolean | 2022-08-17 | - | Rule 18 done - Completed
CL2575 | 2022-08-17 | T.V.Kovil | C | Rule 18 work | Certification | Nepolean | 2022-08-17 | - | Rule 18 done - Completed
CL2576 | 2022-08-17 | Devakottai | D | Dispenser installation | New Project | Nivas | 2022-08-17 | - | Dispenser installation done - Completed
CL2577 | 2022-08-17 | Chengalpattu | C | PMR work | Certification | Suneel Sagar | 2022-08-17 | - | PMR done - Completed
CL2578 | 2022-08-18 | Thuraiyur | C | Rule 18 work | Certification | Nepolean | 2022-08-18 | - | Rule 18 done - Completed
CL2579 | 2022-08-18 | Devakottai | G | Pipeline hydro test | New Project | Nivas | 2022-08-18 | - | Pipeline hydro test done at pressure 48 Kg/cm2 - Completed
CL2580 | 2022-08-19 | Thiruvaiyaru | C | Rule 18 work | Certification | Nepolean & Vignesh | 2022-08-19 | - | Rule 18 done - Completed
CL2581 | 2022-08-19 | Puliyur | G | Nitrogen testing | New Project | Chandrasekar & Dharmesh | 2022-08-19 | - | N2 test completed at pressure 14 kg/cm2 - Holding pressure 10 kg/cm2 - Automation installation partially done - Control panel booted - Completed
CL2582 | 2022-08-19 | Namakkal 2 | D | Dispenser low flow slow delievery | Breakdown | Prabu | 2022-08-19 | - | Bypass valve cleaned and equaliser ball valve adjusted - Dispenser filling pressure developed - Kept under observation - Resolved
CL2583 | 2022-08-19 | Kodungaiyur | T | ATG configuration and PMR | Preventive | Suneel Sagar | 2022-08-19 | - | ATG configured and PMR done - Completed
CL2584 | 2022-08-19 | T.V.Kovil | D | Batchen dispenser B side nozzle teeth damage | Breakdown | Avinash | 2022-08-19 | - | Nozzle teeth 4 nos replaced - Rectified
CL2585 | 2022-08-19 | Kumbakonam | C | Rule 18 work | Certification | Nepolean & Vignesh | 2022-08-19 | - | Rule 18 done - Completed
CL2586 | 2022-08-19 | Villapuram | D | Dispencer C side nozzle leakage | Breakdown | Kathiresan | 2022-08-19 | - | Nozzle teeth 4 nos replaced - Compressor oil changed - Tank area liquid and unloading vapour line ball valve leakage arrested by tightening the stem - PMR done - Rectified
CL2587 | 2022-08-20 | Pudukkottai | C | Rule 18 work | Certification | Nepolean & Vignesh | 2022-08-20 | - | Rule 18 done - Completed
CL2588 | 2022-08-20 | Ramnad | C | Rule 18 work | Certification | Kathiresan,Nepolean & Vignesh | 2022-08-20 | - | Rule 18 done - Completed
CL2589 | 2022-08-20 | T.V.Kovil | D | Batchen dispenser B side metering unit | Breakdown | Avinash | 2022-08-20 | 2 Hours (B side) | Leakage arrested by changing bearing and seal kit - Testing : 10.55 lts - Rectified
CL2590 | 2022-08-20 | Puliyur | G | Genset and Compressor commisioning | New Project | Thirumalaisamy | 2022-08-20 | - | Commisioning done - Control panel Dispensing motor decanting motor woring in DG mode - Completed
CL2591 | 2022-08-20 | Cantonment | D | C side nozzle teeth damaged | Breakdown | Chandrasekar | 2022-08-20 | - | Nozzle teeth 4nos replaced - Rectifeid
CL2592 | 2022-08-21 | Karur | D | D side nozzle teeth damaged | Breakdown | Thirumalaisamy | 2022-08-21 | - | Nozzle teeth 4nos replaced - Rectifeid
CL2593 | 2022-08-21 | Palldam 2 | A | Camera hard disk failure and Automation network issue | Breakdown | Gowtham | 2022-08-21 | - | Hard disk replaced - Network issue resolved - Rectified
CL2594 | 2022-08-21 | Vadivelan nagar | T | Dispensing vapour ROV LPG leakage | Breakdown | Suneel Sagar | 2022-08-21 | - | Dispensing vapour ROV leakage arrested by tightening the nut - Resolved
CL2595 | 2022-08-21 | Tirunelveli | C | Rule 18 work | Certification | Kathiresan,Nepolean & Vignesh | 2022-08-21 | - | Rule 18 done - Completed
CL2596 | 2022-08-21 | Virudhunagar | C | Rule 18 work | Certification | Kathiresan,Nepolean & Vignesh | 2022-08-21 | - | Rule 18 done - Completed
CL2597 | 2022-08-21 | Villapuram | C | Rule 18 work | Certification | Kathiresan,Nepolean & Vignesh | 2022-08-21 | - | Rule 18 done - Completed
CL2598 | 2022-08-22 | Theni | C | Rule 18 work | Certification | Kamaraj,Nepolean & Vignesh | 2022-08-22 | - | Rule 18 done - Completed
CL2599 | 2022-08-22 | Namakkal 3 | R | Control panel booting - Tank N2 test | New Project | Prabu, Chandrasekar & Dharmesh | 2022-08-22 | - | Control panel booted - N2 Testing done - Testing pressure 14.5Kg/cm^2 - Holding pressure 10kg/cm^2 - Completed
CL2600 | 2022-08-22 | T.V.Kovil | D | Batchen dispenser B side low flow solenoid problem | Breakdown | Avinash | 2022-08-22 | 2 Hours (B side) | New low flow solenoid coil replaced - Dispenser working fine - Testing : 6.59 Ltrs - Rectified
CL2601 | 2022-08-22 | Vadivelan nagar | T | Tank 1 unloading liquid and vapour flanges leakage | Breakdown | Suneel Sagar | 2022-08-22 | - | Tank 1 unloading liquid and vapour flanges leakage arrested by tightening the nut - unloading front ROV leakage and 2nd dispenser Liquid RoV gland leakage arrested by tightening the nut - Resolved
CL2602 | 2022-08-22 | Theni | D | Angle needle valve leakage | Breakdown | Nepolean | 2022-08-22 | -
CL2603 | 2022-08-23 | Velachery | G | ALDS emergency & Fire extinguisher operation training | Preventive | Suneel Sagar | 2022-08-23 | - | ALDS emergency & Fire extinguisher operation training given - Completed
CL2604 | 2022-08-23 | T.V.Kovil | D | C side nozzle teeth damage | Breakdown | Avinash | 2022-08-23 | - | Nozzle teeth 4 nos replaced - Rectified
CL2605 | 2022-08-23 | Devakottai | G | Chemical earth installation | New Project | Nivas | 2022-08-23 | - | Chemical earth installation done - Completed
CL2606 | 2022-08-23 | Bodi | C | Rule 18 work | Certification | Kamaraj,Nepolean & Vignesh | 2022-08-23 | - | Rule 18 done - Completed
CL2607 | 2022-08-23 | Uthamapalayam | C | Rule 18 work | Certification | Kamaraj,Nepolean & Vignesh | 2022-08-23 | - | Rule 18 done - Completed
CL2608 | 2022-08-23 | Vedachandur | C | Rule 18 work | Certification | Kamaraj,Nepolean & Vignesh | 2022-08-23 | - | Rule 18 done - Completed
CL2609 | 2022-08-23 | Dindigul | C | Rule 18 work | Certification | Kamaraj,Nepolean & Vignesh | 2022-08-23 | - | Rule 18 done - Completed
CL2610 | 2022-08-23 | Theni | D | B side metering unit LPG leakage | Breakdown | Kamaraj,Nepolean & Vignesh | 2022-08-23 | - | Leakage arrested by changing bearing and seal kit - Rectified
CL2611 | 2022-08-23 | Villapuram | G | Earth generation and dispenser bottom side LPG leakage | Breakdown | Kathiresan | 2022-08-23 | - | Earth generated and dispenser bottom side LPG leakage arrested by tightening the nut - Rectified
CL2612 | 2022-08-24 | Tharamangalam | C | Calibration and stamping | Certification | Vignesh | 2022-08-24 | - | Calibration and stamping done - Completed
CL2613 | 2022-08-25 | Velachery | D | A side on/off switch problem | Breakdown | Suneel Sagar | 2022-08-25 | - | On/off switch NC element replaced - Testing : 30.31 Ltrs - Resolved
CL2614 | 2022-08-25 | Tiruchengode | T | N2 testing | New Project | Dharmesh | 2022-08-25 | - | N2 testing done - Testing Pressure : 14.5 kg/cm2 - Holding pressure 10 kg/cm2 - Control panel booted - Completed
CL2615 | 2022-08-25 | T.V.Kovil | D | Batchen dispenser B side Low flow solenoid coil heating problem | Breakdown | Avinash | 2022-08-25 | 20 Hours (B side) | Low flow and High flow solenoid coil inter changed - Working fine - Resolved
CL2616 | 2022-08-25 | Chengalpattu | D | Yenen dispenser keypad problem | Breakdown | Suneel Sagar | 2022-08-25 | - | Keypad replaced
CL2617 | 2022-08-25 | Sankari | C | Calibration and stamping | Certification | Prabu | 2022-08-24 | - | Calibration and stamping done - Completed
CL2618 | 2022-08-27 | Ellis Nagar | G | Total leakage testing and PMR | Preventive | Kathiresan | 2022-08-27 | - | Total leakage testing and PMR done - Completed
CL2619 | 2022-08-27 | Devakottai | G | Electrical cable and air hose laying and connection | New Project | Nivas | 2022-08-27 | - | Electrical cable and air hose laying and connection done - Completed
CL2620 | 2022-08-27 | Nasiyanur | T | Dispensing liquid pipe line welding | New Project | Thirumalaisamy | 2022-08-27 | - | Tank flanges removed and dispensing liquid pipe line welding work done - Completed
CL2621 | 2022-08-28 | Namakkal 3 | G | Genset and Compressor commisioning | New Project | Prabu | 2022-08-29 | - | Genset and compressor commissioning done - Control panel, dispensing and decanding motor working fine in DG mode - Completed
CL2622 | 2022-08-28 | Nasiyanur | T | Dispensing liquid line hydro test | New Project | Thirumalaisamy | 2022-08-28 | - | Dispensing liquid line hydro test done - Hydro test pressure @ 48kg/cm^2 - Holding pressure 48kg/cm^2 - Completed
CL2623 | 2022-08-29 | Avadi | G | Input supply fuse damaged due earthing problem | Breakdown | Suneel Sagar | 2022-08-29 | - | Incoming supply B phase 100amps fuse Replaced by new one - Eath pits regenerated now Neutral to earth value is 5v and earlier it was 15 V - Yard light cable joint corrected and pulled back into conduit. Now ALDS and lighting is working on EB and DG satisfactory - Lodged complaint in EB as meter is not working due to heavy rain on yesterday so transformer short circuit happened - Resolved
CL2624 | 2022-08-29 | Puliyur | G | Commissioning work | New Project | Thirumalaisamy, Prakash, Chandrasekar & Dharmesh | 2022-08-30 | - | Commissioning and calibration done - Dispenser, dispensing pump, decanting pump, atg, rochester working fine - Puliyur outlet opening reading:- A Nozzle-257.28 B Nozzle-286.19 Tank-75% - Attended
CL2625 | 2022-08-29 | Villapuram | A | A and B side automation cable damaged | Breakdown | Kathiresan | 2022-08-29 | 1 Hour (A & B side) | 32 mtrs automation cable replaced - Working fine - Rectified
CL2626 | 2022-08-30 | T.V.Kovil | T | Oil pump FRC damaged | Breakdown | Vignesh | 2022-08-30 | - | Oil pump FRC replaced - Working fine - Resolved
CL2627 | 2022-08-30 | Puliyur | C | Dispenser stamping | Certification | Thirumalaisamy, Prakash, Chandrasekar & Dharmesh | 2022-08-30 | - | Stamping done - Calibration report: "A" side 10 ltrs = 10.00 "B" side 10 ltrs = 10.01 "K" factor report; ' A ' side K = 10000 ' B ' side K = 10000 - Training provided to Outlet staffs - Completed
CL2628 | 2022-08-31 | Puliyur | A | Automation installation | New Project | Madhavan | 2022-08-31 | - | Automation installed and outlet brought online - Data available online in KR admin app - Completed
CL2629 | 2022-08-31 | Dharapuram | D | B side display not working | Breakdown | Gowtham | 2022-08-31 | - | Temporarily replaced by a new display - Working fine - Rectified
CL2630 | 2022-09-01 | Dharmapuri | D | B side display not working | Breakdown | Prabu | 2022-09-01 | - | Display cable interchanged - A side nozzle serviced - Testing : 10 Ltrs - Resolved
CL2631 | 2022-09-01 | T.V.Kovil | A | Automation software testing | Preventive | Madhavan | 2022-09-01 | - | Automation software testing done - C nozzle testing - 43.39 liters D nozzle testing - 166.26 liters Total testing - 209.65 liters - Completed
CL2632 | 2022-09-01 | Melur | C | Calibration and stamping | Certification | Kathiresan | 2022-09-01 | - | Calibration and stamping done Calibration report: "A" side 10 ltrs = 9.98 "B" side 10 ltrs = 10.02 "K" factor report : "A" side = 10100 "B" side = 10070 - Completed
CL2633 | 2022-09-01 | Hosur | D | B side nozzle leakage | Breakdown | Suresh | 2022-09-01 | - | Nozzle teeth replaced - Working fine - Resolved
CL2634 | 2022-09-02 | Melur | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-09-02 | - | Rule 18 done - Completed
CL2635 | 2022-09-02 | Vedachandur | C | Stamping work | Certification | Nepolean & Dharmesh | 2022-09-02 | - | Stamping work done - Attended
CL2636 | 2022-09-02 | Thiruvaiyaru | D | A nozzle slow delivery | Breakdown | Chandrasekar | 2022-09-02 | - | Flow adjusted - Working fine - Testing : A side : 3.18 Ltrs - B side - 1.59 Ltrs - Resolved
CL2637 | 2022-09-02 | Kattupakkam | C | PMR work | Certification | Suneel Sagar | 2022-09-02 | - | PMR done - Completed
CL2638 | 2022-09-02 | Vellakovil | C | Calibration work | Certification | Nepolean, Thirumalaisamy & Dharmesh | 2022-09-03 | - | Calibration done - Calibration report: 'A' side 10 ltrs = 10.02 'B' side 10 ltrs = 10.00 'C' side 10 ltrs = 10.06 'D' side 10ltrs = 9.98 "K" factor report: "A" side Old 'K' =1.0446 "A" side New 'K'=1.0602 "B " side old 'K'= 1.0286 "B" side New 'K' =1.0071 "C" side old 'K' =10000 "C" side New 'K'=10000 "D" side old 'K' =10000 "D"side New 'K'=10000 Testing: A Nozzle-401.14 liters B Nozzle-590.08 liters C Nozzle-176.74 liters D Nozzle-152.57 liters Total Testing-1320.53liters - Completed
CL2639 | 2022-09-03 | Ramnad | D | A nozzle slow delivery | Breakdown | Kathiresan | 2022-09-03 |  | Dispenser filter cleaned and refitted - Slow delivery arrested - Testing : 20 Ltrs - Rectified
CL2640 | 2022-09-03 | Sulur | C | Stamping work | Certification | Nepolean, Dharmesh & Gowtham | 2022-09-03 | - | Stamping done "K" factor report: "A" side 'K' = 10175 "B" side 'K' = 10175 Testing: A Nozzle- 177.80 ltrs B Nozzle- 164.90 ltrs Total Testing- 342.70 ltrs - Completed
CL2641 | 2022-09-03 | Neelambur | C | Stamping work | Certification | Nepolean, Dharmesh & Gowtham | 2022-09-03 | - | Stamping done Calibration report: 'A' side 10 ltrs = 10.02 'B' side 10 ltrs = 10.02 "K" factor report: "A" side Old 'K' = 10200 "A" side New 'K'= 10035 "B" side Old 'K'= 10200 "B" side New 'K' = 10035 Testing: A Nozzle- 159.49 ltrs B Nozzle- 301.47 ltrs Total Testing- 460.96 ltrs - Completed
CL2642 | 2022-09-03 | Saravanampatty | C | Calibration work | Certification | Nepolean, Dharmesh & Gowtham | 2022-09-04 | - | Calibration done Calibration details: 'A' side 10 ltrs = 9.99 'B' side 10 ltrs = 9.98 "K" factor report: "A" side Old 'K' = 10015 "A" side New 'K'= 9920 "B" side Old 'K'= 10025 "B" side New 'K' = 10015 Testing: A Nozzle- 935.46 ltrs B Nozzle- 416.19 ltrs Total Testing- 1351.65 ltrs- Completed
CL2643 | 2022-09-04 | Kangayam | C | Calibration work | Certification | Nepolean, Dharmesh & Gowtham | 2022-09-04 | - | Calibration done Calibration report: 'A' side 10 ltrs = 10.02 'C' side 10 ltrs = 9.99 'D' side 10ltrs = 9.98 'B" side not calibrated due to display problem. "K" factor report: "C" side Old 'K' =10200 "C" side New 'K'=10250 "D" side Old 'K' =10300 "D" side New 'K'=10250 A & B side no K factor (Kalvacha dispenser) Testing: A Nozzle- 106.37 ltrs C Nozzle- 216.19 ltrs D Nozzle- 208.49 ltrs Total Testing- 531.05 - Completed
CL2644 | 2022-09-04 | Dharapuram | C | Calibration work | Certification | Nepolean, Dharmesh & Gowtham | 2022-09-04 | - | Calibration done A side- 434.80 B side - 437.15 Total testing lts - 871.95 lts - Completed
CL2645 | 2022-09-05 | Ariyamangalam | C | Calibration work | Certification | Nepolean | 2022-09-05 | - | Calibration done Testing liters. A side : 126.88 B side : 144.47 C side : 141.10 D side : 444.23 Total testing: 856.68 lit. - Completed
CL2646 | 2022-09-06 | Velachery | C | Calibration work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-07 | - | Calibration completed - A side metering unit LPG leakage arrested by replacing mechanical seal kit - Testing at A Side : 172.05 Ltrs - Rule 18 done - Working fine (Kalvacha dispenser) A. Side sales-10=10.08 B. Side sales-10=9.99 C. Side sales-10=10.05 D. Side sales-10=10.02 A-testing=104.32 B-testing=100.15 C-testing=105.21 D-testing=98.51 Total testing=408.19 litre - Completed
CL2647 | 2022-09-06 | Virudhunagar | A | Dispenser jumping problem | Breakdown | Madhavan, Prakash, Arulrayappan & Kathiresan | 2022-09-06 | - | Point jumping is under observation - Attended
CL2648 | 2022-09-06 | Dharapuram | C | Stamping Work | Certification | Thirumalai samy & Gowtham | 2022-09-06 | - | Stamping done - Completed
CL2649 | 2022-09-06 | Vellakoil | C | Stamping Work | Certification | Thirumalai samy & Gowtham | 2022-09-06 | - | Stamping done - Completed
CL2650 | 2022-09-06 | Kangeyam | C | Stamping Work | Certification | Thirumalai samy & Gowtham | 2022-09-06 | - | Stamping done - Completed
CL2651 | 2022-09-06 | Namakkal 3 | G | Fire extinguisher filling | Preventive | Prabu | 2022-09-06 | - | Fire extinguishers filled - Completed
CL2652 | 2022-09-06 | Namakkal 1 | G | Fire extinguisher replacing | Preventive | Prabu | 2022-09-06 | - | 9 kg fire extinguisher 1 no replaced with ABC type extinguisher - Training provided - Completed
CL2653 | 2022-09-06 | Rasipuram | G | Fire extinguisher hose problem | Preventive | Prabu | 2022-09-06 | - | 70 Kg fire extinguisher hose replaced - Resolved
CL2654 | 2022-09-07 | Dharmapuri | A | Automation communication cable problem | Breakdown | Prabu | 2022-09-07 | - | Communication cable replaced - Working fine - Testing : A side 10.00 - B side 03.57 Total testing. 13.57 Ltrs - Resolved
CL2655 | 2022-09-07 | Virudhunagar | A | Communication error | Breakdown | Kathiresan | 2022-09-07 | - | Two mobiles given for separate nozzles - Under observation - Resolved
CL2656 | 2022-09-07 | Theni | G | Canopy light cable fully damaged | Breakdown | Kamaraj | 2022-09-08 | - | Lights installed temporarily - Completed
CL2657 | 2022-09-07 | Vadivelan nagar | C | Rule 18 and calibration work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-07 | - | Rule 18 and calibration done A. Side-10=10.06 B. Side-10=10.02 C. Side-10=10.03 D. Side-10=10.08 K. Factors : A. Side-10110 B. Side-10160 C. Side-10160 D. Side-10100 K. Factor no changes. Testing : A. Side=107.76 B. Side=104.78 C. Side=124.16 D. Side=102.00 Total testing =438.70 litre - Completed
CL2658 | 2022-09-08 | Nasiyanur | G | Site marking | New Project | Prabu | 2022-09-08 | - | Fill point marking done - Completed
CL2659 | 2022-09-08 | Thuraiyur | D | Dispenser running in test mode not working in run mode | Breakdown | Nepolean | 2022-09-08 | - | R1 relay replaced with new one - Working fine - Dispenser running in run mode - Rectified
CL2660 | 2022-09-08 | Thanjavur | G | Fire extinguisher servicing and refilling | Preventive | Pandi Durai | 2022-09-08 | - | Fire extinguisher servicing and refilling done - Completed
CL2661 | 2022-09-08 | Tirunelveli | T | Unloading line ballvalve stem leakage | Breakdown | Kathiresan | 2022-09-08 | - | Ballvalve stem leakage arrested by tightening the nut - Rectified
CL2662 | 2022-09-08 | Tirunelveli | G | Camera not working and stock problem | Breakdown | Kathiresan | 2022-09-16 | Batchen from 9am on 16.09.2022 | One camera serviced and another camera installed - Yenen dispenser kept under observation - Batchen sales stopped - 10 days under observation - Attended
CL2663 | 2022-09-08 | Tenkasi | G | Site marking | New Project | Kathiresan | 2022-09-08 | - | Site boundary line, Tank area, Office room and EB room marking done - Completed
CL2664 | 2022-09-08 | Kodungaiyur | C | Rule 18 work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-08 | - | Rule 18 work done - Completed
CL2665 | 2022-09-08 | Velachery | C | Stamping work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-08 | - | Stamping work done A. Testing =46.69 B. Testing =51.12 C. Testing =38.18 D. Testing =40.24 Total testing =176.23litre - Attended
CL2666 | 2022-09-08 | Vadivelan nagar | C | Stamping work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-08 | - | Stamping work done - Attended
CL2667 | 2022-09-08 | Pudukkottai | G | Fire extinguisher servicing and refilling | Preventive | Pandi Durai | 2022-09-08 | - | Fire extinguisher servicing and refilling done - Training provided - Completed
CL2668 | 2022-09-09 | Avadi | C | Rule 18 work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-09 | - | Rule 18 done - To avoid miscommunication between nozzles to converter interface, the head has been assigned with default values : AB - 1; CD - 2; EF -3 - Completed
CL2669 | 2022-09-09 | Kattupakkam | T | Pressure gauge and needle valve defect | Breakdown | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-09 | - | Pressure gauge and needle valve replaced with new one - To avoid miscommunication between nozzles to converter interface, the head has been assigned with default values : AB - 1; CD - 2; EF -3 - Completed
CL2670 | 2022-09-09 | Vadivelan nagar | A | C and D nozzle address changing | Preventive | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-09 | - | To avoid miscommunication between nozzles to converter interface, the head has been assigned with default values : AB - 1; CD - 2; EF -3 - Completed
CL2671 | 2022-09-09 | Ellis Nagar | A | C and D nozzle address changing | Preventive | Kathiresan | 2022-09-09 | - | To avoid miscommunication between nozzles to converter interface, the head has been assigned with default values : AB - 1; CD - 2; EF -3 - Completed
CL2672 | 2022-09-09 | Chengalpattu | C | Rule 18 work | Certification | Chandrasekar, Vignesh & Suneel Sagar | 2022-09-09 | - | Rule 18 work done - Completed
CL2673 | 2022-09-10 | Virudhachalam | C | Rule 18 work | Certification | Chandrasekar & Vignesh | 2022-09-10 | - | Rule 18 work done - Completed
CL2674 | 2022-09-10 | Villapuram | A | C and D nozzle address changing | Preventive | Kathiresan | 2022-09-10 | - | To avoid miscommunication between nozzles to converter interface, the head has been assigned with default values : AB - 1; CD - 2; EF -3 - Completed
CL2675 | 2022-09-11 | Mulanur | R | Servo stabilizer R phase carbon bush burnt | Breakdown | Kamaraj | 2022-09-11 | - | R phase carbon replaced - Working fine - Rectified
CL2676 | 2022-09-12 | Kodumudi | D | Nozzle teeth problem | Breakdown | Thirumalaisamy | 2022-09-12 | - | Nozzle teeth 4nos replaced - Rectifeid
CL2677 | 2022-09-12 | Ariyamangalam | C | Stamping work and nozzle teeth problem | Certification | Nepolean | 2022-09-12 | - | Stamping work done - Nozzle teeth 4nos replaced - D side testing: 100.13 ltrs - Rectifeid
CL2678 | 2022-09-12 | Nasiyanur | G | Electrical cable measuring | New Project | Thirumalaisamy | 2022-09-12 | - | Electrical cable measuring done - Pipeline welding partially completed - Attended
CL2679 | 2022-09-12 | T.V.Kovil | D | Dispenser A nozzle not working properly | Breakdown | Avinash | 2022-09-12 | - | Nozzle teeth 4 Nos replaced - B side nozzle front O ring replaced - Working fine - Resolved
CL2680 | 2022-09-12 | Tharamangalam | D | Dispenser A nozzle not working properly | Breakdown | Prabu | 2022-09-12 | - | Nozzle teeth replaced on both A and B side - PMR done - Working fine - Resolved
CL2681 | 2022-09-13 | Tirunelveli | C | Calibration work | Certification | Dharmesh & Kathiresan | 2022-09-14 | - | Calibration done - Calibration reports: "A " side 10 ltr = 10.00 "B " side 10 ltr = 9.98 "C " side 10 ltr = 9.98 "D " side 10 ltr = 9.99 " K " factor There is no changes " A " side = 102300 " B " side = 102000 " C " side = 10341 " D " side = 10330 Density reports : 1. Batchen = 525 2. Yenen = 535 - Completed
CL2682 | 2022-09-13 | Saravanampatty | C | Stamping work | Certification | Gowtham | 2022-09-13 | - | Stamping done - Dispenser display glass changed - Completed
CL2683 | 2022-09-13 | Tiruchengode | G | Fire extinguisher filling | Preventive | Prabu | 2022-09-13 | - | Fire extinguisher filling done - Completed
CL2684 | 2022-09-13 | Tharamangalam | G | Fire extinguisher servicing | Preventive | Prabu | 2022-09-13 | - | 9 kg fire extinguisher 1 no replaced with ABC type extinguisher - 75 Kg fire extinguisher top up done - Training provided - Completed
CL2685 | 2022-09-13 | Ayothiyapattinam | G | Fire extinguisher servicing | Preventive | Prabu | 2022-09-13 | - | 75 Kg fire extinguisher top up done - Training provided - Completed
CL2686 | 2022-09-13 | Perambalur | D | Dispenser bottom liquid line ROV leakage | Breakdown | Avinash | 2022-09-13 | - | Leakage arrested by applying teflon and tightening the nut - Completed
CL2687 | 2022-09-14 | Bodi | G | Unloading camera not working | Breakdown | Kamaraj | 2022-09-15 | - | Alternative camara replaced temporarily - Dispenser nozzle rope changed - PMR done - Resolved
CL2688 | 2022-09-14 | Udumalpet | T | CP inspection and dispenser keypad replacing | Breakdown | Gowtham | 2022-09-14 | - | CP inspection done - Anodes and CP juction box to be replaced - B side litre preset keypad newly replaced - Testing : 55.46 Ltrs - Attended
CL2689 | 2022-09-14 | Nasiyanur | G | Pipeline hydro test | New Project | Thirumalaisamy | 2022-09-14 | - | Pipeline hydro test done at pressure 48 Kg/cm2 - Rule 33 data collected - Completed
CL2690 | 2022-09-14 | Kattupakkam | D | D side keypad not working | Breakdown | Suneel Sagar | 2022-09-25 | - | Working with mobile - D side keypad replaced by new - Resolved
CL2691 | 2022-09-14 | Neelambur | T | CP inspection | Preventive | Gowtham | 2022-09-14 | - | Anode and reference electrode re arraged - Found satisfactory - Completed
CL2692 | 2022-09-14 | Avinashi | T | CP inspection | Preventive | Gowtham | 2022-09-14 | - | CP needs to be replaced - Attended
CL2693 | 2022-09-15 | Uthamapalayam | D | Dispenser rope replacing | preventive | Kamaraj | 2022-09-15 | - | Dispenser nozzle rope changed - PMR done - Resolved
CL2694 | 2022-09-15 | Devakottai | G | Site visit | New Project | Chandrasekar | 2022-09-15 | - | Canopy and fencing work in process - Attended
CL2695 | 2022-09-15 | Namakkal 2 | D | Nozzle leakage | Breakdown | Prabu | 2022-09-15 | - | Nozzle teeth replaced and serviced - Control panel RYB indication damaged lights replaced with new - Rectified
CL2696 | 2022-09-16 | Ariyamangalam | A | Dispenser going offline for automation maintenance | Preventive | Madhavan | 2022-09-16 | - | Maintenance done - Outlet back online - Completed
CL2697 | 2022-09-16 | Cantonment | G | N2 machine hose leakage | Breakdown | Chandrasekar | 2022-09-16 | - | New hose replaced - Rectified
CL2698 | 2022-09-16 | Ayothiyapattinam | G | Unloading training | Preventive | Prabu | 2022-09-16 | - | Unloading training done - Compressor oil changed - UPS battery topped up with distilled water - Total pipeline leakage checked - Found satisfactory - Completed
CL2699 | 2022-09-16 | Eral | T | Tank N2 testing | New Project | Kathiresan | 2022-09-16 | - | Nitrogen testing completed - Testing pressure 14 kg/cm2, holding pressure 10 kg/cm² - Electrical work done - Completed
CL2700 | 2022-09-17 | Kattupakkam | T | Pressure gauge defect | Breakdown | Suneel Sagar | 2022-09-17 | - | Pressure gauge replaced with new one - Resolved
CL2701 | 2022-09-17 | Velachery | A | A nozzle lock damaged | Breakdown | Suneel Sagar | 2022-09-17 | - | Nozzle lock 1 set replaced - Working fine - Resolved
CL2702 | 18-09-2022 | Devakottai | G | Canopy and fencing | New Project | Dharmesh & Chandrasekar | 19-09-2022 | - | Canopy and fencing work done - Completed
CL2703 | 18-09-2022 | Nasiyanur | C | Rule 33 inspection & cable laying work | New Project | Thirumalaisamy | 18-09-2022 | - | Rule 33 inspection done - attended
CL2704 | 19-09-2022 | Eral | G | Fire extinguisher filling | New Project | Kathiresan | 19-09-2022 | - | Fire extinguisher filling done - Completed
CL2705 | 19-09-2022 | Cantonment | D | Batchen dispenser light replacing | Breakdown | Vigneshwaran | 19-09-2022 | - | 2 nos light replaced - Resolved
CL2706 | 20-09-2022 | Krishnagiri | C | Rule 18 and calibration work | Certification | Nepolean, vignesh & Prabu | 21-09-2022 | - | Rule 18 done - Calibration done - Completed
CL2707 | 20-09-2022 | Hosur | C | Rule 18 and calibration work | Certification | Nepolean, vignesh & Prabu | 21-09-2022 | - | Rule 18 done - Calibration done - Completed
CL2708 | 20-09-2022 | Nasiyanur | R | Electrical work | New Project | Thirumalaisamy | 20-09-2022 | - | Electrical work partially completed - Attended
CL2709 | 20-09-2022 | T.V.Kovil | A | Automation Maintenance | Preventive | Madhavan | 20-09-2022 | - | Maintenance done - Outlet back online - Completed
CL2710 | 20-09-2022 | Namakkal 3 | C | PESO Inspection | Certification | Chandrasekar, Pandi durai, Prakash, Venkatesh | 21-09-2022 | - | PESO inspection completed - Attended
CL2711 | 20-09-2022 | Tiruchengode | C | PESO Inspection | Certification | Chandrasekar, Pandi durai, Prakash, Venkatesh | 21-09-2022 | - | PESO inspection completed - Attended
CL2712 | 21-09-2022 | Cantonment | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 21-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2713 | 21-09-2022 | Ariyamangalam | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 21-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2714 | 21-09-2022 | T.V.Kovil | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 21-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2715 | 21-09-2022 | Dharmapuri | C | Rule 18 | Certification | Nepolean, vignesh & Prabu | 21-09-2022 | - | Rule 18 done - Completed
CL2716 | 21-09-2022 | Tharamangalam | C | Rule 18 | Certification | Nepolean, vignesh & Prabu | 21-09-2022 | - | Rule 18 done - Completed
CL2717 | 22-09-2022 | Dharapuram | D | Display damaged | Breakdown | Gowtham | 23-09-2022 | - | New display replaced & PRV installed - Resolved
CL2718 | 22-09-2022 | Villapuram | D | C and D side Dispenser slow delivery | Breakdown | Kathiresan | 22-09-2022 | 20 Mins | Dispenser filter and excess flow valve cleaned - refitted - Slow delivery arrested - Testing : 5 Ltrs - Rectified
CL2719 | 22-09-2022 | Velacherry | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 22-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2720 | 22-09-2022 | Vadivelan nagar | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 22-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2721 | 22-09-2022 | Virudhunagar | A | Automation going offline due to CPU not working | Breakdown | Madhavan | 2022-09-27 | - | New CPU replaced - Working fine - Resolved
CL2722 | 22-09-2022 | Salem | C | Rule 18 | Certification | Nepolean, Vignesh & Prabu | 22-09-2022 | - | Rule 18 done - Completed
CL2723 | 22-09-2022 | Uthamacholapuram | C | Rule 18 | Certification | Nepolean, vignesh & Prabu | 22-09-2022 | - | Rule 18 done - Completed
CL2724 | 23-09-2022 | Erode | C | Rule 18 | Certification | Nepolean, vignesh & Thirumalaisamy | 23-09-2022 | - | Rule 18 done - Completed
CL2725 | 23-09-2022 | Namakkal 2 | G | Unloading training | Preventive | Prabu | 23-09-2022 | - | Unloading training provided - Attended
CL2726 | 23-09-2022 | Sankari | C | Rule 18 | Certification | Nepolean, vignesh & Prabu | 23-09-2022 | - | Rule 18 done - Completed
CL2727 | 23-09-2022 | Bhavani | C | Rule 18 | Certification | Nepolean, vignesh & Prabu | 23-09-2022 | - | Rule 18 done - Completed
CL2728 | 24-09-2022 | Avadi | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2729 | 24-09-2022 | Kattupakkam | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2730 | 24-09-2022 | Hosur | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Prabu | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2731 | 24-09-2022 | Krishnagiri | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Prabu | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2732 | 24-09-2022 | Dharmapuri | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Prabu | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2733 | 24-09-2022 | Uthamacholapuram | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Prabu | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2734 | 24-09-2022 | Tharamangalam | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Prabu | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2735 | 24-09-2022 | Villapuram | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kathiresan | 24-09-2022 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2736 | 2022-09-24 | Perundurai | C | Rule 18 | Certification | Nepolean | 24-09-2022 | - | Rule 18 done - Completed
CL2737 | 2022-09-24 | Kodumudi | C | Rule 18 | Certification | Nepolean | 24-09-2022 | - | Rule 18 done - Completed
CL2738 | 2022-09-25 | Namakkal 3 | G | Commissioning work | New Project | Prabu, Dharmesh, Chandrasekar & Prakash | 2022-09-25 | - | Commissioning done - Decanding and Dispensing pump &motor, Dispenser, Atg, and Rochester all working good - Dispensing with Automation working fine - Completed
CL2739 | 2022-09-25 | Velachery | G | Pneumatic pipe damaged | Breakdown | Suneel Sagar | 2022-09-25 | - | Pneumatic pipes and connectors replaced by new - Kalvacha spare relay board changed - Kept under observation - Rectified
CL2740 | 2022-09-25 | Ellis Nagar | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kathiresan | 2022-09-25 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2741 | 2022-09-26 | Devakottai | G | Electical work | New Project | Nivas & Pandi Durai | 2022-09-26 | - | Granite work done - Electrical and yard installation in process - Attended
CL2742 | 2022-09-26 | Avadi | T | Dispensing line rov stem leakage | Breakdown | Suneel Sagar | 2022-09-26 | - | Leakage arrested by tightening the nut - Rectified
CL2743 | 2022-09-26 | Namakkal 3 | C | Stamping work | Certification | Prabu | 2022-09-26 | - | Stamping work done Calibration K factors A side 10000 B side 10000 MF reading A side 10.01 B side 10.03 Total testing 605.40lit - Completed
CL2744 | 2022-09-26 | Aravakurichi | C | Stamping and calibration work | Certification | Thirumalaisamy | 2022-09-26 | - | Calibration and stamping work done Calibration report: 'A' side 10 ltrs = 9.95 'B' side 10 ltrs = 9.96 "K" factor report: "A" side 'K'=10100 "B" side 'K' =10100 Total testing=292.42litters - Completed Camera not working - In process - Camera back online on 23.12.2022 - Resolved
CL2745 | 2022-09-26 | Kangeyam | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Gowtham | 2022-09-26 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2746 | 2022-09-26 | Dharapuram | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Gowtham | 2022-09-26 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2747 | 2022-09-26 | Palladam 1 | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Gowtham | 2022-09-26 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2748 | 2022-09-26 | Palladam 2 | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Gowtham | 2022-09-26 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2749 | 2022-09-27 | Tiruchengode | T | Commissioning and Automation work | New Project | Dharmesh, Pandi durai, Prabu & Chandrasekar | 2022-09-29 | - | All equipment commissioned - Automation installation done - Completed
CL2750 | 2022-09-27 | Udumalpet | D | Dispenser B side breakaway coupling LPG leakage | Breakdown | Gowtham | 2022-09-27 | - | Breakaway leakage arrested - Testing : 10.72 Ltrs - Rectified
CL2751 | 2022-09-27 | Erode | G | Fire extinguisher srevice and training | Preventive | Thirumalaisamy | 2022-09-27 | - | Fire extinguisher service and training done - Completed
CL2752 | 2022-09-27 | Dindigul | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kamaraj | 2022-09-27 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2753 | 2022-09-27 | Perundurai | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Thirumalaisamy | 2022-09-27 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2754 | 2022-09-27 | Dharapuram | G | Camera not working | Breakdown | Gowtham | 2022-09-27 | - | Camera repaired - Accessible from HO - Resolved
CL2755 | 2022-09-27 | Kodungaiyur | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 2022-09-27 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2756 | 2022-09-28 | Namakkal 3 | G | Outlet inauguration | New Project | Prakash | 2022-09-28 | - | Outlet opened to public - Opening reading A side 362.28 B side 495.57 Tank 75% - Completed
CL2757 | 2022-09-28 | Namakkal 3 | A | Automation installation | New Project | Madhavan | 2022-09-29 | - | Automation installed and data available in KR admin app - Completed
CL2758 | 2022-09-28 | Palayam | T | Air hose and Rov leakage | Breakdown | Thirumalaisamy | 2022-09-28 | - | Tank to eb room air hose changed - Rov leakage arrested by tightening the secrew - Rectified
CL2759 | 2022-09-28 | Tiruchengode | T | Commisioning work | New Project | Prakash, Venkatesh, Prabu, Chandrasekar, Dharmesh | 2022-09-29 | - | Commisioning done - Dispensing motor decanting motor atg rochester woring fine - Completed
CL2760 | 2022-09-29 | Viruthunagar | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kathiresan | 2022-09-29 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2761 | 2022-09-30 | Erode | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Thirumalaisamy | 2022-09-30 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2762 | 2022-09-30 | Kodumudi | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Thirumalaisamy | 2022-09-30 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2763 | 2022-09-30 | Aravakurichi | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Thirumalaisamy | 2022-09-30 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2764 | 2022-09-30 | Palayam | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Thirumalaisamy | 2022-09-30 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2765 | 2022-09-30 | Uthamacholapuram | T | Dispensing motor noise | Breakdown | Prabu | 2022-09-30 | - | Dispensing motor noise resolved - Motor and pump reassembled grease applied - Working fine - Resolved
CL2766 | 2022-09-30 | Ellis Nagar | T | Rov leakage and Oil dispenser measurement checked | Breakdown | Kathiresan | 2022-09-30 | - | Ballvalve with rov leakage arrested by tightened the screw - Oil dispenser measurement checking done Oil testing 1 ltrs - Resolved
CL2767 | 2022-09-30 | Velachery | R | Dispensing motor contactor issue | Breakdown | Suneel Sagar | 2022-09-30 | - | Dispensing motor contractor issue resolved by reset the contactor. Measured motor current 7A found satisfactory - Rectified
CL2768 | 2022-09-30 | T.V.Kovil | T | Dol starter contactor and relay issue | Breakdown | Vigneshwaran | 2022-09-30 | - | Dol starter contactor and relay issue resolved by changing the contator and relay - Rectified
CL2769 | 2022-10-01 | Tiruchengode | G | Outlet inauguration | New Project | Chandrasekar, Prasanna narasimman, Navaneetha krishnan, Dharmesh | 2022-09-28 | - | Outlet opened to public - Completed
CL2770 | 2022-10-01 | Tiruchengode | G | Stamping and calibration work | Certification | Prabu | 2022-09-01 | - | Calibration and stamping work done Opening reading : A side 1167.39 B side 392.60 Opening Tank 76%. Calibration report: A side 10.01 B side 10.02 K factors A side 10000 B side 10000 - Completed
CL2771 | 2022-10-02 | Tiruchengode | A | Automation installation | New Project | Madhavan | 2022-10-02 | - | Automation installed and data available in KR admin app - Completed
CL2772 | 2022-10-02 | Chengalpattu | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Suneel Sagar | 2022-10-02 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2773 | 2022-10-02 | Madurai | D | Nozzle leakage | Breakdown | Kathiresan | 2022-10-02 | - | B side nozzle leakage arrested by changing the front O ring and teeth 4 nos - Resolved
CL2774 | 2022-10-03 | Musiri | T | ATG offset checking | Preventive | Vigneshwaran | 2022-10-03 | - | Rochester gauge checked and ATG offset changed - Rectified
CL2775 | 2022-10-03 | Paramathivelur | T | Ball valve with rov leakage, Nozzle leakage, Online ups battery issue | Breakdown | Thirumalaisamy | 2022-10-03 | - | Ball valve with ROV lpg leakage arrested by tightening a screw - Nozzle lpg leakage arrested by changing a O ring - PMR done - Online ups battery issue complaint registered - Completed
CL2776 | 2022-10-03 | Ariyamangalam | D | Nozzle teeth problem | Breakdown | Nepolean | 2022-10-03 | - | C and D side nozzle teeth replaced - Resolved
CL2777 | 2022-10-03 | Tiruchengode | G | Pump staff training | New Project | Prabu | 2022-10-03 | - | Staff training provided - Done
CL2778 | 2022-10-04 | Avinashi | T | Product automatically transfers from Tank 2 to Tank 1 | Breakdown | Gowtham | 2022-10-04 | - | Both tank dispensing and vapour line ROV interchanged - Dispensing liquid ballvalve serviced and refitted - Dispensing motor spider replaced - Kept under observation - Resolved
CL2779 | 2022-10-05 | Eral | G | Site visit | New Project | Kathiresan | 2022-10-05 | - | Paver and civil work almost done - Site measurement checked - Site visit done - Completed
CL2780 | 2022-10-06 | T.V.Kovil | D | D nozzle teeth problem | Breakdown | Vigneshwaran | 2022-10-06 | - | D nozzle teeth 4 nos replaced - Batchen dispenser A and B side nozzle front O ring replaced - Rectified
CL2781 | 2022-10-06 | Kattupakkam | R | Signal interference in VFD | Breakdown | Suneel Sagar | 2022-10-12 | - | Complaint logged at vendor - Pressure gauge replaced in unloading pump - ATG consule position shifted to rectify VFD interference - ATG working fine - Kept under observation - Resolved
CL2782 | 2022-10-07 | Virudhunagar | D | B nozzle not working properly | Breakdown | Kathiresan | 2022-10-07 | - | Spare OPW nozzle replaced - Unloading point 50 NB ball valve leakage arrested by tightening the nut - Resolved
CL2783 | 2022-10-07 | Mulanur | R | Control panel not working | Breakdown | Thirumalaisamy | 2022-10-08 | 3.15 Hours | Surge arrester replaced with new one - Tank 2 VSC contactor replaced - Working fine - Eb supply voltage RY-401V YB-401V BR-400V - Found satisfactory - Dispensing motor lovejoy coupling - Dispenser retraction rope replaced at both sides - Rectified
CL2784 | 2022-10-08 | Ammapet | T | Site marking | New Project | Prabu | 2022-10-08 | - | Tank area, Dispensing and unloading motor, Dispenser and trench marking done - Completed
CL2785 | 2022-10-08 | Namakkal 3 | R | VFD installation | Preventive | Chandrasekar & Nivas | 2022-10-09 | - | VFD installation completed - Working fine - Kept under observation for a day and it is satisfactory - Completed
CL2786 | 2022-10-08 | Ellis Nagar | G | Oil dispenser calibration | Preventive | Kathiresan | 2022-10-08 | - | Oil dispenser calibration done - Testing : 1.90 Ltrs - Resolved
CL2787 | 2022-10-08 | Tharamangalam | R | Changeover DG mode not working due to phase lines loose contact | Breakdown | Prabu | 2022-10-08 | - | Changeover phase lines reconnected - DG Battery and UPS Battery distilled water level topped-up - Rectified
CL2788 | 2022-10-09 | Kattupakkam | D | Point jumping | Breakdown | Suneel Sagar | 2022-10-09 | - | D side bypass valve adjusted and excess flow valve cleaned - Resolved
CL2789 | 2022-10-09 | Velachery | G | Fire extinguisher refilling and operation training | Preventive | Suneel Sagar | 2022-10-09 | - | Fire extinguisher refilling and training done - Completed
CL2790 | 2022-10-09 | Vadivelan nagar | G | Fire extinguisher refilling and operation training | Preventive | Suneel Sagar | 2022-10-09 | - | Fire extinguisher refilling and training done - Completed
CL2791 | 2022-10-09 | Velachery | D | C and D nozzle preset mode not working due to mother board not working properly | Breakdown | Suneel Sagar,Vigneshwaran and Dharmesh | 2022-10-13 | 3.12 Hours | New motherboard replaced - Working fine - Calibration done - Calibration report: "A " side 10 ltr = 10.12 "B " side 10 ltr = 10.05 "C " side 10 ltr = 10.10 "D " side 10 ltr = 10.11 Total Testing liters - 1438.82 - Rectified
CL2792 | 2022-10-09 | Thanjavur | C | Calibration work | Certification | Nepolean and Vignesh | 2022-10-09 | - | Stamping done - K factor : A & B : 10000 A side : 10 lit - 9.97 lit B side : 10 lit - 10.03 lit - Total testing: 206.84 lit - Completed
CL2793 | 2022-10-10 | Paramathivelur | T | Unloading liquid ballvalve not working | Breakdown | Thirumalaisamy | 2022-10-10 | - | Ballvalve stem jam released - Working fine - A nozzle hammer teeth replaced - Decanting pneumatic hose replaced due to leakage - Resolved
CL2794 | 2022-10-10 | Chengalpattu | G | Fire extinguisher refilling and operation training | Preventive | Suneel Sagar | 2022-10-10 | - | Fire extinguisher refilling and training done - Completed
CL2795 | 2022-10-10 | Thiruvaiyaru | D | Dispenser bottom liquid line ballvalve LPG leakage | Breakdown | Nepolean | 2022-10-10 | - | Leakage arrested by tightening the nut - Rectified
CL2796 | 2022-10-11 | Tiruchengode | G | Unloading training and pipeline leakage test | Preventive | Prabu | 2022-10-11 | - | Unloading training provided - Pipeline leakage test done - Completed
CL2797 | 2022-10-11 | Ariyamangalam | D | Nozzle testing | Preventive | Nepolean | 2022-10-11 | - | Virudhunagar nozzle tested on D side - Testing : 1.57 Ltrs - Completed
CL2798 | 2022-10-11 | T.V.Kovil | D | B nozzle not working properly | Breakdown | Avinash | 2022-10-11 | - | Nozzle teeth 4 nos replaced - Working fine - Rectified
CL2799 | 2022-10-12 | Tenkasi | T | Tank installation and foundation concrete work | New Project | Kathiresan | 2022-10-12 | - | Tank installation and concrete work completed - Attended
CL2800 | 2022-10-12 | Theni | D | Batchen dispenser B side metering unit leakage | Breakdown | Kamaraj | 2022-10-13 | - | Metering unit bearing and oil seal kit replaced by new - Leakage arrested - Working fine - Rectified
CL2801 | 2022-10-12 | Eral | G | Commissioning work | New Project | Prakash, Chandrasekar, Kathiresan & Avinash | 2022-10-14 | - | Commissioning done - Decanding and Dispensing pump & motor, Dispenser, Atg, and Rochester all working good - Dispensing stamping done - Completed
CL2802 | 2022-10-12 | Vellakovil | D | A nozzle keypad not working | Breakdown | Thirumalaisamy | 2022-10-13 | - | Keypad replaced with new one - Working fine - Resolved
CL2803 | 2022-10-12 | Mulanur | R | Outlet went offline due to automation extension box fuse damaged | Breakdown | Thirumalaisamy | 2022-10-12 | - | Extension box fuse replaced - On/Off switch serviced - Outlet back online - Resolved
CL2804 | 2022-10-13 | Neelambur | D | Dispenser error E00 occurred | Breakdown | Gowtham | 2022-10-13 | - | Input voltage checked - Loose contacts checked - UPS restarted - PMR done - Resolved
CL2805 | 2022-10-14 | Uthamasolapuram | C | Stamping work | Certification | Nepolean & Dharmesh | 2022-10-14 | - | D.L stamping work done . A side Old k factor: 10100 B side Old k factor: 10100 A new k factor: 10010 B. New k factor: 10030 A side 10 lit - 10.05 lit B side 10 lit - 10.00 lit A side testing: 232.41 B side testing: 268.25 - Completed
CL2806 | 2022-10-14 | Ariyamangalam | D | B nozzle not working properly | Breakdown | Pandi Durai | 2022-10-14 | - | Nozzle teeth 4 nos replaced - Working fine - Resolved
CL2807 | 2022-10-14 | Ariyalur | G | Fire extinguisher servicing | Preventive | Pandi Durai | 2022-10-14 | - | Fire extinguisher servicing completed - Attended
CL2808 | 2022-10-14 | Kattupakkam | T | ATG output relay is not working | Breakdown | Suneel Sagar | 2022-11-16 | - | Output relay changed - Both tank levels showing - Rectified
CL2809 | 2022-10-14 | Ayothiyapattinam | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-14 | - | Rule 18 done - Completed
CL2810 | 2022-10-15 | Eral | G | Outlet inauguration | New Project | Prakash, Chandrasekar, Kathiresan & Avinash | 2022-10-15 | - | Outlet opened to public - Inaugurated - Completed
CL2811 | 2022-10-15 | Eral | A | Automation installation | New Project | Madhavan | 2022-10-15 | - | Automation installed and data available online in KR admin application - Completed
CL2812 | 2022-10-15 | Theni | A | Outlet going offline due to automation converter board communication disturbance | Breakdown | Kamaraj | 2022-10-15 | - | Network cable reconnected - Working fine - Outlet back online - Rectified
CL2813 | 2022-10-15 | Ellis Nagar | T | Dispensing motor makes noise due to damage in lovjoy coupling joint gear teeth | Breakdown | Kathiresan, Prakash, Vignesh and Chandrasekar | 2022-10-19 | - | Motor and pump alignment done - Teflon gear coupling replaced - Noise arrested - Working fine - Resolved
CL2814 | 2022-10-15 | Kattupakkam | T | Frequent failure of pressure gauge | Breakdown | Suneel Sagar | 2022-10-15 | - | Dispenser pump assembly and piping realigned by Corken Engineer - Dispensing pump sound and vibration is satisfactory - Resolved
CL2815 | 2022-10-16 | Attur | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-16 | - | Rule 18 done - Completed
CL2816 | 2022-10-16 | Rasipuram | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-16 | - | Rule 18 done - Completed
CL2817 | 2022-10-16 | Paramathivelur | C | Rule 18 work | Certification | Thirumalaisamy, Nepolean & Dharmesh | 2022-10-16 | - | Rule 18 done - Completed
CL2818 | 2022-10-16 | Namakkal 1 | C | Rule 18 work | Certification | Prabu, Nepolean & Dharmesh | 2022-10-16 | - | Rule 18, PMR and Earth generation work done - Completed
CL2819 | 2022-10-16 | Namakkal 2 | C | Rule 18 work | Certification | Prabu, Nepolean & Dharmesh | 2022-10-16 | - | Rule 18, PMR and Earth generation work done - Completed
CL2820 | 2022-10-17 | Cantonment | R | Compressor oil changing | Preventive | Chandrasekar | 2022-10-17 | - | Compressor oil changed - Resolved
CL2821 | 2022-10-17 | Tharamangalam | D | Dispenser motherboard hang - Error 21 occurred due to mishandling of manpower | Breakdown | Prabu | 2022-10-18 | - | Mother board cables reconnected - Working fine - Testing : A side: 8.63 Ltrs B side : 1.17 Ltrs Total : 9.80 ltrs - Rectifed
CL2822 | 2022-10-17 | Karur | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-17 | - | Rule 18 done - Completed
CL2823 | 2022-10-17 | Aravakurichi | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-17 | - | Rule 18 done - Completed
CL2824 | 2022-10-18 | Palayam | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-18 | - | Rule 18 done - Completed
CL2825 | 2022-10-18 | Manapparai | C | Rule 18 work | Certification | Nepolean & Dharmesh | 2022-10-18 | - | Rule 18 done - Completed
CL2826 | 2022-10-18 | T.V.Kovil | D | Batchen dispenser A nozzle leakage | Breakdown | Vigneshwaran | 2022-10-18 | - | Spare nozzle replaced - Testing : 1.2 Ltrs - Rectified
CL2827 | 2022-10-18 | Namakkal 3 | D | Dispenser slow delivery problem | Breakdown | Prabu | 2022-10-18 | - | Dispenser pipeline equalizer ballvalve and bypass valve adjusted - Working fine - Resolved
CL2828 | 2022-10-19 | Kodumudi | R | Dispenser w1 contactor not working | Breakdown | Thirumalaisamy | 2022-10-19 | - | Tank 2 contactor interchanged - Working fine - Safety training provided to pump staffs - Rectified
CL2829 | 2022-10-20 | Pudukkottai | C | Stamping work and nozzle teeth problem | Certification | Nepolean & Dharmesh | 2022-10-20 | - | DL Stamping work done - K factor A side : 10190 B side :. 10190 A side 10 lit - 9.98 lit B side 10 lit - 9.96 lit Total testing : 352.14 lit Nozzle teeth 4 nos replaced - Control panel RYB indicator changed - Completed
CL2830 | 2022-10-20 | Udumalpet | G | Fire extinguisher refilling | Preventive | Gowtham | 2022-10-20 | - | BC type fire extinguisher replaced by 2 nos of ABC type fire extinguishers - General service done - Completed
CL2831 | 2022-10-20 | Cantonment | G | Dispenser tube light not working | Breakdown | Chandrasekar | 2022-10-20 | - | Tube light newly replaced - Resolved
CL2832 | 2022-10-21 | Sulur | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2022-10-20 | - | BC type fire extinguisher replaced by 2 nos of ABC type fire extinguishers - New CO2 fire extinguisher supplied - General service done - Completed
CL2833 | 2022-10-21 | Saravanampatty | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2022-10-20 | - | BC type fire extinguisher replaced by 2 nos of ABC type fire extinguishers - General service done - New CO2 fire extinguisher supplied - Completed
CL2834 | 2022-10-21 | Mettupalayam | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2022-10-20 | - | 9kg and 75 kg fire extinguishers serviced - New CO2 fire extinguisher supplied - Found satisfactory - Completed
CL2835 | 2022-10-21 | Tenkasi | T | Tank hydro test | New Project | Kathiresan | 2022-10-21 | - | Tank hydro test done - Pressure holded at 28 kg/cm^2 - CP installation done - Dispensing and decanting motor marking done CP reading : R1 to C1 = -0.588 R1 to C2 = -0.545 R1 to A1 = -1.212 R1 to A2 = -1.320 R1 to A3 = -1.255 R1 to A4 = -1.342 After looping = - 1.32- Rectified
CL2836 | 2022-10-21 | Vadivelan nagar | D | B and D side nozzle not working properly | Breakdown | Suneel Sagar | 2022-10-21 | - | Nozzle teeth replaced for both sides - Working fine - Resolved
CL2837 | 2022-10-22 | Tiruchengode | G | 75 kg fire extinguisher Co2 leakage | Breakdown | Prabu | 2022-10-22 | - | Co2 cylinder replaced - . Unloading and fire extinguisher operation training provided - ATG cut off working checked - Completed
CL2838 | 2022-10-22 | Virudhunagar | T | Dispensing air hose damaged | Breakdown | Kathiresan | 2022-10-22 | - | Pneumatic hose replaced about 30 mtrs - Working fine - Resolved
CL2839 | 2022-10-23 | Theni | A | Outlet going offline due to dispenser communication disturbed | Breakdown | Kamaraj | 2022-10-24 | - | Network cable reconnected - Working fine - Outlet back online - Rectified
CL2840 | 2022-10-24 | Ariyamangalam | D | Dispenser nozzle LPG leakage | Breakdown | Nepolean | 2022-10-24 | - | Nozzle teeth 4 nos replaced at A side - Working fine - Rectified
CL2841 | 2022-10-26 | Avinashi | T | Tank 1 dispensing air hose damaged | Breakdown | Gowtham | 2022-10-26 | - | Partially replaced with new pneumatic hose - Working fine - Resovled
CL2842 | 2022-10-26 | T.V.Kovil | G | Genset maintenance | Preventive | Dharmesh | 2022-10-26 | - | Generator engine oil, fuel filter, strainer fuel filter changed - Air filter cleaned - Working good - Completed
CL2843 | 2022-10-26 | T.V.Kovil | D | Batchen dispenser A side on/ off switch problem | Breakdown | Nepolean | 2022-10-26 | - | A side on / off switch replaced - C side keypad replaced - Working fine - Resolved
CL2844 | 2022-10-26 | Cantonment | G | Fire extinguisher service and training | Preventive | Chandrasekar | 2022-10-26 | - | 75 kg fire extinguisher Co2 changed - Training provided - Attended
CL2845 | 2022-10-27 | Ellis Nagar | D | A nozzle not working properly | Breakdown | Kathiresan | 2022-10-27 | - | Nozzle teeth 4 nos and front O ring replaced - Working fine - Resolved
CL2846 | 2022-10-28 | T.V.Kovil | D | Batchen dispenser B side solenoid coil not opening | Breakdown | Vigneshwaran | 2022-10-28 | - | B side high flow and low flow coil cleaned - Testing : 25.74 Ltrs - Rectified
CL2847 | 2022-10-29 | Ariyamangalam | D | B nozzle not working properly | Breakdown | Nepolean | 2022-10-29 | - | Service nozzle replaced - Testing : 1.13 Ltrs - Working fine - Completed
CL2848 | 2022-10-30 | Rasipuram | G | DG battery to self motor wire and leg broken | Breakdown | Prabu | 2022-10-30 | - | DG battery to self motor wire and leg changed - Working fine - Rectified
CL2849 | 2022-10-30 | Namakkal 3 | R | Control panel not working in DG mode | Breakdown | Prabu | 2022-10-30 | - | Control panel transformer input voltage adjusted - Working in DG mode - Resolved
CL2850 | 2022-10-31 | Velachery | R | Dispenser MCB problem | Breakdown | Suneel Sagar | 2022-10-31 | - | 10A single pole dispenser MCB - 2 nos replaced by new - Resolved
CL2851 | 2022-11-01 | Nasiyanur | T | Tank N2 testing | New Project | Chandrasekar, Thirumalaisamy and Nivas | 2022-11-03 | - | Nitrogen testing completed - Testing pressure 14.5 kg/cm2, holding pressure 10 kg/cm² - Electrical and mechanical work done - Control panel booted - Completed
CL2852 | 2022-11-01 | Palladam 2 | A | Automation converter board damaged and dispenser both side keypad is not working | Breakdown | Gowtham | 2022-11-01 | 10 Hours | Spare keypad changed in one side - Converter board and another keypad replaced - Outlet back online - Testing : 34.36 Ltrs - Partially Rectified
CL2853 | 2022-11-01 | T.V.Kovil | A | Dispenser running without mobile billing due to mobile API software issue | Breakdown | Madhavan | 2022-11-01 | - | Software updated - Mobile billing back online - Resolved
CL2854 | 2022-11-02 | Tenkasi | T | Excess flow valve fitting and Hydro test | New Project | Kathiresan | 2022-11-02 | - | EFV and flanges fitting done - Hydro test done - Dispenser marking done - Rule 33 data collected - Found satisfactory - Completed
CL2855 | 2022-11-02 | Vedachandur | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kamaraj | 2022-11-02 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2856 | 2022-11-02 | Bodi | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kamaraj | 2022-11-02 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2857 | 2022-11-02 | Uthamapalayam | G | ALDS general inspection, Safety audit, Electrical audit | Preventive | Kamaraj | 2022-11-02 | - | ALDS general inspection, Safety audit, Electrical audit - Completed
CL2858 | 2022-11-03 | Velachery | T | Fill point indicator junction box O ring problem | Breakdown | Suneel Sagar | 2022-11-03 | - | Fill point indicator junction box O ring replaced to stop moisture entry - Indicator is working and showing ATG tank levels - Resolved
CL2859 | 2022-11-04 | Manapparai | R | Online UPS not working | Breakdown | Nivas | 2022-11-04 | - | New batteries replaced - Working fine - A and B nozzle leakage arrested by replacing 8 nos of nozzle teeth - Rectified
CL2860 | 2022-11-05 | Nasiyanur | G | Fire extinguisher filling | Preventive | Thirumalaisamy | 2022-11-05 | - | Fire extinguisher powder filled - Genset eatthing done - Attended
CL2861 | 2022-11-05 | Thuraiyur | R | Dispenser to EB room air hose damaged | Breakdown | Dharmesh | 2022-11-05 | - | Pneumatic hose replaced in both main and spare line - FRL replaced with new - Working fine - Resolved
CL2862 | 2022-11-05 | Avadi | D | C side keypad not working properly | Breakdown | Suneel Sagar | 2022-11-05 | - | Keypad replaced with new one - Working fine - Resolved
CL2863 | 2022-11-05 | Dharmapuri | G | Fire extinguisher servicing | Preventive | Prabu | 2022-11-05 | - | 9 kg fire extinguisher and fire ball replaced - Attended
CL2864 | 2022-11-05 | Kodungaiyur | R | ATG Battery to be changed | Breakdown | Suneel Sagar | 2022-11-05 | - | ATG battery replaced and reconfigured - ATG working fine - Rectified
CL2865 | 2022-11-05 | Tenkasi | T | Tank area welding work | New Project | Kathiresan | 2022-11-05 | - | Welding work done - Dispenser installed - 4 Earth installation done - Completed
CL2866 | 2022-11-05 | Kodumudi | T | Unloading vapour hose adapter damaged | Breakdown | Thirumalaisamy | 2022-11-05 | - | Hose brass adapter replaced with new - Working fine - Resolved
CL2867 | 2022-11-05 | Uthamapalayam | G | Fire extinguisher servicing | Preventive | Prabu | 2022-11-05 | - | 9 kg fire extinguisher and fire ball replaced - Attended
CL2868 | 2022-11-06 | Paramathivelur | G | Fire extinguisher servicing | Preventive | Thirumalaisamy | 2022-11-06 | - | 9 kg fire extinguishers replaced - Fire fighting training and unloading training provided - Attended
CL2869 | 2022-11-06 | Ellis Nagar | T | Tank area leakage | Preventive | Kathiresan | 2022-11-06 | - | Tank area complete leakage test done - Unloading point 50NB ballvalve stem LPG leakage arrested by tightening the bolt nut - PMR done - Working fine - Rectified
CL2870 | 2022-11-07 | Ariyalur | C | Rule 18 work | Certification | Chandrasekar and Vignesh | 2022-11-07 | - | Rule 18 done - PMR and master data collected - Completed
CL2871 | 2022-11-07 | Villapuram | C | Calibration work | Certification | Kathiresan and Avinash | 2022-11-08 | - | Calibration done Calibration reports: "A" side 10 ltrs = 9.97 "B" side 10 ltrs = 9.97 "C" side 10 ltrs = 10.00 "D" side 10 ltrs = 9.96 "K" factor reports : "A" side Old 'K' = 10100 "A" side New 'K' =10150 "B" side Old ' K'= 10100 "C" side 'K' = 10400 "D" side Old 'K' = 10080 "D" side New 'K' = 10150 Total testing ltrs =931.91 - Completed
CL2872 | 2022-11-07 | Kodumudi | T | Unloading pneumatic hose damaged by rat | Breakdown | Thirumalaisamy | 2022-11-07 | - | Pneumatic hose connected by straight joint - Unloading vapour ROV LPG leakage arrested - Tank area LPG leakage tested - Resolved
CL2873 | 2022-11-07 | Perambalur | C | Rule 18 work | Certification | Chandrasekar and Vignesh | 2022-11-07 | - | Rule 18 done - PMR and master data collected - Completed
CL2874 | 2022-11-07 | Namakkal 3 | D | Dispenser slow delivery | Breakdown | Prabu | 2022-11-07 | - | Pipeline equalizer ballvalve adjusted - Testing : 35.58 Ltrs - Working fine - Rectified
CL2875 | 2022-11-08 | Ellis Nagar | C | Calibration work | Certification | Kathiresan and Avinash | 2022-11-08 | - | Calibration done Calibration reports: "A" side 10 ltrs = 9.98 "B" side 10 ltrs = 9.98 "C" side 10 ltrs = 9.99 "D" side 10 ltrs = 9.99 "K" factor reports : "A" side 'K' = 10000 "B" side ' K'= 10000 "C" side Old 'K'= 10000 "C" side New 'K' = 10050 "D" side Old 'K' = 10000 "D" side New 'K' =10050 Total testing ltrs =735.33 - Completed
CL2876 | 2022-11-08 | Musiri | C | Rule 18 work | Certification | Chandrasekar & Vignesh | 2022-11-08 | - | Rule 18 done - PMR and master data collected - Completed
CL2877 | 2022-11-08 | T.V.Kovil | D | B side metering unit LPG leakage, calibration work, B side new metering unit testing | Breakdown | Nepolean | 2022-11-09 | 5 Days | LPG leakage arrested by replacing O ring, Oil Seal and bearing - Working fine - Kept under observation - B side testing : 62.20 Ltrs - Calibration done on 10.11.2022 - B side testing : 421.47 Ltrs - B nozzle black O ring replaced - C nozzle teeth 4 nos replaced - New metering unit testing done on 11.11.2022 - A side testing: 19.41 lit B side testing: 226.53 lit - Metering unit working fine - Recalibration done - B side testing: 367.21 lit A side testing: 19.98 lit Total testing: 387.19 lit - Rectified
CL2878 | 2022-11-08 | Eral | C | Calibration work | New Project | Kathiresan | 2022-11-08 | - | Calibration done - Calibration reports: "A" side 10 ltrs = 9.98 "B" side 10 ltrs = 9.97 "K" factor reports : "A" side Old 'K' = 10000 "A" side New 'K' =10050 "B" side Old ' K'= 10000 "B" side New 'K'= 10050 Total testing ltrs =551.01 - Completed
CL2879 | 2022-11-09 | Velachery | C | PMR work | Preventive | Suneel Sagar | 2022-11-09 | - | PMR done - Completed
CL2880 | 2022-11-09 | Villapuram | D | A side on/off switch problem | Breakdown | Kathiresan | 2022-11-09 | - | New on/off switch and NO element changed - Rectified
CL2881 | 2022-11-09 | Tenkasi | T | Pipeline hydro test | New Project | Avinash | 2022-11-09 | - | Pipeline hydro test completed - Testing pressure : 48 Kg/Cm2 - Completed
CL2882 | 2022-11-10 | Rasipuram | G | Earth regeneration | Preventive | Prabu | 2022-11-10 | - | 3 new chemical earth connected - Attended
CL2883 | 2022-11-10 | Tenkasi | G | Welding work | New Project | Avinash | 2022-11-10 | - | Welding work done - Cable laying started - Completed
CL2884 | 2022-11-10 | Vadivelan nagar | C | PMR work | Preventive | Suneel Sagar | 2022-11-10 | - | PMR done - Completed
CL2885 | 2022-11-12 | Tenkasi | G | Electrical Work | New Project | Avinash | 2022-11-12 | - | Electrical work partially done - Attended
CL2886 | 2022-11-12 | Theni | D | Batchen dispenser error 23 occurred | Breakdown | Kamaraj | 2022-11-13 | 30 Minutes | Temperature wire reconnected - Error solved - Rectified
CL2887 | 2022-11-12 | Ariyamangalam | D | C and D side power card testing work | Preventive | Nepolean | 2022-11-12 | - | Power card testing done C side testing: 8.64 lit D side testing: 4.98 lit Total testing: 13.62 lit - Completed
CL2888 | 2022-11-13 | Velachery | R | 3 HP compressor | Breakdown | Suneel Sagar | 2022-11-13 | - | Compressors reconnected - Working fine - Rectified
CL2889 | 2022-11-15 | Udumalpet | T | Tank 1 above ground motor takes high ampere while running through genset power | Breakdown | Gowtham | 2022-11-15 | - | Soft starter installed - Found satisfactory - Completed
CL2890 | 2022-11-15 | Vadivelan nagar | A | C and D nozzle going offline to check dispenser keypad settings and nozzle switch | Breakdown | Madhavan | 2022-11-15 | - | Program fetching time adjusted by Arul Rayappan sir - Resolved
CL2891 | 2022-11-15 | Nasiyanur | G | Genset commissioning | New Project | Thirumalaisamy | 2022-11-15 | - | Genset commissioned by affinity without service person - Completed
CL2892 | 2022-11-15 | T.V.Kovil | D | D nozzle teeth problem | Breakdown | Vigneshwaran | 2022-11-15 | - | D side nozzle teeth replaced - Working fine - Resolved
CL2893 | 2022-11-15 | Namakkal 2 | R | 2 HP compressor oil drain nut damaged | Breakdown | Prabu | 2022-11-15 | - | Oil drain front door replaced - Oil changed for both compressors - Working fine - Rectified
CL2894 | 2022-11-15 | Namakkal 3 | R | N2 machine FRL unit installation | Preventive | Prabu | 2022-11-15 | - | FRL unit connected - Completed
CL2895 | 2022-11-16 | Tirunelveli | D | Error 99 occurred | Breakdown | Kathiresan | 2022-11-17 | - | Network communication board connected with offline UPS - Dispenser C and D parameter address changed - Rule 19 material requirement collected - Resolved
CL2896 | 2022-11-16 | Ayothiyapattinam | R | N2 machine FRL unit installation | Preventive | Prabu | 2022-11-16 | - | FRL unit connected - Tank area total leakage test done - Completed
CL2897 | 2022-11-16 | Cantonment | D | C nozzle teeth replacement for testing purpose | Breakdown | Chandrasekar | 2022-11-16 | - | Nozzle teeth replaced - Completed
CL2898 | 2022-11-16 | Ariyamangalam | A | Automation running without mobile due to local network issue for 20 mins | Breakdown | Nepolean | 2022-11-16 | - | BSNL service person attended and serviced - Resolved
CL2899 | 2022-11-16 | T.V.Kovil | D | Batchen dispenser door lock replacement | Breakdown | Vigneshwaran | 2022-11-16 | - | Dispenser door lock set replaced - N2 air machine damaged air hose replaced - Resolved
CL2900 | 2022-11-17 | Perambalur | R | Offline inverter UPS installation | Preventive | Chandrasekar and Avinash | 2022-11-17 | - | UPS installation done - Completed
CL2901 | 2022-11-17 | T.V.Kovil | D | C and D side keypads not working properly | Breakdown | Vigneshwaran | 2022-11-17 | - | New keypad replaced both sides - Working fine - Rectified
CL2902 | 2022-11-17 | Virudhunagar | D | B nozzle front O ring damaged | Breakdown | Kathiresan | 2022-11-17 | - | Front O ring changed - Rule 19 requirements collected - Fencing and compound damage visit done - Completed
CL2903 | 2022-11-17 | Sankari | T | ATG not working | Breakdown | Prabu | 2022-11-17 | - | ATG display batteries changed - Reprogramming and 85% cutoff set - Resolved
CL2904 | 2022-11-18 | Nasiyanur | C | PESO Inspection | Certification | Prakash | 2022-11-18 | - | PESO inspection completed - Attended
CL2905 | 2022-11-19 | Cantonment | D | D side nozzle teeth replacment for testing purpose | Preventive | Chandrasekar | 2022-11-19 | - | New teeth 4 nos replaced - Completed
CL2906 | 2022-11-19 | Chengalpattu | T | Unloading ROV leakage | Breakdown | Suneel Sagar | 2022-11-19 | - | ROV gland leakage arrested by tightening the nut - Leak test done - Rule 19 material reequirement list collected - Completed
CL2907 | 2022-11-19 | Nasiyanur | G | Commissioning and outlet inauguration | New Project | Prakash, Dharmesh, Avinash & Navaneethan | 2022-11-20 | - | Outlet opened to public - sales started. Opening reading A Nozzle-499.56 B Nozzle-304.95 Tank-55% - Completed
CL2908 | 2022-11-20 | Attur | R | Control panel booting problem and emergency switch broken | Breakdown | Prabu | 2022-11-20 | 30 Minutes | Emergency switch replaced - Control panel booted - Resolved
CL2909 | 2022-11-20 | Udumalpet | T | Tank 2 dispensing control relay not working properly | Breakdown | Gowtham | 2022-11-20 | - | Tank 2 relay interchanged - Working fine - Leakage arrested in unloading liquid hose brass adapters by refitting it - Rectified
CL2910 | 2022-11-20 | Nasiyanur | A | Automation installation | New Project | Madhavan | 2022-11-20 | - | Data available online in KR admin application - Completed
CL2911 | 2022-11-20 | Tirunelveli | D | Dispenser running in offline mode due to communication error testing purpose | Breakdown | Kathiresan | 2022-12-24 | - | New dispenser installed - Both dispensers back to online - Rectified
CL2912 | 2022-11-20 | Erode | C | Stamping and calibration work | Certification | Thirumalaisamy | 2022-11-20 | - | Calibration and stamping done - Calibration report: "A" side 10 ltrs = 9.97 "B" side 10 ltrs = 10.07 "K" factor report : "A" side Old 'K' = 10100 "A" side New 'K' =10100 "B" side Old ' K'= 10100 "B" side New 'K'= 10100 Total testing ltrs =309.82 ltrs - Completed
CL2913 | 2022-11-20 | Bhavani | C | Stamping and calibration work | Certification | Thirumalaisamy | 2022-11-20 | - | Calibration and stamping done - Calibration report: "A" side 10 ltrs = 9.97 "B" side 10 ltrs = 9.99 "K" factor report: "A" side Old 'K' = 10050 "A" side New 'K' =10050 "B" side Old ' K'= 10050 "B" side New 'K'= 10050 Total testing ltrs =424.43 ltrs - Completed
CL2914 | 2022-11-21 | Nasiyanur | C | Stamping and calibration work | Certification | Prabu | 2022-11-21 | - | Calibration and stamping done Calibration report: A side 10lit =9.99 B side 10lit =9.98 K factors report: A side 10000 B side 10000 Testing lit: A side 176.05 B side 175.74 Total testing 351.79 lit - Completed
CL2915 | 2022-11-21 | Ellis Nagar | A | Dispenser going offline due to system port address interchanged while booting | Breakdown | Kathiresan | 2022-11-21 | - | Port address of the system changed - Outlet back online - Working fine - Resolved
CL2916 | 2022-11-21 | T.V.Kovil | G | N2 machine Error E2 occurred | Breakdown | Vigneshwaran | 2022-11-21 | - | Sensors and solenoid valves cleaned - Working fine - Rectified
CL2917 | 2022-11-22 | Tirunelveli | G | Offline UPS battery problem | Breakdown | Kathiresan | 2022-11-22 | - | UPS battery replaced - Working fine - Resolved
CL2918 | 2022-11-22 | Karur | D | D nozzle keypad not working properly | Breakdown | Thirumalaisamy | 2022-11-22 | - | Keypad cable serviced and refitted - Working fine - Temporarily rectified
CL2919 | 2022-11-22 | Kodumudi | C | Stamping and calibration work | Certification | Dharmesh | 2022-11-22 | - | Calibration and stamping done A side 10lit =9.98 B side 10lit =9.99 K factors report: A side 10300 B side 10300 Testing lit: A side - 133.19 B side - 170.57 Total testing -303.76 lit Dispensing line ROV LPG leakage arrested by tightening the nut - Unloading solinoid coil cleaned - Wroking fine - Completed
CL2920 | 2022-11-22 | Ariyamangalam | T | Unloading vapour line ROV with ballvalve LPG leakage | Breakdown | Pandi Durai | 2022-11-22 | - | ROV with ballvalve LPG leakage arrested by tightening the nut and teflon applied - Tank area decanting line air hose and fittings replaced - Rectified
CL2921 | 2022-11-22 | Palayam | R | Control panel tripping | Breakdown | Thirumalaisamy | 2022-11-22 | - | M1 contactor wire loose connection adjusted - Working fine - Resolved
CL2922 | 2022-11-23 | Tenkasi | G | Site visit | New Project | Kathiresan | 2022-11-23 | - | EB, Genset and earth marking done - Paver work in process - Attended
CL2923 | 2022-11-23 | Rasipuram | R | Control panel dispensing solenoid air leakage | Breakdown | Prabu | 2022-11-23 | - | Dispensing solenoid coil replaced - Working fine - Resolved
CL2924 | 2022-11-23 | Virudhachalam | G | Fire extinguisher service and training | Preventive | Nivas | 2022-11-23 | - | Fire extinguisher service and training done - Completed
CL2925 | 2022-11-24 | Melur | A | Automation work and A side slow delivery | Breakdown | Kathiresan | 2022-11-24 | - | A side 3/4" excess flow valve cleaned - Tank area dispensing line ball valve LPG leakage arrested by tightening the nut and teflon applied - Printer installed near dispenser - PMR done - Rectified
CL2926 | 2022-11-24 | Nasiyanur | G | Site visit | New Project | Thirumalaisamy | 2022-11-24 | - | General inspection done - Overall leakage checked
CL2927 | 2022-11-24 | Ariyamangalam | D | Batchen D side Error 23 occurred | Breakdown | Nivas | 2022-11-24 | 30 Minutes | Cold boot done - Working fine - Resolved
CL2928 | 2022-11-25 | Uthamapalayam | C | Stamping and calibration work | Certification | Chandrasekar & Kamaraj | 2022-11-26 | - | Stamping and calibration done - Completed
CL2929 | 2022-11-25 | Avinashi | G | Site visit | Preventive | Gowtham | 2022-11-25 | - | General site visit completed - Found satisfactory - Attended
CL2930 | 2022-11-25 | Dharmapuri | T | Pressure not developed in dispensing motor | Breakdown | Prabu | 2022-11-25 | - | Bypass valve and equalizer ball valve adjusted - Pressure developed to 11 bar and working fine - Rectified
CL2931 | 2022-11-25 | Ellis Nagar | G | Oil dispenser air lock problem | Breakdown | Kathiresan | 2022-11-25 | - | Air lock removed by refitting the dispenser - Working fine - Oil testing : 1.50 Ltrs - Rectified
CL2932 | 2022-11-25 | Kattupakkam | R | ATG configuration | Breakdown | Suneel Sagar | 2022-11-25 | - | ATG reconfigured and relay working - Relay is working and cut off at 85% - Working fine - Resolved
CL2933 | 2022-11-25 | Avadi | T | Dispensing liquid ROV with ball valve gland leakage | Breakdown | Suneel Sagar | 2022-11-25 | - | ROV with ball valve gland leakage arrested by tightening and applying the teflon - Rectified
CL2934 | 2022-11-25 | Pudukkottai | T | Dispensing Vapor line ROV with ballvalve LPG leakage | Breakdown | Avinash | 2022-11-26 | - | ROV with ball valve LPG leakage arrested by tightening and applying the teflon - Tank area leakage tested - Rectified
CL2935 | 2022-11-26 | Nasiyanur | T | Unloading and unloading training | Preventive | Thirumalaisamy | 2022-11-26 | - | Unloading done - Training provided - ATG 83% cutoff checked - Working fine - Attended
CL2936 | 2022-11-26 | Theni | C | Stamping and calibration work | Certification | Chandrasekar & Kamaraj | 2022-11-26 | - | Stamping and calibration done - Completed
CL2937 | 2022-11-26 | Bodi | C | Stamping and calibration work | Certification | Chandrasekar & Kamaraj | 2022-11-26 | - | Stamping and calibration done - Completed
CL2938 | 2022-11-26 | Villapuram | G | Genset general service | Preventive | Kathiresan | 2022-11-26 | - | Diesel filter, oil filter, air filter and engine oil changed - Serviced completely - Working fine - Attended
CL2939 | 2022-11-27 | Kodumudi | T | Unloading process | Preventive | Thirumalaisamy | 2022-11-27 | - | Unloading completed - Training provided - Completed
CL2940 | 2022-11-27 | Dharapuram | D | B side keypad not working properly | Breakdown | Gowtham | 2022-11-27 | - | Keypad replaced with new one - PMR done - Working fine - Resolved
CL2941 | 2022-11-27 | Ayothiyapattinam | T | Unloading process | Preventive | Prabu | 2022-11-27 | - | Unloading completed - Training provided - Completed
CL2942 | 2022-11-28 | Ramnad | C | Stamping work | Certification | Kathiresan & Dharmesh | 2022-11-28 | - | Calibration and stamping done - Calibration report: A side 10 - 9.97 B side 10 - 9.96 'K' factor A side old K - 10000 B side old K - 10000 A side new K - 10030 B side new K - 10030 A side testing - 397.33 ltr B side testing - 440.75 ltr - ALDS compressor oil changed, tank area leakage tested - Resolved
CL2943 | 2022-11-28 | Velachery | R | Online UPS with isolation transformer installation | Preventive | Suneel Sagar | 2022-11-28 | - | Online UPS with isolation transformer installed - Completed
CL2944 | 2022-11-28 | Devakottai | G | Site visit | New Project | Nivas | 2022-11-28 | - | General site visit completed - Found satisfactory - Attended
CL2945 | 2022-11-29 | Palladam | G | Sales stopped due to PNG project | Breakdown | Gowtham | 2022-11-29 | 8 Hours | Civil work done - Sales started - Attended
CL2946 | 2022-11-29 | Tharamangalam | A | Dispenser going offline due to RS485 to USB converter cable damage | Breakdown | Prabu | 2022-11-29 | - | RS485 to USB converter cable reconnected - Automation back online - Resolved
CL2947 | 2022-11-30 | Tenkasi | C | Rule 33 third party inspection | Certification | Kathiresan | 2022-11-30 | - | Rule 33 third party inspection done - Attended
CL2948 | 2022-11-30 | Ariyamangalam | D | Dispenser bottom liquid line ROV air leakage | Breakdown | Nepolean | 2022-11-30 | - | 50E ROV replaced - Leakage arrested - Working good - Resolved
CL2949 | 2022-11-30 | Dindigul | R | Dispensing solenoid coil air leakage | Breakdown | Kamaraj | 2022-11-30 | - | Dispensing solenoid coil 1 no replaced - Working fine - Rectified
CL2950 | 2022-11-30 | Palakkad | C | FCRI mass flow meter calibration | Certification | Gowtham and Nivas | 2022-12-02 | - | Mass flow meter calibration done - Completed
CL2951 | 2022-12-01 | Sankari | R | Dispensing solenoid coil air leakage | Breakdown | Prabu | 2022-12-01 | - | New solenoid coil changed - Dispenser to control panel new air hose changed - Compressor oil changed - Attended
CL2952 | 2022-12-02 | Devakottai | A | Automation installation, Nitrogen testing and Electrical work | New Project | Chandrasekar and Dharmesh | 2022-12-04 | - | N2 testing done - Testing Pressure : 14.5 kg/cm2 - Holding pressure 10 kg/cm2 - Electrical work done - Pipeline painting work done - Completed
CL2953 | 2022-12-02 | Attur | R | Emergency switch problem | Breakdown | Prabu | 2022-12-02 | - | New emergency switch replaced - Resolved
CL2954 | 2022-12-02 | Velachery | D | Dispenser hanging while running both C and D side | Breakdown | Suneel Sagar | 2022-12-04 | C side - 24 Hours D side - 24 Hours | Running D side only to observe the complaint - C side hanging - Keypad and mother board to keypad cable replaced - C and D side working fine - Resolved
CL2955 | 2022-12-03 | Ammapet | G | Material unloading and Tank cleaning | New Project | Prabu | 2022-12-03 | - | Material unloading and tank cleaning done - Attended
CL2956 | 2022-12-03 | Udumalpet | C | Stamping and calibration work | Certification | Gowtham | 2022-12-03 | - | Calibration done A side- K fact- 101500 B side K fact- 101100 C side K fact- 10300 D side K fact- 10350 A side - 9.92/10.00 B side - 9.95/10.00 C side - 9.83/10.00 D side - 9.80/10.00 Testing litters: A side - 1066.76 ltr B side - 859.92 C side - 782.48 D side - 1120.00 Total - 3829.16 - Completed
CL2957 | 2022-12-05 | Virudhunagar | G | Compressor starter relay switch and oil replacing | Preventive | Kathiresan | 2022-12-05 | - | Compressor starter relay switch and oil changed - N2 machine SMPS power card capacitor changed - Working fine - Resolved
CL2958 | 2022-12-05 | Saravanampatty | R | Stabilizer power board failure | Breakdown | Gowtham | 2022-12-06 | - | Worked in bypass mode - New control board replaced - Panel working fine in both servo, EB and genset mode - Rectified
CL2959 | 2022-12-06 | Tenkasi | T | Tank N2 test | New Project | Kathiresan | 2022-12-06 | - | N2 testing done - Testing Pressure : 14.5 kg/cm2 - Holding pressure 10.5 kg/cm2 - Electrical work done - Genset commissioning done - Completed
CL2960 | 2022-12-06 | Virudhachalam | C | Stamping work | Certification | Nepolean and Vignesh | 2022-12-06 | - | Stamping done A side k factor : 10100 B side k factor :. 10200 A side testing : 150.09 lit B side testing. : 174.92 . A side 10 lit. 10.00 lit B side 10 lit : 10.04 lit Control panel damaged indicator replaced - Working fine - Completed
CL2961 | 2022-12-06 | Coimbatore | G | Visiting the yenen preset keypad and our control panel PLC programmer | New Project | Prakash, Suneel Sagar, Prasath, Gowtham and Arul Rayappan | 2022-12-06 | - | Visited to Dotkeys and Gilbergo for yenen dispenser keypad design and Aadhityaa for control panel signal wiring details - Completed
CL2962 | 2022-12-06 | Perambalur | G | Fire equipment refilling | Preventive | Avinash | 2022-12-06 | - | Fire extinguisher refilling work done - Training provided - Attended
CL2963 | 2022-12-07 | Udumalpet | D | Batchen dispenser B side breakaway coupling damaged | Breakdown | Gowtham | 2022-12-07 | - | New breakaway coupling replaced - Vapour line ROV replaced - Found Satisfactory - Resolved
CL2964 | 2022-12-07 | Manapparai | R | Online UPS battery problem | Breakdown | Nivas | 2022-12-07 | - | Online UPS battery new one replaced - Working good - Resolved
CL2965 | 2022-12-08 | Devakottai | R | Servo stabilizer R phase high voltage problem | Breakdown | Chandrasekar, Prasanna narasimman & Navaneetha krishnan | 2022-12-08 | - | Step up motor alignment adjusted - Control panel booted - Dispenser, dispensing motor and decanting motor working fine in both EB and Genset mode - Air compressor checked - Genset engine oil, oil filter and fuel filter replaced - Working fine - Completed
CL2966 | 2022-12-08 | Ammapet | T | Pipeline hydro test | New Project | Prabu | 2022-12-08 | - | Tank flanges liquid pipeline hydro test done - EFV and tank flanges fixed - Pipes and cable data collected - Completed
CL2967 | 2022-12-08 | Dindigul | C | Calibration work | Certification | Kamaraj & Vigneshwaran | 2022-12-08 | - | Calibration done A side- K fact- 09800 B side K fact- 09800 A side - 9.99/10.00 B side - 10.02/10.00 Testing litters: A side - 131.70 lit B side - 150.25 lit Total - 281.95 - Completed
CL2968 | 2022-12-09 | Namakkal 1 | C | Stamping and calibration work | Certification | Vigneshwaran & Prabu | 2022-12-09 | - | Stamping and calibration done K.factors A side 10150 B side 10150 Testing lit 249.21 Reading for A side 10.00/10.00 B side 10.05/10.00 - Completed
CL2969 | 2022-12-09 | Paramathivelur | A | Dispenser running in offline mode due to system high temperature issue | Breakdown | Thirumalaisamy | 2022-12-09 | - | System serviced - Dispenser back online - Unloading done - Recalibration done - Both side K-factor not changed. A side k factor-10000 B side k factor-10000 A side - 10.01 B side - 10.01 Testing litters: A side - 157.88litters B side - 153.33litters Total - 311.21litters Resolved
CL2970 | 2022-12-09 | Rasipuram | C | Stamping and calibration work | Certification | Vigneshwaran & Prabu | 2022-12-09 | - | Stamping and calibration done Old K factors A side 10050 B side 10100 New K factors A side 10150 B side 10100 Reading for A side 10.02/10.00 B side 9.96/10.00 Testing lit 422.31- Completed
CL2971 | 2022-12-09 | Neelambur | D | Dispensing air hose damaged | Breakdown | Gowtham | 2022-12-09 | - | New air hose replaced - Unloading done - Rectified
CL2972 | 2022-12-10 | Perambalur | C | Stamping work | Certification | Nepolean and Vignesh | 2022-12-10 | - | DL stamping done A side testing: 271.06 lit B side testing: 482.11 lit A & B old k factor: 10000 A & B new k factor: 09900. A side 10.00lit -10.00 B side 10.00lit - 9.98 - Completed
CL2973 | 2022-12-10 | Ariyalur | C | Stamping work | Certification | Nepolean and Vignesh | 2022-12-10 | - | DL stamping done A & B k factor: 10000 A & B side k factor No changes. A side testing : 135.19 lit B side testing: 142.59 lit A side 10.00 lit - 10.00 B side 10.00 lit - 9.99 - Completed
CL2974 | 2022-12-10 | Manapparai | R | Online UPS battery problem | Breakdown | Nivas | 2022-12-10 | - | Online UPS battery replaced - Working good - Resolved
CL2975 | 2022-12-11 | Villapuram | D | A nozzle mount problem | Breakdown | Kathiresan | 2022-12-11 | - | Spare nozzle replaced - B side nozzle teeth replaced to arrest leakage - Working fine - Rectified
CL2976 | 2022-12-11 | Uthamasolapuram | D | A and B side nozzle teeth problem | Breakdown | Prabu | 2022-12-11 | - | Nozzle teeth 6 nos replaced for both A and B nozzle - Unloading training provided - Completed
CL2977 | 2022-12-12 | Kangeyam | G | Tank area pavor block work | Preventive | Gowtham | 2022-12-12 | - | Civil work in process - Air hose conduit line replacement will be done along with pavor block installation - Attended
CL2978 | 2022-12-12 | Kodungaiyur | D | Keypad and dispensing hose defect | Breakdown | Suneel Sagar | 2022-12-12 | - | 2 nos keypad and dispensing hose replaced - Consol exhaust fan 2 nos replaced - Pneumatic fittings changed - Dispensing working in automation mode with both mobile and keypad - Resolved
CL2979 | 2022-12-12 | Tenkasi | G | Fire extinguisher refilling | New Project | Kathiresan | 2022-12-12 | - | Fire extinguisher refilling done - Training provided - Attended
CL2980 | 2022-12-12 | Salem | D | Dispenser error occurred | Breakdown | Prabu | 2022-12-12 | - | Dispenser cold boot done - Working fine - Rectified
CL2981 | 2022-12-12 | Virudhunagar | G | Fire extinguisher refilling | Preventive | Kathiresan | 2022-12-12 | - | Fire extinguisher refilling done - 75Kg fire extinguisher out hose replaced - Training provided - Attended
CL2982 | 2022-12-13 | Kangeyam | G | Air hose conduit work | Breakdown | Gowtham | 2022-12-13 | - | Conduit work done - Pavor work in process - Attended
CL2983 | 2022-12-14 | Ariyamangalam | T | Liquid line ROV damaged | Breakdown | Nepolean | 2022-12-14 | - | ROV replaced with new - N2 machine mouth replaced - Working good - Resolved
CL2984 | 2022-12-14 | Avinashi | T | Tank 2 dispensing vapour line ROV with ballvalve LPG leakage | Breakdown | Gowtham | 2022-12-14 | - | Ballvalve LPG leakage arrested by tightening the bolt nut - Rectified
CL2985 | 2022-12-14 | Avadi | D | Point jumping | Breakdown | Suneel Sagar | 2022-12-14 | - | DP valve spring tension adjusted - Resolved
CL2986 | 2022-12-14 | Kattupakkam | T | Tank 2 probe failure | Breakdown | Suneel Sagar | 2022-12-14 | - | Probe signal cabe reconnected - C side new keypad replaced - Rectified
CL2987 | 2022-12-14 | Devakottai | G | Fill point wicket gate welding work | New Project | Chandrasekar | 2022-12-14 | - | Fill point wicket gate welding work done - Fire extinguisher unloaded - Attended
CL2988 | 2022-12-14 | Cantonment | D | Yenen D nozzle on/off switch problem | Breakdown | Vigneshwaran | 2022-12-14 | - | On/off switch refitted - Working fine - Resolved
CL2989 | 2022-12-15 | Erode | D | B nozzle got auto preset | Breakdown | Thirumalaisamy | 2022-12-15 | - | Keypad cable reconnection done - ATG alarm selected - Rectified
CL2990 | 2022-12-15 | Sulur | D | Dispensing air hose damaged | Breakdown | Gowtham | 2022-12-15 | - | All air hoses for dispensing replaced - Resolved
CL2991 | 2022-12-15 | Tirunelveli | C | Rule 19 and new dispenser installation | Certification | Chandrasekar, Kathiresan & Dharmesh | 2022-12-21 | - | Rule 19 done for 2 tanks - Dispenser and ATG installation done - Rule 33 data collected - Dispensing and decanting operation working fine - Completed
CL2992 | 2022-12-17 | Mettupalayam | C | Calibration work | Certification | Gowtham | 2022-12-17 | - | Calibration done - A side K factor- 10200 B side K factor- 10200 A side testing - 267.03 ltrs B side testing - 228.02 ltrs. Total testing - 495.05 ltrs A side - 9.87/10.00 ltr B side - 9.86/10.00 ltr Automation metal box with data connector cable installed - Completed
CL2993 | 2022-12-17 | Tharamangalam | D | A and B nozzle servicing | Preventive | Prabu | 2022-12-17 | - | A and B nozzle serviced - Nozzle lock spring set and teeth 8 Nos changed - Dispensing liquid line ball valve leakage arrested by tightening the nut - Working fine - Rectified
CL2994 | 2022-12-17 | Devakottai | C | PESO Final inspection | Certification | Prakash | 2022-12-17 | - | PESO inspection completed - Attended
CL2995 | 2022-12-18 | Namakkal 2 | A | Automation went offline due to power strip fuse damaged and printer cable damaged | Breakdown | Prabu | 2022-12-18 | - | Power strip fuse replaced - Printer cable serviced and reconnected - Outlet back online - Resolved
CL2996 | 2022-12-18 | Puliyur | C | Outlet recalibration work | Certification | Gowtham & Thirumalaisamy | 2022-12-19 | - | Recalibration done K-factor details A side old k factor-10000 A side new k factor-10050 B side old k factor-10000 B side new k factor-10050 A side - 9.97litters B side - 9.96litters Testing litters: A side - 512.04liters B side - 207.58liters Total - 719.62liters - Completed
CL2997 | 2022-12-18 | Aravakurichi | T | Unloading and unloading training | Preventive | Thirumalaisamy | 2022-12-18 | - | Unloading done - Training provided - Attended
CL2998 | 2022-12-18 | Cantonment | D | Yenen D nozzle on/off switch problem | Breakdown | Vigneshwaran | 2022-12-18 | - | New on/off switch replaced - Working fine - Rectified
CL2999 | 2022-12-19 | Tiruchengode | R | Control panel booting problem | Breakdown | Prabu | 2022-12-19 | - | Stabilizer parameters changed - Input voltages R 218 Y 215 B 235 Output voltages R 230 Y 229 B 230 RB 398 RY 406 YB 398 - Working fine - Resolved
CL3000 | 2022-12-19 | Kumbakonam | G | Genset service | Preventive | Nepolean | 2022-12-19 | - | Genset oil service done - Completed
CL3001 | 2022-12-20 | Nasiyanur | D | Nozzle LPG leakage | Breakdown | Thirumalaisamy | 2022-12-20 | - | A nozzle center mount o ring adjusted - Unloading training provided - Testing : 2.40 Ltrs - Working good - Rectified
CL3002 | 2022-12-20 | Ariyamangalam | G | Compressor oil changing | Preventive | Nepolean | 2022-12-20 | - | Compressor oil changed - Resolved
CL3003 | 2022-12-22 | Ayothiyapattinam | R | Servo stabilizer motor problem | Breakdown | Prabu | 2022-12-23 | - | Stabilizer step up motor replaced new by Mothish service person - Working fine - Input voltage R 236 Y 240 B 234 Output voltages R 229 Y 230 B 229 - Resolved
CL3004 | 2022-12-22 | Avinashi | D | Batchen A side breakaway coupling failure | Breakdown | Gowtham | 2022-12-23 | - | A side breakaway coupling replaced with new one - Tank 1 unloading liquid line ROV replaced with new - Testing : 8.33 Ltrs - Rectified
CL3005 | 2022-12-22 | Vadivelan nagar | R | Control panel RYB and panel on indicator lamps not working | Breakdown | Suneel Sagar | 2022-12-22 | - | Control panel RYB and panel on indicator lamps changed - Completed
CL3006 | 2022-12-22 | Cantonment | D | F nozzle lock problem | Breakdown | Chandrasekar | 2022-12-22 | - | F nozzle lock replaced with new for testing - Resolved
CL3007 | 2022-12-22 | Dharapuram | G | Camera installation | New Project | Gowtham | 2022-12-22 | - | Camera jack replaced with new - Working fine - Rectified
CL3008 | 2022-12-22 | T.V.Kovil | D | C side latch changing | Preventive | Vigneshwaran | 2022-12-22 | - | Latch changed for testing purpose - Completed
CL3009 | 2022-12-22 | Ariyamangalam | D | B side latch changing | Preventive | Vigneshwaran | 2022-12-22 | - | Latch changed for testing purpose - Completed
CL3010 | 2022-12-22 | Attur | D | Dispenser to control panel air hose damaged | Breakdown | Prabu | 2022-12-22 | - | Air hose replaced - Working fine - Rectified
CL3011 | 2022-12-23 | Aravakurichi | T | Unloading pneumatic hose damaged | Breakdown | Thirumalaisamy | 2022-12-23 | - | Unloading air hose replaced - PMR done - Rectified
CL3012 | 2022-12-23 | Ariyamangalam | D | A nozzle leakage | Breakdown | Nepolean | 2022-12-23 | - | Serviced nozzle replaced - Testing : 3.48 Ltrs - Working fine - Completed
CL3013 | 2022-12-24 | Tirunelveli | C | New dispenser stamping | Certification | Prakash, Kathiresan and Vigneshwaran | 2022-12-24 | - | New dispenser installation and stamping work done Calibration report : "A" side 10 ltrs = 10.01 "B" side 10 ltrs = 10.02 "C" side 10 ltrs = 10 "D" side 10 ltrs = 9.97 "K" Factor report: "A" side 'K' factor = 10000 "B" side 'K' factor= 10000 "C" side 'K' factor =10330 "D" side 'K' factor =10341 Both dispenser working online - Total leakage test done - Unloading camer replaced - Completed
CL3014 | 2022-12-24 | Thuraiyur | D | Dispenser A side on/off switch damaged | Breakdown | Dharmesh | 2022-12-24 | - | On/off switch NO element replaced with new - Working fine - Rectified
CL3015 | 2022-12-24 | Palayam | G | Unloading camera not working | Breakdown | Thirumalaisamy | 2022-12-24 | - | Alternate camera installed at Unloading point due to unloading camera damaged - B side retraction rope replaced - Automation maintenance done - Resolved
CL3016 | 2022-12-25 | Rasipuram | D | Dispenser pressure not developing | Breakdown | Prabu | 2022-12-25 | - | Equalizer ball valve adjusted - A nozzle teeth 4 Nos replaced - Working good - Rectified
CL3017 | 2022-12-26 | Kattupakkam | G | PMR and safety training | Preventive | Suneel Sagar | 2022-12-26 | - | PMR and safety training done - Completed
CL3018 | 2022-12-27 | Melur | D | B nozzle leakage | Breakdown | Kathiresan | 2022-12-27 | - | NRV O ring refitted to arrest the leakage - Automation maintenance done - Working fine - Rectified
CL3019 | 2022-12-27 | Nasiyanur | D | A nozzle leakage | Breakdown | Thirumalaisamy | 2022-12-27 | - | Spare nozzle replaced - NRV O ring to be changed in defective nozzle - Working good - Resolved
CL3020 | 2022-12-27 | T.V.Kovil | G | Running in DG mode due to EB meter box servicing | Breakdown | Nepolean | 2022-12-27 | - | EB main box servicing done by EB person - Pump working in EB mode - Attended
CL3021 | 2022-12-27 | Kodungaiyur | C | PMR work | Certification | Suneel Sagar | 2022-12-27 | - | PMR done - Completed
CL3022 | 2022-12-27 | Velachery | C | PMR work | Certification | Suneel Sagar | 2022-12-27 | - | PMR done - Completed
CL3023 | 2022-12-29 | Kumbakonam | G | Site visit | Preventive | Prakash & Prasath | 2022-12-29 | - | Above ground motor serviced to arrest the noise - Dispenser keypad settings changed - Material to purchase listed down - Completed
CL3024 | 2022-12-29 | Bathlagundu | G | Site visit | Preventive | Kamaraj | 2022-12-29 | - | General training provided - Completed
CL3025 | 2022-12-29 | Ariyamangalam | D | OPW nozzle from Nasiyanur testing and servicing at D side | Preventive | Nepolean | 2022-12-29 | - | Nozzle testing and servicing done - Kept under observation - Testing D side : 1.52 Ltrs - Completed
CL3026 | 2022-12-29 | Avadi | C | PMR work | Certification | Suneel Sagar | 2022-12-29 | - | PMR done - Completed
CL3027 | 2022-12-30 | Virudhachalam | D | Dispensing line air hose leakage | Breakdown | Avinash | 2022-12-30 | - | New air hose replaced - Dispensing & decanding solenoid coil plunger interchanged - Working fine - Rectified
CL3028 | 2022-12-30 | Sulur | T | Decanting liquid hose brass nut damaged | Breakdown | Gowtham | 2022-12-30 | - | Unloading done by borrowed unloading hose - Hose needs to be replaced
CL3029 | 2022-12-30 | Ariyamangalam | D | OPW nozzle from Nasiyanur testing and servicing at D side | Preventive | Nepolean | 2022-12-30 | - | Nozzle testing and servicing done - Testing D side : 2.33 Ltrs - Completed
CL3030 | 2022-12-31 | Chengalpattu | C | PMR work | Certification | Suneel Sagar | 2022-12-31 | - | PMR done - Completed
CL3031 | 2022-12-31 | Villapuram | D | Dispensing air hose damaged | Breakdown | Kathiresan | 2022-12-31 | - | Damaged air hose line- replaced - PMR Done - Rectified
CL3032 | 2023-01-01 | Renganathan Gas Bunk | D | Display cable not working | Breakdown | Dharmesh | 2023-01-01 | - | Display cable refitted - Working fine - Resolved
CL3033 | 2023-01-02 | T.V.Kovil | R | Offline UPS battery low voltage problem | Breakdown | Vigneshwaran | 2023-01-02 | - | New battery replaced - Oil changed for both compressors - Working fine - Rectified
CL3034 | 2023-01-02 | Namakkal 3 | G | N2 machine not working | Breakdown | Prabu | 2023-01-02 | - | Pressure increased - N2 machine working fine - PMR done - Completed
CL3035 | 2023-01-02 | Velachery | D | C side excess flow valve jammed | Breakdown | Suneel Sagar | 2023-01-02 | - | C side excess flow valve activated - Product recirculated - Working fine - Rectified
CL3036 | 2023-01-03 | Kumbakonam | G | Water motor control box capacitor damaged | Breakdown | Nepolean | 2023-01-03 | - | New capacitor 36MFD/440VAC replaced - Working fine - Resolved
CL3037 | 2023-01-04 | Palladam 2 | G | Unloading training | Breakdown | Gowtham | 2023-01-04 | - | Unloading training provided - Completed
CL3038 | 2023-01-05 | Chinnasalem | D | Dispensing motor noise due to misalignment | Breakdown | Prabu | 2023-01-05 | - | Noise arrested by fixing alignment - Unloading and safety training done - Tank 85% cut off checked - Completed
CL3039 | 2023-01-05 | Neelambur | G | Unloading and unloading training | Preventive | Gowtham | 2023-01-05 | - | Unloading and Unloading training completed - PMR done - Attended
CL3040 | 2023-01-05 | Kattupakkam | T | OPW not working for tank 2 - Probe signal failure | Breakdown | Suneel Sagar | 2023-01-05 | - | Junction box replaced - Both tank 85% cutoff working - Resolved
CL3041 | 2023-01-05 | Ariyamangalam | D | Dispenser LED not working and RO water motor filter damaged | Breakdown | Nepolean | 2023-01-05 | - | Dispenser LED replaced - Water motor filter 2 Nos replaced - Working fine - Resolved
CL3042 | 2023-01-06 | Hosur | T | KR Gases new TT Vessel N2 purging | New Project | Prakash & Dharmesh | 2023-01-07 | - | N2 testing done at pressure 7 Kg/cm2 - Holding pressure 7 Kg/cm2 - No leakage found - Completed
CL3043 | 2023-01-06 | T.V.Kovil | G | Genset battery defect | Breakdown | Nepolean | 2023-01-06 | - | New genset battery replaced - Resolved
CL3044 | 2023-01-07 | Manapparai | G | Fire extinguisher refilling and operation training | Preventive | Avinash | 2023-01-07 | - | Fire extinguisher refilled and training provided - 75 Kg fire extinguishers painted - Attended
CL3045 | 2023-01-07 | Namakkal 3 | T | Unloading work | Preventive | Prabu | 2023-01-07 | - | Unloading done - Cut off at 85% working good - Attended
CL3046 | 2023-01-07 | Ramnad | D | Dispensing line air hose leakage | Breakdown | Kathiresan | 2023-01-07 | - | Air hose replaced - PMR done - Working fine - Rectified
CL3047 | 2023-01-07 | Theni | G | Fire extinguisher refilling and operation training | Preventive | Kamraj | 2023-01-07 | - | Fire extinguisher refilled and training provided - 75 Kg fire extinguisher hose replaced - Attended
CL3048 | 2023-01-07 | Bodi | G | Fire extinguisher refilling and operation training | Preventive | Kamraj | 2023-01-07 | - | Fire extinguisher refilled and training provided - Attended
CL3049 | 2023-01-07 | Uthamapalayam | G | Fire extinguisher refilling and operation training | Preventive | Kamraj | 2023-01-07 | - | Fire extinguisher refilled and training provided - Attended
CL3050 | 2023-01-09 | Tenkasi | G | Outlet commissioning and inauguration | New Project | Prakash, Chandrasekar, Kathiresan & Vignesh | In process | - | In process