## All
Service Logs - Jan' 2023 to Dec' 2023
ticket_no | date | name_of_the_outlet | code | nature_of_the_complaint | breakdown__ preventive | service_engineer | rectified_on | interruption_of_sales_if_any__time_duration | details_of_work_done | Remarks
CL3051 | 2023-01-01 | Renganathan Gas Bunk | D | Display cable not working | Breakdown | Dharmesh | 2023-01-01 | - | Display cable refitted - Working fine - Resolved
CL3052 | 2023-01-02 | T.V.Kovil | R | Offline UPS battery low voltage problem | Breakdown | Vigneshwaran | 2023-01-02 | - | New battery replaced - Oil changed for both compressors - Working fine - Rectified
CL3053 | 2023-01-02 | Namakkal 3 | G | N2 machine not working | Breakdown | Prabu | 2023-01-02 | - | Pressure increased - N2 machine working fine - PMR done - Completed
CL3054 | 2023-01-02 | Velachery | D | C side excess flow valve jammed | Breakdown | Suneel Sagar | 2023-01-02 | - | C side excess flow valve activated - Product recirculated - Working fine - Rectified
CL3055 | 2023-01-03 | Kumbakonam | G | Water motor control box capacitor damaged | Breakdown | Nepolean | 2023-01-03 | - | New capacitor 36MFD/440VAC replaced - Working fine - Resolved
CL3056 | 2023-01-04 | Palladam 2 | G | Unloading training | Breakdown | Gowtham | 2023-01-04 | - | Unloading training provided - Completed
CL3057 | 2023-01-05 | Chinnasalem | D | Dispensing motor noise due to misalignment | Breakdown | Prabu | 2023-01-05 | - | Noise arrested by fixing alignment - Unloading and safety training done - Tank 85% cut off checked - Completed
CL3058 | 2023-01-05 | Neelambur | G | Unloading and unloading training | Preventive | Gowtham | 2023-01-05 | - | Unloading and Unloading training completed - PMR done - Attended
CL3059 | 2023-01-05 | Kattupakkam | T | OPW not working for tank 2 - Probe signal failure | Breakdown | Suneel Sagar | 2023-01-05 | - | Junction box replaced - Both tank 85% cutoff working - Resolved
CL3060 | 2023-01-05 | Ariyamangalam | D | Dispenser LED not working and RO water motor filter damaged | Breakdown | Nepolean | 2023-01-05 | - | Dispenser LED replaced - Water motor filter 2 Nos replaced - Working fine - Resolved
CL3061 | 2023-01-06 | Hosur | T | KR Gases new TT Vessel N2 purging | New Project | Prakash & Dharmesh | 2023-01-07 | - | N2 testing done at pressure 7 Kg/cm2 - Holding pressure 7 Kg/cm2 - No leakage found - Completed
CL3062 | 2023-01-06 | T.V.Kovil | G | Genset battery defect | Breakdown | Nepolean | 2023-01-06 | - | New genset battery replaced - Resolved
CL3063 | 2023-01-07 | Manapparai | G | Fire extinguisher refilling and operation training | Preventive | Avinash | 2023-01-07 | - | Fire extinguisher refilled and training provided - 75 Kg fire extinguishers painted - Attended
CL3064 | 2023-01-07 | Namakkal 3 | T | Unloading work | Preventive | Prabu | 2023-01-07 | - | Unloading done - Cut off at 85% working good - Attended
CL3065 | 2023-01-07 | Ramnad | D | Dispensing line air hose leakage | Breakdown | Kathiresan | 2023-01-07 | - | Air hose replaced - PMR done - Working fine - Rectified
CL3066 | 2023-01-07 | Theni | G | Fire extinguisher refilling and operation training | Preventive | Kamraj | 2023-01-07 | - | Fire extinguisher refilled and training provided - 75 Kg fire extinguisher hose replaced - Attended
CL3067 | 2023-01-07 | Bodi | G | Fire extinguisher refilling and operation training | Preventive | Kamraj | 2023-01-07 | - | Fire extinguisher refilled and training provided - Attended
CL3068 | 2023-01-07 | Uthamapalayam | G | Fire extinguisher refilling and operation training | Preventive | Kamraj | 2023-01-07 | - | Fire extinguisher refilled and training provided - Attended
CL3069 | 2023-01-09 | Tenkasi | G | Outlet commissioning | New Project | Prakash, Chandrasekar, Kathiresan & Vignesh | 2023-01-10 | - | Vessel purging, Unloading done - Dispensing and decanting pump commissioned - All equipment working fine - Dispenser stamping done - Automation work done - Completed
CL3070 | 2023-01-10 | T.V.Kovil | D | Yenen C side Dotkeys keypad testing | Preventive | Nepolean | 2023-01-10 | - | Keypad tested and 1 keypad kept fixed in C side for observation - Completed
CL3071 | 2023-01-10 | Ariyamangalam | D | B nozzle leakage | Breakdown | Nepolean | 2023-01-10 | - | Nozzle teeth 4 nos replaced - Working fine - Resolved
CL3072 | 2023-01-10 | Ammapet | C | Rule 33 data collection and third party inspection | Certification | Prabu | 2023-01-10 | - | Rule 33 data collected - Third party inspection done - Attended
CL3073 | 2023-01-10 | Karur | R | Compressor contactor and V belt damaged | Breakdown | Thirumalaisamy | 2023-01-10 | - | Contactor and V belt replaced - Compressor oil changed - Working fine - Resolved
CL3074 | 2023-01-11 | Tenkasi | G | Outlet inauguration | New Project | Prakash, Chandrasekar, Kathiresan & Vignesh | 2023-01-11 | - | Outlet opened to public Opening reading "A" side= 336.87 "B" side= 274.74 Tank open= 40% - Attended
CL3075 | 2023-01-11 | Cantonment | A | Automation testing to predict minimum preset transaction | Preventive | Dharmesh | 2023-01-11 | - | Testing done - Minimum preset has to be avoided - Testing E side : 1 Ltr - Completed
CL3076 | 2023-01-11 | Kattupakkam | A | Automation testing to predict minimum preset transaction | Breakdown | Suneel Sagar | 2023-01-11 | - | Testing done - Minimum preset has to be avoided - Completed
CL3077 | 2023-01-12 | Namakkal 2 | G | Fire extinguisher refilling and operation training | Preventive | Prabu | 2023-01-12 | - | Fire and safety training provided to pump staffs - Leakage tested - 5 kg fire extinguishers serviced - Attended
CL3078 | 2023-01-12 | Theni | G | Additional earth marking | Preventive | Kathiresan | 2023-01-12 | - | Earth marking done - Completed
CL3079 | 2023-01-12 | Tirunelveli | G | Additional earth marking | Preventive | Kathiresan | 2023-01-12 | - | Earth marking done - Completed
CL3080 | 2023-01-14 | Thuraiyur | D | Dispenser program switch defective | Breakdown | Avinash | 2023-01-14 | - | Program switch replaced - Testing : 2.92 Ltrs - Working fine - Resolved
CL3081 | 2023-01-14 | Chinnasalem | D | Dispensing motor vibrating | Breakdown | Prabu | 2023-01-14 | - | Motor bolts tightened - Pump to motor distance aligned - Working fine - Rectified
CL3082 | 2023-01-14 | Virudhunagar | B | B side on/off switch not working | Breakdown | Kathiresan | 2023-01-14 | - | On/off switch NO element replaced - PMR done - Working good - Resolved
CL3083 | 2023-01-14 | Vadivelan Nagar | D | B and C side keypads testing | New Project | Suneel Sagar | 2023-01-14 | - | Keypads replaced for testing purpose - Kept under observation - Completed
CL3084 | 2023-01-14 | Eral | R | Servo stabilizer B side damaged due to short circuit | Breakdown | Kathiresan | 2023-01-15 | - | Power directed to control panel bypassing the servo stabilizer for temporarily - Attended
CL3085 | 2023-01-15 | Avadi | D | Dispenser not working in Run mode | Breakdown | Suneel Sagar | 2023-01-15 | - | Control panel Tank 1 W1 axilliary contactor NO element replaced - Dispenser working in Run mode - AB nozzle manual to automation switch 1 no replaced - Working satisfied - Rectified
CL3086 | 2023-01-15 | Avinashi | G | Outlet working in Genset mode due to EB high voltage problem | Breakdown | Prabu | 2023-01-15 | - | EB - RYB line reconnected - After assuring the EB voltage is normal, line changed to EB - Working fine in both EB and Genset mode - Resolved
CL3087 | 2023-01-16 | Kodumudi | G | General inspection | Preventive | Thirumalaisamy | 2023-01-16 | - | Inspection done - Found satisfactory - Completed
CL3088 | 2023-01-17 | Palayam | D | B side display shows error during dispensing randomly | Breakdown | Thirumalaisamy | 2023-01-17 | - | A and B side keypads interchanged and display cable refitted - Automation CPU serviced for heating issue - Kept under observation - Rectified
CL3089 | 2023-01-18 | Namakkal 3 | T | Tank liquid line pressure not developed | Breakdown | Prabu | 2023-01-18 | - | Emergency liquid line is connected - Pressure maintained at 12 bar - Working fine - Resolved
CL3090 | 2023-01-18 | Tirunelveli | G | Fire extinguisher refilling and servicing | Preventive | Kathiresan | 2023-01-18 | - | Fire extinguisher serviced - Refilling required - 75 Kg extinguishers wheels to be replaced - Camera line POE switch to be replaced - Attended
CL3091 | 2023-01-18 | T.V.Kovil | C | PMR work | Certification | Vigneshwaran | 2023-01-18 | - | PMR done - Vapour line ball valve leakage arrested by tightening the nut - Working fine - Completed
CL3092 | 2023-01-18 | Avadi | D | B side point jumping complaint | Breakdown | Suneel Sagar | 2023-01-18 | - | DP valve diaphragm replaced - Point jumping stopped - B and D nozzle teeth replaced - Working fine - Rectified
CL3093 | 2023-01-19 | Dharmapuri | G | EB line B phase wire melted | Breakdown | Prabu | 2023-01-19 | - | B phase wire reconnected - MCB 1 No replaced - Working fine - Resolved
CL3094 | 2023-01-19 | Cantonment | A | CD and EF nozzles going offline for automation maintenance | Preventive | Madhavan | 2023-01-19 | - | Automation maintenance done - CD and EF nozzles back online - Completed
CL3095 | 2023-01-19 | Saravanampatty | C | PMR work | Certification | Gowtham | 2023-01-19 | - | PMR done - Completed
CL3096 | 2023-01-20 | Sulur | T | Unloading liquid hose brass adapter damaged | Breakdown | Gowtham | 2023-01-21 | - | Unloading liquid hose brass adapter replaced - Unloading can be done - Resolved
CL3097 | 2023-01-20 | T.V.Kovil | D | Dispenser on/off switch defect | Breakdown | Dharmesh | 2023-01-20 | - | On/off switch replaced with new - Working fine - Rectified
CL3098 | 2023-01-20 | Ariyamangalam | G | Genset battery defect | Breakdown | Nepolean | 2023-01-21 | - | Genset battery replaced - Working good - Resolved
CL3099 | 2023-01-20 | Villapuram | D | D nozzle leakage | Breakdown | Kathiresan | 2023-01-20 | - | D nozzle teeth 4 Nos replaced - Spare nozzle teeth and NRF O ring changed to make it ready - Rectified
CL3100 | 2023-01-21 | Chengalpattu | C | Rule 19 work | Certification | Suneel Sagar, Chandrasekar, Nivas and Avinash | 2023-01-23 | 2 Days | Rule 19 done - New ATG installed - Sales started with automation - Completed
CL3101 | 2023-01-21 | Ramnad | T | Decanting pump leakage | Breakdown | Kathiresan | 2023-01-22 | - | Pump seal and inner "O Ring" 3 nos newly changed - Working fine - Unloading done upto 70% - No leakage found - Resolved
CL3102 | 2023-01-21 | Renganathan Gas Bunk | D | Dispensing not working | Breakdown | Nepolean | 2023-01-21 | - | Panel incoming phase changed - Dispensing working fine - Rectified
CL3103 | 2023-01-22 | Saravanampatty | D | Dotkeys keypad testing | New Project | Gowtham | 2023-01-22 | - | 2 keypads failure and 1 working fine in A side - Defective keypads returned to supplier for defect analysis and replacement - Resolved
CL3104 | 2023-01-23 | Musiri | T | Unloading pump abnormal sound | Breakdown | Dharmesh | 2023-01-23 | - | Bypass valve adjusted & grease applied to the pump to reduce the abnormal sound - N2 machine sound buzzer and clip connector replaced - Control panel & DB panel R and B phase indicator light changed - PMR done - Completed
CL3105 | 2023-01-23 | Virudhunagar | G | Site visit | Preventive | Kathiresan | 2023-01-23 | - | Rule 19 materials and Fencing, compound wall civil work requirements noted - Attended
CL3106 | 2023-01-23 | Tenkasi | T | Unloading and unloading training | Preventive | Kathiresan | 2023-01-23 | - | Unloading done - Cut off at 84% working good - Camera connected to HO - Total leakage test done - Attended
CL3107 | 2023-01-24 | Namakkal 3 | T | Vapour balancing line issue | Breakdown | Prakash & Prabu | 2023-01-24 | - | Proper guidance has been provided - Attended
CL3108 | 2023-01-24 | Avadi | A | A nozzle latch assembly problem | Breakdown | Chandrasekar | 2023-01-24 | - | Latch assembly changed - Working fine - Resolved
CL3109 | 2023-01-24 | Kodungaiyur | C | Calibration work | Certification | Chandrasekar | 2023-01-24 | - | Calibration work done - A. Testing =167.03 B. Testing =151.69 Total testing =318.72 litre A. Sales.10=9.99 B. Sales.10=10 - Completed
CL3110 | 2023-01-25 | Cantonment | C | Calibration work | Certification | Nepolean | 2023-01-25 | - | Calibration work done - A side Testing : 132.85 B side Testing: 106.08 C side Testing: 100.50 D side Testing: 110.34 E side Testing: 110.62 F side Testing: 110.20 Total Testing: 670.59 ltrs - Completed
CL3111 | 2023-01-25 | Chengalpattu | G | Site visit | Preventive | Suneel Sagar | 2023-01-25 | - | Site visit done - All components working fine - Completed
CL3112 | 2023-01-26 | Manapparai | D | A side on/off switch defect | Breakdown | Nepolean | 2023-01-26 | - | On/off switch replaced with new - Working fine - Rectified
CL3113 | 2023-01-26 | Paramathivelur | D | Dispensing motor cooling fan damaged | Breakdown | Thirumalaisamy | 2023-01-26 | - | Fan to be replaced - System CPU serviced for heating issue - Temporarily rectified
CL3114 | 2023-01-27 | Eral | R | Servo stabilizer short circuit and online UPS defect | Breakdown | Kathiresan | 2023-01-27 | - | Servo stablizer complete unit - Working fine - Online UPS replaced temporarily - Resolved
CL3115 | 2023-01-27 | Kangeyam | D | Yenen D side high flow solenoid coil fuse failure | Breakdown | Gowtham | 2023-01-27 | - | Solenoid coil fuse replaced - Dispensing motor spider replaced with new - PMR done - Rectified
CL3116 | 2023-01-27 | Musiri | R | Compressor oil changing and DB panel indicator light broken | Breakdown | Nivas | 2023-01-27 | - | Compressor oil changed for both compressor - DB panel Y phase indicator light changed - Working fine - Resolved
CL3117 | 2023-01-27 | Kumbakonam | C | PMR work | Certification | Vigneshwaran and Navaneetha Krishnan | 2023-01-27 | - | PMR done - Completed
CL3118 | 2023-01-27 | Karur | D | Batchen B side slow delivery | Breakdown | Thirumalaisamy | 2023-01-27 | - | High flow low flow solenoid valve cleaned - Testing : 84.24 Ltrs - Working fine - Rectified
CL3119 | 2023-01-28 | Kodumudi | T | Tank area dispensing line pneumatic hose damaged rat bite | Breakdown | Thirumalaisamy | 2023-01-28 | - | Pneumatic hose replaced for 10 feet - Working fine - Resolved
CL3120 | 2023-01-28 | Virudhunagar | C | Rule 19 work | Certification | Prakash, Kathiresan, Chandrasekar & Dharmesh | 2023-01-31 | 33 Hours | Sales stopped - Rule 19 done - Dispensing and decanting working fine - Sales started - Testing : 10.44 Ltrs - Completed
CL3121 | 2023-01-29 | Attur | D | Batchen A side nozzle leakage | Breakdown | Prabu | 2023-01-29 | - | Spare nozzle replaced - Tank area ballvalve with ROV leakage arrested by tightening the nut - Working fine - Rectified
CL3122 | 2023-01-30 | Chengalpattu | T | Above ground motor commissioning | Preventive | Nivas and Vigneshwaran | 2023-01-31 | 4.30 Hours | Above ground motor commissioned and performance is satisfactory - Motor drawing current 6.7A, 7.2A and 6.9A in RYB respectively - Tank pressure 6kg - Pump pressure 15kg - Completed
CL3123 | 2023-01-30 | Tiruchengode | T | Tank area vapour line ROV inside air leakage | Breakdown | Prabu | 2023-01-30 | - | ROV replaced - Working fine - Resolved
CL3124 | 2023-01-30 | Palladam 1 | D | Batchen dispenser both side solenoid not working properly | Breakdown | Gowtham | 2023-01-30 | - | Power cord replaced with new - Solenoid coil interchanged - Yenen D side nozzle teeth replaced - Kept under observation - Testing : 204.79 Ltrs - Rectified
CL3125 | 2023-01-31 | Tirunelveli | G | Fire extinguisher refilling work | Preventive | Dharmesh | 2023-01-31 | - | Fire extinguisher refilling done - Fire safety training provided to pump staffs - Attended
CL3126 | 2023-01-31 | T.V.Kovil | D | Error 23 occurred | Breakdown | Pandi Durai | 2023-01-31 | - | Display cable loose connection refitting done - Resolved
CL3127 | 2023-02-01 | Sulur | T | Unloading vent pipeline installation due to 6mm SS vent tube got block internally | Breakdown | Gowtham | 2023-02-01 | - | Unloading vent pipeline installed - Air inflator compressor oil changed - PMR done - Nozzle 1 No serviced - Testing : 0.89 Ltrs - Resolved
CL3128 | 2023-02-01 | Velachery | D | CD nozzle motherboard replacement | Breakdown | Suneel Sagar | 2023-02-01 | - | Repaired motherboard replaced - Under observation - Completed
CL3129 | 2023-02-03 | Virudhunagar | G | Civil work | New Project | Kathiresan | 2023-02-03 | - | Civil work and tottem pole foundation work done - Control panel FRL changed - Attended
CL3130 | 2023-02-03 | Manapparai | T | Dispensing air hose damaged | Breakdown | Pandi Durai | 2023-02-03 | - | Dispensing and decanting line air hose replaced with new - No leakage found - Resolved
CL3131 | 2023-02-03 | Cantonment | D | B and E nozzles leakage | Breakdown | Chandrasekar | 2023-02-03 | - | Nozzle teeth 4 nos replaced - Leakage arrested - Working fine - Resolved
CL3132 | 2023-02-03 | Ariyamangalam | R | Control panel B phase indicator not working | Breakdown | Nepolean | 2023-02-03 | - | B phase indicator replaced with new - Working good - Rectified
CL3133 | 2023-02-04 | Bodi | A | Automation and camera maintenance | Preventive | Prasath, Madhavan & Kamaraj | 2023-02-04 | - | Automation and camera maintenance done - Operation training provided to new staffs - Dispensing motor lovejoy coupling replaced - Completed
CL3134 | 2023-02-04 | Uthamapalayam | A | Automation and camera maintenance | Preventive | Prasath, Madhavan & Kamaraj | 2023-02-04 | - | Automation and camera maintenance done - Completed
CL3135 | 2023-02-04 | Theni | A | Automation and camera maintenance | Preventive | Prasath, Madhavan & Kamaraj | 2023-02-04 | - | Automation and camera maintenance done - Completed
CL3136 | 2023-02-04 | Palladam 2 | G | Unloading training | Preventive | Gowtham | 2023-02-04 | - | Unloading training provided - Completed
CL3137 | 2023-02-05 | Avinashi | G | Control panel not booting up with EB power due to phase reverse | Breakdown | Gowtham | 2023-02-05 | - | EB phase reversed - PMR done - Rectified
CL3138 | 2023-02-06 | Dindigul | A | Dispenser going offline due to CPU fan issue | Breakdown | Kamaraj | 2023-02-06 | - | CPU serviced - Outlet back online - Resolved
CL3139 | 2023-02-06 | T.V.Kovil | A | Automation maintenance | Preventive | Madhavan | 2023-02-06 | - | Automation maintenance done - Outlet back online - Completed
CL3140 | 2023-02-06 | Cantonment | D | C and D nozzles not working properly | Breakdown | Chandrasekar | 2023-02-06 | - | New nozzles replaced - C. Pump opening=3085017.81 C. Pump closing =3653300.52 D. Pump opening =3007289.92 D. Pump closing=3549212.69 C. Testing =1.01 D. Testing =0.90 - Completed
CL3141 | 2023-02-06 | T.V.Kovil | D | A nozzle teeth worn out | Breakdown | Vigneshwaran | 2023-02-06 | - | Nozzle teeth 4 nos replaced - Working fine - Resolved
CL3142 | 2023-02-06 | Chengalpattu | R | Online UPS battery defect | Breakdown | Suneel Sagar | 2023-02-06 | - | UPS battery replaced - Leakage test done - Rectified
CL3143 | 2023-02-06 | Villapuram | A | A and B nozzle going offline due to system hang | Breakdown | Kathiresan & Madhavan | 2023-02-07 | - | Automation system restarted - A and B nozzle back online - Resolved
CL3144 | 2023-02-07 | Tenkasi | C | PESO inspection | Certification | Kathiresan | 2023-02-07 | - | PESO inspection done - Completed
CL3145 | 2023-02-07 | Cantonment | A | Automation demo to BPCL officers | Preventive | Chandrasekar | 2023-02-07 | - | Demo done on 04.02.2023 - E side Testing : 30.84 Ltrs - Attended
CL3146 | 2023-02-07 | Ariyamangalam | D | Nozzle testing at D side | Preventive | Nepolean | 2023-02-07 | - | Nozzle serviced and tested - Testing : 3.15 Ltrs - Completed
CL3147 | 2023-02-08 | Palladam 1 | C | Calibration and stamping work | Certification | Dharmesh | 2023-02-08 | - | Calibration and stamping done - A & B side K factor-101000 C & D side K factor- 10050 A side - 10.00/10.00 ltrs B side - 9.97/10.00 ltrs C side - 9.99/10.00 ltrs D side - 10.01/10.00 ltrs Total testing - 776.87 ltrs - Completed
CL3148 | 2023-02-08 | Ramnad | T | Unloading pump o ring damage | Breakdown | Kathiresan | 2023-02-08 | - | Unloading pump inside "12/4" and "4/2" bearing 'O Ring' changed - 50NB ballvalve with ROV stem LPG leakage arrested by applying teflon - 84% cutoff working fine - Resolved
CL3149 | 2023-02-08 | Namakkal 2 | C | Dispenser stamping work | Certification | Prabu | 2023-02-08 | - | Dispenser stamping done - Dispensing motor spider replaced with new - Rectified
CL3150 | 2023-02-08 | Chinnasalem | D | Dispensing motor suction problem | Breakdown | Chandrasekar | 2023-02-08 | - | Emergency evacuation line changed - Suction adjusted - Kept under observation - Resolved
CL3151 | 2023-02-09 | Chinnasalem | D | Dispensing motor suction problem | Breakdown | Prabu | 2023-02-10 | - | Bypass valve cleaned - Pump unit reassembled to develop the pressure - Working fine - Rectified
CL3152 | 2023-02-11 | Bathlagundu | G | Site visit | Preventive | Kamaraj | 2023-02-11 | - | Total leakage check - Nozzle stuck up released - Completed
CL3153 | 2023-02-12 | Dindigul | C | Rule 19 work | Certification | Chandrasekar, Kamaraj & Nivas | 2023-02-14 | 30 Hours | Sales stopped - Rule 19 done - Commisssioning done - Sales started - Completed
CL3154 | 2023-02-12 | Mettupalayam | T | Unloading and dispensing vapour ball valve leakage | Breakdown | Gowtham | 2023-02-12 | - | Vapour ball valve leakage arrested by tightening the nut - PMR done - Dispensing and unloading air hose changed - Resolved
CL3155 | 2023-02-12 | Virudhunagar | G | Site visit | Renovation | Kathiresan | 2023-02-12 | - | Site visit done - Completed
CL3156 | 2023-02-13 | Dharmapuri | C | Stamping and calibration work | Certification | Prabu & Vigneshwaran | 2023-02-13 | - | Calibration and stamping done - "A" side 10 ltrs = 10.01 "B" side 10 ltrs = 9.98 "K" Factor reports: "A" side 'K' factor = 10100 "B" side 'K' factor= 10100 Testing A side - 100 Ltrs B side - 100 Ltrs Total - 200 Ltrs - Completed
CL3157 | 2023-02-13 | Avadi | C | PMR work | Preventive | Suneel Sagar | 2023-02-13 | - | PMR done - Completed
CL3158 | 2023-02-14 | Cantonment | C | Stamping work | Certification | Nepolean | 2023-02-14 | - | DL stamping done - Testing: A side : 230.80 B side : 150.17 C side: 175.17 D side: 124.81 E side : 150.06 F side : 150.06. Total Testing: 981.07 lit. K factor not changed - Completed
CL3159 | 2023-02-15 | T.V.Kovil | G | Outlet going offline due to electrical work | Renovation | Nepolean | 2023-02-16 | 30 Mins | Overall electrical panel shifting work done - Working fine - Completed
CL3160 | 2023-02-15 | Chinnasalem | T | Dispensing pump not working | Breakdown | Prabu | 2023-02-15 | 24 Hours (One Side) | Pump unit changed - Pressure developed to 12 bar - Working fine - Resolved
CL3161 | 2023-02-16 | Virudhunagar | G | Fencing and compound civil work | Renovation | Kathiresan | 2023-02-16 | - | Fencing and compound civil work done - Painting work done - New tottempole installed - Air compressor pressure switch and NRV O ring to be replaced - Rectified
CL3162 | 2023-02-16 | Chengalpattu | C | PMR work | Preventive | Suneel Sagar | 2023-02-16 | - | PMR done - Completed
CL3163 | 2023-02-17 | Kodungaiyur | C | PMR work | Preventive | Suneel Sagar | 2023-02-17 | - | PMR done - Unloading solenoid assembly and dispensing pump spider changed - Completed
CL3164 | 2023-02-18 | T.V.Kovil | A | Automation offline billing provision | Preventive | Madhavan | 2023-02-18 | - | Offline billing provided - Completed
CL3165 | 2023-02-18 | Dharapuram | C | Recalibration due to stock loss | Breakdown | Gowtham and Vigneshwaran | 2023-02-19 | - | Calibration done - Kept under observation - Dispensing vapour 1" ROV replaced by new one - Testing : 352.27 Ltrs - Completed
CL3166 | 2023-02-18 | Vedachandur | G | Site visit | Preventive | Kamaraj | 2023-02-18 | - | Dispensing ROV air hose line changed with spare air hose line - All leakage checked - Resolved
CL3167 | 2023-02-18 | T.V.Kovil | A | Offline billing initiated due to civil and electrical work | Renovation | Madhavan | 2023-02-20 | - | Both dispensers back online - Completed
CL3168 | 2023-02-19 | Avadi | R | Unloading solenoid not working | Breakdown | Suneel Sagar | 2023-02-19 | - | Unloading solenoid assembly replaced - Working fine - Resolved
CL3169 | 2023-02-20 | T.V.Kovil | D | D nozzle leakage | Breakdown | Vigneshwaran | 2023-02-20 | - | Nozzle hammer teeth 4 Nos replaced - Working good - Rectified
CL3170 | 2023-02-20 | Theni | T | Decanting motor not working due to return signal problem | Breakdown | Kamaraj | 2023-02-21 | - | Return signal cable newly changed - Decanting motor working fine - Dispensing solenoid coil cleaned - General check up done - Completed
CL3171 | 2023-02-20 | Ariyalur | R | Dispensing solenoid coil air leakage | Breakdown | Avinash | 2023-02-20 | - | New dispensing solenoid coil replaced - Working fine - Resolved
CL3172 | 2023-02-21 | Attur | C | Dispenser calibration and stamping work | Certification | Vigneshwaran and Prabu | 2023-02-21 | - | Dispenser calibration and stamping done - Attended
CL3173 | 2023-02-21 | Tirunelveli | T | Tank 1 rochester gauge dial not working | Breakdown | Kathiresan | 2023-02-21 | - | Rochester gauge dial replaced - 2 Earth provision given additionally - Earth value = 1.8 v - Working good - Completed
CL3174 | 2023-02-21 | Mettupalayam | T | ATG junction box to OPW display extension cable earth wire damage inside due to rat bite | Breakdown | Gowtham | 2023-02-21 | - | Earth cable replaced - Automation maintenance done - Resolved
CL3175 | 2023-02-21 | T.V.Kovil | G | Fire extinguisher hose damaged | Breakdown | Avinash | 2023-02-21 | - | ABC type fire extinguisher hose changed - Attended
CL3176 | 2023-02-21 | Ariyamangalam | G | N2 machine On/off switch not working | Breakdown | Nepolean | 2023-02-21 | - | On/off switch replaced with new - Working fine - Rectified
CL3177 | 2023-02-22 | Thuraiyur | G | Site visit | Preventive | Nivas | 2023-02-22 | - | Site visit done - Rule 19 requirement noted - Completed
CL3178 | 2023-02-22 | Tharamangalam | A | Outlet went offline due to earthing problem | Breakdown | Prabu | 2023-02-22 | - | 3 units of chemical earthing installed - Earthing is stable - RS485 to USB converter board replaced - Working fine - Rectified
CL3179 | 2023-02-23 | Cantonment | G | ABC fire extinguisher hose damage | Breakdown | Chandrasekar | 2023-02-23 | - | ABC fire extinguisher hose 2 nos replaced - Working fine - Resolved
CL3180 | 2023-02-23 | Mulanur | G | Fire extinguisher service | Preventive | Thirumalaisamy | 2023-03-23 | - | Fire extinguisher serviced - 9kg ABC fire extinguisher 1 no replaced with new - Fire fighting training provided to pump staffs - Completed
CL3181 | 2023-02-23 | Kangeyam | G | Fire extinguisher service | Preventive | Gowtham | 2023-02-23 | - | Fire extinguisher serviced - 9kg ABC fire extinguisher 1 no and Co2 extinguisher replaced with new - Fire fighting training provided to pump staffs - Completed
CL3182 | 2023-02-23 | Ariyamangalam | D | B side LPG dispensing hose damaged | Breakdown | Nepolean | 2023-02-23 | - | LPG dispensing hose and Yenen nozzle lock replaced - Working fine - Testing : 1.05 Ltrs - Rectified
CL3183 | 2023-02-24 | Rasipuram | G | Servo stablizer inside wire burnt | Breakdown | Prabu | 2023-02-27 | - | Co2 Fire extinguisher used - Stabilizer bypassed - Resolved temporarily on 24.02.2023 - Stabilizer serviced by service person - R 229 Y 230 B 229 - Working fine - Resolved
CL3184 | 2023-02-24 | Tiruchengode | G | Unloading training | Preventive | Prabu | 2023-02-24 | - | Unloading training provided - Unloading cut off checked - Completed
CL3185 | 2023-02-26 | Ellis Nagar | G | Fire lightened by unknown person in vacant area next to side road | Preventive | Venkatesh | 2023-02-26 | - | Fire, EB and police personnel have been called by nearby persons and immediately rushed and extinguished the fire
CL3186 | 2023-02-27 | Vadivelan Nagar | T | Dispenser 2 pneumatic line leakage | Breakdown | Suneel Sagar | 2023-02-27 | - | Pneumatic hose replaced - Working fine - Resolved
CL3187 | 2023-02-27 | Velachery | T | Unloading pump not working | Breakdown | Suneel Sagar | 2023-02-27 | - | New unloading pump replaced, commissioned and unloaded product - Found LPM 201 Ltrs and no liquid while venting liquid hose - Working fine - Rectified
CL3188 | 2023-02-28 | Cantonment | D | Nozzle replacement with Czar nozzles for testing | Preventive | Chandrasekar | 2023-02-28 | - | Czar nozzles replaced at C, D, E, F sides for testing purpose - C. Reading. 3707925.55 D. Reading.3597379.52 E. Reading.361821.67 F. Reading.343410.68 C. Testing.1.01 (Brass Nozzle) D. Testing.0.92 (Aluminium Nozzle) E. Testing.0.92 (Brass Nozzle) F. Testing.0.79 (Aluminium Nozzle) Total Testing. 3.64 litre - Kept under observation - A side switch NO element and hammer teeth replaced - Completed
CL3189 | 2023-02-28 | Salem | D | Dispenser bottom vapour ROV leakage | Breakdown | Prabu | 2023-02-28 | - | Ball valve with ROV replaced with new - Tank area liquid line ball valve leakage arrested by tightening the nut and teflon applied - Testing : 3.36 Ltrs - Resolved
CL3190 | 2023-03-01 | Kumbakonam | G | Fire extinguisher service | Preventive | Pandi Durai | 2023-03-01 | - | Fire extinguisher service done - Safety training provided to pump staff - Completed
CL3191 | 2023-03-01 | Thiruvaiyaru | G | Fire extinguisher service | Preventive | Pandi Durai | 2023-03-01 | - | Fire extinguisher service done - Co2 fire extinguishers 2 nos changed- 10 kg DCP powder changed - Safety training provided to pump staff - Completed
CL3192 | 2023-03-01 | Ammapet | G | Earthing installation | New Project | Prabu | 2023-03-01 | - | Earth installed - Connected to DG and EB room - Completed
CL3193 | 2023-03-01 | Vadivelan Nagar | C | PMR work | Certification | Suneel Sagar | 2023-03-01 | - | PMR done - C side dispenser hose replaced - Completed
CL3194 | 2023-03-02 | Tenkasi | R | Servo stabilizer servo mode not working | Breakdown | Kathiresan | 2023-03-02 | - | Servo stabilizer commissioned - Servo mode working fine - RN 238, YN 237, BN 239 volts. Neutral to Earth = 1.4 (v) - Automation camera back online - Completed
CL3195 | 2023-03-02 | T.V.Kovil | G | Sales stopped due to road construction work | Renovation | Avinash | 2023-03-02 | 2 Hours | Sales started - Construction work done - completed
CL3196 | 2023-03-02 | Manapparai | C | Stamping and calibration work | Certification | Dharmesh & Pandi Durai | 2023-03-02 | - | Calibration done - "A" side 10 ltrs = 9.97 "B" side 10 ltrs = 9.97 "K" Factor reports: "A" side 'K' factor = 10190 "B" side 'K' factor= 10280 Testing A side 153.28 B side 148.30 PMR done Master data collected - Completed
CL3197 | 2023-03-02 | Velachery | C | PMR work | Certification | Suneel Sagar | 2023-03-02 | - | PMR done - Completed
CL3198 | 2023-03-03 | Melur | G | Unloading and unloading training | Preventive | Kathiresan | 2023-03-03 | - | Unloading done - Cutoff works at 84% - Unloading training provided - Unloading solenoid cleaned and refitted - Working fine - Attended
CL3199 | 2023-03-03 | Uthamasolapuram | R | Servo stabilizer not working properly | Breakdown | Prabu | 2023-03-03 | - | Stabilizer 230v 50/60Hz contactor 1 no changed - Output R 230 Y 229 B 230 voltages - Working fine - Resolved
CL3200 | 2023-03-04 | Thiruvaiyaru | C | DL stamping work | Certification | Nepolean & Dharmesh | 2023-03-04 | - | DL stamping done - A sideTesting: 127.21 , B side testing: 291.83 . Total testing: 419.04 lit - Completed
CL3201 | 2023-03-04 | T.V.Kovil | G | Sales stopped due to road construction work | Renovation | Avinash | 2023-03-04 | 1 Hour | Sales started - Construction work done - completed
CL3202 | 2023-03-04 | Vellakovil | D | C side keypad not functioning | Breakdown | Thirumalaisamy | 2023-03-04 | - | C keypad refitted - Nozzle hose retraction rope replaced - PMR done - Working fine - Rectified
CL3203 | 2023-03-05 | Palladam 1 | D | Error 62 occurred | Breakdown | Gowtham | 2023-03-05 | - | Reset done - Testing : 1.15 Ltrs - Error rectified
CL3204 | 2023-03-05 | Neelambur | T | Unloading vapour ACME adapter problem | Breakdown | Gowtham | 2023-03-05 | - | Unloading vapour ACME adapter refitted - A nozzle LPG leakage from inner mount arrested by NRV tightened - Resolved
CL3205 | 2023-03-06 | Saravanampatty | D | Dispenser not working in Run mode and unloading cant be done | Breakdown | Gowtham | 2023-03-07 | - | Unloading NO element and R2 contactor replaced - Dispenser working in run mode - Unloading done - Rectified
CL3206 | 2023-03-06 | Ammapet | G | Fire extinguisher service | Preventive | Prabu | 2023-03-06 | - | Fire extinguisher service done - Fire safety training provided - Completed
CL3207 | 2023-03-06 | Bhavani | G | Fire extinguisher service | Preventive | Prabu | 2023-03-06 | - | Fire extinguisher service done - Fire safety training provided - Completed
CL3208 | 2023-03-06 | Perundurai | G | Fire extinguisher service | Preventive | Prabu | 2023-03-06 | - | Fire extinguisher service done - Fire safety training provided - Completed
CL3209 | 2023-03-07 | Rasipuram | T | Unloading and unloading training | Preventive | Prabu | 2023-03-07 | - | Unloading done - Unloading training provided - Attended
CL3210 | 2023-03-07 | Ariyamangalam | D | B nozzle LPG leakage | Breakdown | Nepolean | 2023-03-07 | - | Serviced nozzle replaced - Working fine - Testing : 1.07 Ltrs - Resolved
CL3211 | 2023-03-07 | Musiri | G | Fire extinguisher service | Preventive | Nivas | 2023-03-07 | - | 75kg extinguisher damaged hose serviced by crimping - 9Kg extinguisher hose replaced for both - Fire safety training provided - Completed
CL3212 | 2023-03-07 | T.V.Kovil | D | Batchen dispenser B nozzle teeth damage | Breakdown | Vigneshwaran | 2023-03-07 | - | Nozzle teeth 4 Nos replaced - Rectified
CL3213 | 2023-03-07 | Namakkal 1 | D | A side keypad defect | Breakdown | Prabu | 2023-03-07 | - | A side keypad 1 no replaced - Compressor oil changed - UPS battery water level top up done - PMR completed - Resolved
CL3214 | 2023-03-08 | Ammapet | T | N2 test | New Project | Prabu | 2023-03-08 | - | Nitrogen test done - Testing pressure - 14 kg/cm² - Holding pressure 10 kg/cm² - Electrical work finished - Completed
CL3215 | 2023-03-08 | Saravanampatty | R | Dispensing contactor failure | Breakdown | Gowtham | 2023-03-08 | - | R1 contactor replaced with new one - Working fine - Rectified
CL3216 | 2023-03-08 | Devakottai | G | Site visit | New Project | Prakash, Prasath, Prasanna Narasimhan and Dharmesh | 2023-03-08 | - | Site visit done - Completed
CL3217 | 2023-03-08 | Palladam 1 | D | Keypad installation for testing | Preventive | Gowtham | 2023-03-08 | - | Vadivelan Nagar keypad installed - Kept under observation - Completed
CL3218 | 2023-03-08 | Villapuram | A | Outlet going offline due to CPU maintenance | Preventive | Kathiresan | 2023-03-08 | - | CPU maintenance done - Outlet back online - Rectified
CL3219 | 2023-03-08 | Kodumudi | D | Nozzle retraction rope damage | Breakdown | Thirumalaisamy | 2023-03-08 | - | Nozzle retraction rope changed - Unloading training provided - Safety training provided - Resolved
CL3220 | 2023-03-08 | Neelambur | A | Automation maintenance | Preventive | Gowtham | 2023-03-08 | - | Automation maintenance done - Completed
CL3221 | 2023-03-08 | Ariyamangalam | D | D side old nozzle service and testing | Preventive | Nepolean | 2023-03-08 | - | Old nozzle serviced and tested - Testing : 2.34 Ltrs - Completed
CL3222 | 2023-03-08 | Kattupakkam | D | D side keypad replacing | Breakdown | Suneel Sagar | 2023-03-08 | - | Keypad replaced with new (Coimbatore keypad) - Resolved
CL3223 | 2023-03-09 | Chinnasalem | D | Dispensing pump problem | Breakdown | Prabu | 2023-03-09 | - | Dispensing pump unit replaced - Tank pressure 6 bar and Dispensing developing pressure 12.5 bar - Working fine - Rectified
CL3224 | 2023-03-09 | Palladam 1 | D | D nozzle leakage | Breakdown | Gowtham | 2023-03-09 | - | D nozzle serviced - Testing : 0.91 Ltr - Completed
CL3225 | 2023-03-09 | Dharapuram | G | Site visit | Preventive | Gowtham | 2023-03-09 | - | Site visit done - Completed
CL3226 | 2023-03-13 | Tiruchengode | T | Tank area vapour line ROV defect | Breakdown | Prabu | 2023-03-13 | - | Tank area vapour line ROV replaced - Working fine - Resolved
CL3227 | 2023-03-13 | Vedachandur | R | Servo stabilizer R phase carbon and winding rework | Breakdown | Kamaraj | 2023-03-13 | - | Servo stabilizer R phase carbon and winding rework done - Overload indicating randomly - Informed to Mothish
CL3228 | 2023-03-13 | Kumbakonam | C | DL stamping work | Certification | Nepolean & Dharmesh | 2023-03-13 | - | DL stamping done - A side Testing: 200.31 Ltrs B side Testing: 312.91 lit Total testing: 513.22 lit. K factory two side No changes. A side : 10100, B side : 10100. A side 10.00 = 9.99 lit B side 10.00 = 9.98 lit - Completed
CL3229 | 2023-03-13 | Sankari | T | ATG probe failure and Automation system maintenance | Breakdown | Prabu | 2023-03-13 | - | ATG probe cleaned and reconnected - Working fine - Automation maintenance done - Resolved
CL3230 | 2023-03-14 | Villapuram | D | B nozzle not working properly | Breakdown | Kathiresan | 2023-03-14 | - | Spare nozzle replaced - Testing : 0.90 Ltrs - Working fine - Rectified
CL3231 | 2023-03-14 | Ramnad | T | Unloading pump leakage | Breakdown | Kathiresan | 2023-03-14 | - | New O ring and bearing - Working fine - Unloading done without leakage - Kept under observation - Resolved
CL3232 | 2023-03-14 | T.V.Kovil | D | A side dispensing hose defect | Breakdown | Vigneshwaran | 2023-03-14 | - | 5m dispensing hose replaced with new one at A side - Testing : 2.18 Ltrs - Resolved
CL3233 | 2023-03-14 | Dharmapuri | G | Rat bite - DG to alternator wire | Breakdown | Prabu | 2023-03-14 | - | Reconnected the wire of alternator - DG RPM 1500 - R 231,Y 230, B 231, voltage - Dispensing motor spider replaced with new - Working fine - Rectified
CL3234 | 2023-03-14 | Ariyamangalam | R | Control panel dispensing air solenoid coil problem | Breakdown | Nepolean | 2023-03-14 | - | New air solenoid coil replaced - working fine - Resolved
CL3235 | 2023-03-15 | Avadi | T | Unloading hose ACME adapter leakage | Breakdown | Suneel Sagar | 2023-03-15 | - | Unloading hose ACME adapter leakage arrested by applying teflon - Unloading done - Completed
CL3236 | 2023-03-15 | Saravanampatty | R | DOL return signal not received | Breakdown | Gowtham | 2023-03-15 | - | R2 contactor NO contactor failure - Signal connected with another NO point - Working good - Rectified
CL3237 | 2023-03-15 | Ayothiyapattinam | D | Dispenser starts running immediately started dispensing | Breakdown | Prabu | 2023-03-15 | - | Dispenser diaphragm spring adjusted - Working fine - 9kg fire extinguisher hose replaced on 21.03.2023 - Resolved
CL3238 | 2023-03-15 | Attur | T | Tank area ball valve with ROV leakage | Breakdown | Prabu | 2023-03-15 | - | Ball valve with ROV leakage arrested by tightening the nut - Unloading liquid line 2" ballvalve replaced on 21.03.2023 - Completed
CL3239 | 2023-03-17 | Karur | C | Calibration and stamping work | Certification | Dharmesh & Thirumalaisamy | 2023-03-17 | - | Calibration and stamping done - Completed
CL3240 | 2023-03-17 | Ammapet | C | PESO inspection | Certification | Chandrasekar, Prabu & Avinash | 2023-03-17 | - | PESO inspection done - Completed
CL3241 | 2023-03-17 | Madurai 3 - Sivagangai Road | G | Office and EB room marking | New Project | Kathiresan | 2023-03-17 | - | Civil marking done - Attended
CL3242 | 2023-03-18 | Eral | R | Online UPS not working properly | Breakdown | Kathiresan | 2023-03-18 | - | New online UPS replaced - Working fine - Input power = 244 (v) Output power = 229 (v) Unloading point "50 NB" ball valve lpg leakage arrested by tightening the nut - Unloading training done - Resolved
CL3243 | 2023-03-18 | Perundurai | C | Calibration and stamping work | Certification | Dharmesh & Thirumalaisamy | 2023-03-18 | - | Calibration and stamping done - Dispensing motor bypass valve cleaned to resolve bypass valve noise - Dispenser both side retraction rope replaced with new - Automation maintenance done - Completed
CL3244 | 2023-03-18 | Mulanur | C | Calibration and stamping work | Certification | Dharmesh & Thirumalaisamy | 2023-03-18 | - | Calibration and stamping done - Dispenser bottom ball valve with ROV LPG leakage arrested by tightening the nut - Completed
CL3245 | 2023-03-18 | Karur | D | Batchen A side 5 Mtr dispensing hose leakage | Breakdown | Thirumalaisamy | 2023-03-18 | - | New 5 Mtr dispensing hose replaced - Working fine - Testing : 1.53 Ltrs - Resolved
CL3246 | 2023-03-19 | Ammapet | G | Outlet inauguration | New Project | Prakash, Madhavan, Prabu and Vigneshwaran | 2023-03-19 | - | Outlet opened to public Opening reading "A" side= 331.64 "B" side= 397.55 Tank = 42% - Attended
CL3247 | 2023-03-19 | Melur | D | Dispensing pressure not developed | Breakdown | Kathiresan | 2023-03-19 | - | Bypass valve cleaned - Pump unit reassembled to develop the pressure - K factor changed - "A" side old = 10100 "A" side New = 10150 "B" side old = 10070 "B" side New = 10150 Working fine - Rectified
CL3248 | 2023-03-19 | Renganathan Gas Bunk | G | Phase reverse problem | Breakdown | Pandi Durai | 2023-03-19 | - | Phase reverse rectified - Outlet working fine - Attended
CL3249 | 2023-03-20 | Dharapuram | T | Dispensing liquid line ROV replacing | Breakdown | Gowtham | 2023-03-20 | - | 2 ROV's replaced at dispensing liquid line - Spare air line provided from EB room to tank area - Completed
CL3250 | 2023-03-20 | Ammapet | C | Dispenser calibration and stamping work | Certification | Prabu | 2023-03-20 | - | Calibration and stamping done - Compressor and Dieser generator commissioned with respective service presons - All equipment working fine - Attended
CL3251 | 2023-03-21 | Mettupalayam | D | Nozzle hose leakage due to crimping damage | Breakdown | Gowtham | 2023-03-21 | - | B nozzle hose recrimping done - Leakage arrested - Rectified
CL3252 | 2023-03-21 | T.V.Kovil | D | Yenen C side 5m dispensing hose busted out | Breakdown | Dharmesh | 2023-03-21 | - | New 5 Mtr dispensing hose replaced - Working fine - Testing : 0.78 Ltrs - Unloading fill point 2" ball valve changed with new - Resolved
CL3253 | 2023-03-21 | Villapuram | D | High dispensing pressure - 15.5Kg | Breakdown | Kathiresan | 2023-03-21 | - | Dispensing bypass valve adjusted and equalizer valve adjusted to 13kg - Working fine - Rectified
CL3254 | 2023-03-22 | Kodumudi | A | Printer installation | Preventive | Thirumalaisamy | 2023-03-22 | - | Printer placed at dispensing area - Working fine - Completed
CL3255 | 2023-03-22 | Villapuram | D | B nozzle not working properly | Breakdown | Kathiresan | 2023-03-22 | - | New nozzle replaced - Totalizer reading : 878923.44 - Resolved
CL3256 | 2023-03-22 | Cantonment | D | D nozzle 5m dispensing hose leakage | Breakdown | Chandrasekar | 2023-03-22 | - | 5m dispensing hose replaced with new one at D side - Testing : 1.74 Ltrs - Resolved
CL3257 | 2023-03-22 | Namakkal 3 | G | Fire extinguisher Co2 - gas released automatically | Breakdown | Prabu | 2023-03-22 | - | Resolved temporarily - Co2 will be changed - Attended
CL3258 | 2023-03-23 | Salem | C | Dispenser calibration and stamping work | Certification | Dharmesh | 2023-03-23 | - | Stamping and calibration work done - Calibration reports : "A" side 10 ltrs = 9.98 "B" side 10 ltrs = 10.01 "K" Factor reports: "A" side 'K' factor = 101770 "B" side 'K' factor= 101770 Testing A side 171.26 B side 160.16 Total Testing : 331.42 Ltrs - PMR done - Completed
CL3259 | 2023-03-23 | Paramathivelur | T | ATG battery dead | Breakdown | Thirumalaisamy | 2023-03-23 | - | ATG 3V battery newly replaced - ATG working fine - Both nozzle hammer teeth replaced - Rectified
CL3260 | 2023-03-23 | Kattupakkam | D | D side DP valve diaphragm defect | Breakdown | Suneel Sagar | 2023-03-23 | - | DP valve diaphragm replaced with new - Completed
CL3261 | 2023-03-23 | T.V.Kovil | D | D nozzle 5m dispensing hose leakage | Breakdown | Avinash | 2023-03-23 | - | 5m dispensing hose replaced with new one at D side - Testing : 0.93 Ltrs - Resolved
CL3262 | 2023-03-23 | Madurai 3 - Sivagangai Road | C | FF Level and tank area marking | New Project | Kathiresan | 2023-03-23 | - | FF Level and tank area marking done - Completed
CL3263 | 2023-03-24 | Ammapet | T | Unloading and unloading training | Preventive | Prabu | 2023-03-24 | - | Unloading and Unloading training completed - PMR done - ATF working fine - Total area leakage checked - Attended
CL3264 | 2023-03-24 | Namakkal 1 | R | Offline UPS switch stuck up | Breakdown | Nivas | 2023-03-24 | - | Complaint registered with APC which will be sorted out with 4 working days - Attended
CL3265 | 2023-03-24 | Namakkal 3 | G | Fire extinguisher Co2 - gas released automatically | Preventive | Nivas | 2023-03-24 | - | 75 Kg fire extinguisher Co2 changed - Completed
CL3266 | 2023-03-25 | Perambalur | G | PNGRB - ERDMP mock drill | Preventive | Venkatesh, Prakash & Prasath | 2023-03-25 | - | Mock drill program completed - Attended
CL3267 | 2023-03-25 | Avadi | D | A nozzle teeth worn out | Breakdown | Suneel Sagar | 2023-03-25 | - | A nozzle hammer teeth replaced - Working fine - Resolved
CL3268 | 2023-03-26 | Udumalpet | D | Error 39 occurred due to Batchen EEPROM IC hanging | Breakdown | Gowtham | 2023-03-28 | 3 Days | Batchen dispenser factory reset and reprogramming done - Totalizer restarts from "0" - Testing : 1.29 Ltrs - Rectified
CL3269 | 2023-03-27 | Chinnasalem | R | Control panel drive display not working properly | Breakdown | Prabu | 2023-03-27 | - | Display replaced - Control panel indicator light changed - Rectified
CL3270 | 2023-03-27 | Velachery | D | D side EMT totalizer defect | Breakdown | Suneel Sagar | 2023-03-27 | - | EMT totalizer replaced with new - Resolved
CL3271 | 2023-03-27 | Ellis Nagar | G | Genset service | Breakdown | Kathiresan | 2023-03-27 | - | Genset general service done - Engine oil leakage arrested - Engine oil top up done - PMR done - Rectified
CL3272 | 2023-03-28 | Ammapet | G | Site visit | Preventive | Prabu | 2023-03-29 | - | EB supply connection done - Compressor and stabilizer working and dispensing motor, unloading motor direction checked - N2 machine connection done - Leakage test done - Completed
CL3273 | 2023-03-28 | Thuraiyur | C | Rule 19 work | Certification | Chandrasekar, Avinash, Prakash and Pandi Durai | 2023-03-30 | 36 Hours | Rule 19 done - New ATG installed - Sales started with automation - Working fine - Completed
CL3274 | 2023-03-29 | Tenkasi | T | Dispensing motor defect | Breakdown | Kathiresan | 2023-03-29 | - | Impeller refitting done - Kept under observation - PMR done - Unloading point 50 NB ball valve LPG leakage arrested - Rectified
CL3275 | 2023-03-29 | Palayam | T | Dispensing motor love joy coupling spider damage | Breakdown | Kamaraj | 2023-03-29 | - | Dispensing motor love joy coupling spider replaced - B side nozzle teeth 4 Nos replaced - Unloading solenoid coil cleaned - Automation maintenance done - Total leakage tested - Resolved
CL3276 | 2023-03-29 | Udumalpet | D | Motherboard EEPROM IC replacement | Breakdown | Gowtham | 2023-03-29 | - | EEPROM IC reassembled - Working fine - Tank 1 dispensing vapour ROV with ballvalve LPG leakage - Testing : 6.09 Ltrs - Completed
CL3277 | 2023-03-30 | Melur | D | Dispensing air hose damaged | Breakdown | Kathiresan | 2023-03-30 | - | Control panel to dispenser bottom and Control panel to tank area new pneumatic hose replaced - Dispenser bottom LPG leakage arrested - PMR done - Working fine - Rectified
CL3278 | 2023-03-30 | Devakottai | G | Fire extinguisher service | Preventive | Nivas | 2023-03-30 | - | Fire extinguisher service done - Attended
CL3279 | 2023-03-30 | T.V.Kovil | D | C nozzle front O ring defect | Breakdown | Dharmesh | 2023-03-30 | - | C nozzle front O ring replaced - Completed
CL3280 | 2023-03-30 | Namakkal 1 | T | Dispensing motor love joy coupling spider damage | Breakdown | Prabu | 2023-03-30 | - | Dispensing motor love joy coupling spider replaced - Automation maintenance done - Total leakage tested - Resolved
CL3281 | 2023-03-31 | Bathlagundu | T | ATG high - high problem | Breakdown | Kamaraj | 2023-03-31 | - | High - high signal cable reconnected to resolve the loose contact - Total leakage checked - PMR done - Rectified
CL3282 | 2023-03-31 | Ariyamangalam | D | 5m dispensing hose damaged | Breakdown | Nepolean | 2023-03-31 | - | New 5m dispensing hose replaced - No leakage found - Working fine - Resolved
CL3283 | 2023-04-01 | Avinashi | D | Batchen dispenser metering unit LPG leakage due to bearing and seal kit failure | Breakdown | Gowtham & Nepolean | 2023-04-06 | B side sales stopped | LPG leakage arrested by replacing bearing and sealkit - Kept under observation - B side testing : 48.82 Ltrs - Resolved
CL3284 | 2023-04-01 | Hosur | D | A and B nozzle teeth problem | Breakdown | Suresh | 2023-04-01 | - | Both side nozzle teeth 4 nos replaced - Working fine - Rectified
CL3285 | 2023-04-01 | Thuraiyur | G | Fire extinguisher service | Preventive | Pandi Durai | 2023-04-01 | - | 75 Kg fire extinguisher Co2 changed - Powder refilling done - Fire safety training provided - Completed
CL3286 | 2023-04-02 | Mettupalayam | T | ATG cable damage due to rat bite | Breakdown | Gowtham | 2023-04-02 | - | Cable serviced and reconnected - ATG working fine - Resolved
CL3287 | 2023-04-03 | T.V.Kovil | A | Dispenser going offline due to CPU issue | Breakdown | Madhavan | 2023-04-03 | - | CPU cabin replaced - Dispenser back online - Rectified
CL3288 | 2023-04-03 | Bodi | G | Unloading training | Preventive | Kamaraj | 2023-04-03 | - | Unloading training provided - Unloading solenoid coil cleaned - Attended
CL3289 | 2023-04-03 | Ayothiyapattinam | D | Dispenser keypads not working properly | Breakdown | Prabu | 2023-04-03 | - | Both side keypad changed - Working fine - Completed
CL3290 | 2023-04-04 | Virudhunagar | D | A nozzle LPG leakage | Breakdown | Kathiresan | 2023-04-04 | - | A nozzle hammer teeth 4 Nos replaced - PMR done - Working fine - Resolved
CL3291 | 2023-04-04 | Palladam 1 | D | Motherboard Error 39 occurred | Breakdown | Nepolean | 2023-04-05 | 5 Hours | Dispenser motherboard EPROM IC reprogrammed - Working fine - A side testing : 44.58 Ltrs - B side Testing : 82.87 Ltrs - Rectified
CL3292 | 2023-04-04 | Ariyamangalam | D | C side 5m dispensing hose damaged | Breakdown | Pandi Durai | 2023-04-04 | - | C side 5m dispensing hose replaced - Testing : 0.72 Ltrs - Rectified
CL3293 | 2023-04-04 | T.V.Kovil | D | Batchen B side 5m dispensing hose damaged | Breakdown | Dharmesh | 2023-04-04 | - | Batchen B side 5m dispensing hose replaced - Testing : 1.22 Ltrs - Rectified
CL3294 | 2023-04-05 | Palayam | G | EB power supply problem | Breakdown | Kamaraj | 2023-04-05 | - | EB service person attended - All 3 phases working fine - VFD Working good - Attended
CL3295 | 2023-04-05 | Chengalpattu | R | Output panel booting problem due to online UPS problem | Breakdown | Suneel Sagar | 2023-04-21 | - | Online UPS bypassed and sales started in manual mode - Automation back online at 06.04.2023 - New online UPS installed - Working fine - Rectified
CL3296 | 2023-04-06 | T.V.Kovil | G | New chemical earth installation | Preventive | Avinash | 2023-04-06 | - | Chemical earth 2 nos installed - Dispenser C side spare nozzle replaced - Testing : 89 Ltrs - Completed
CL3297 | 2023-04-07 | Manapparai | T | Unloading motor belt defect | Breakdown | Nepolean | 2023-04-08 | - | Unloading motor belt replaced - Rectified
CL3298 | 2023-04-08 | Karur | D | Batchen dispenser metering unit LPG leakage due to bearing and seal kit failure | Breakdown | Nepolean | 2023-04-08 | - | Metering unit bearing and seal kit replaced - Leakage arrested - Resolved
CL3299 | 2023-04-08 | Tharamangalam | D | A nozzle leakage due to teeth problem | Breakdown | Prabu | 2023-04-08 | - | Nozzle hammer teeth 4 Nos replaced at A nozzle - B nozzle rope changed due to damage - Unloading cut off checked - Automation maintenance done - Working good - Rectified
CL3300 | 2023-04-08 | Uthamasolapuram | D | A nozzle lock missing | Breakdown | Prabu | 2023-04-08 | 6 Hours (A Nozzle) | Nozzle lock fitted - Working fine - Resolved
CL3301 | 2023-04-09 | Ellis Nagar | G | EB B phase shortcircuited | Breakdown | Kathiresan | 2023-04-09 | - | Cable leg replaced - Working good - Rectified
CL3302 | 2023-04-09 | Rasipuram | D | A side keypad defect and display not working properly | Breakdown | Prabu | 2023-04-09 | - | A side keypad 1 no replaced - Display cable reconnected - Working fine - Resolved
CL3303 | 2023-04-10 | Velachery | D | D side keypad defect | Breakdown | Suneel Sagar | 2023-04-10 | - | Keypad replaced with new - Resolved
CL3304 | 2023-04-10 | Kattupakkam | D | Button type keypad installation | Preventive | Suneel Sagar | 2023-04-10 | - | Button type keypad installed at B side for trial - Completed
CL3305 | 2023-04-11 | Tiruchengode | G | Unloading training | Preventive | Prabu | 2023-04-11 | - | Unloading training provided - Attended
CL3306 | 2023-04-11 | Vellakovil | G | Unloading training | Preventive | Thirumalaisamy | 2023-04-11 | - | Unloading training provided - Attended
CL3307 | 2023-04-11 | Avadi | D | C and D nozzle hangs frequently | Breakdown | Suneel Sagar | 2023-04-11 | - | On/Off switch refitted - Kept under observation - Resolved
CL3308 | 2023-04-11 | Velachery | D | Dispsenser 2 hangs frequently and totalizer became zero due to D side keypad defect | Breakdown | Suneel Sagar | 2023-04-11 | - | D side keypad replaced by spare - Under observation - Rectified
CL3309 | 2023-04-11 | Velachery | D | Sales stopped at D side due to dispenser hanging for observation | Breakdown | Suneel Sagar | 2023-04-11 | 12 Hours (D Nozzle) | Found the root cause of dispenser hangine - Keypad replaced - Working fine - Resolved
CL3310 | 2023-04-11 | Villapuram | T | Dispensing motor love joy coupling spider damage | Breakdown | Kathiresan | 2023-04-11 | - | Love joy coupling spider interchanged - Working fine - Resolved
CL3311 | 2023-04-12 | T.V.Kovil | R | Control panel replacement | Preventive | Prakash | 2023-04-12 | - | New double tank PLC panel replaced - Working fine - Completed
CL3312 | 2023-04-12 | Perundurai | A | Dispenser gone offline due to CPU not working | Breakdown | Thirumalaisamy | 2023-04-12 | - | 1KVa online UPS battery 3 Nos replaced due to defect - CPU service done - Dispenser back online - Rectified
CL3313 | 2023-04-13 | Devakottai | G | Outlet inauguration and commissioning work | New Project | Prakash, Vigneshwaran, Kathiresan, Chandrasekar, Pandi Durai & Dharmesh | 2023-04-14 | - | Commissioning done - All equipment working checked - Dispenser stamping done on 13.04.2023 - Outlet opened to public - Completed
CL3314 | 2023-04-13 | Mulanur | D | A and B nozzles LPG leakage | Breakdown | Thirumalaisamy | 2023-04-13 | - | A and B nozzle hammer teeth replaced - PMR done - Automation maintenance done - Working fine - Resolved
CL3315 | 2023-04-13 | Salem | D | A nozzle product jumping | Breakdown | Prabu | 2023-04-13 | - | Solenoid coil replaced withour our concurrence - Total testing : 27.47 Ltrs
CL3316 | 2023-04-13 | Salem | D | A nozzle product jumping | Breakdown | Prabu | 2023-04-13 | - | High flow low flow solenoid valve cleaned - Under observation - Testing : 123.43 Ltrs - Resolved
CL3317 | 2023-04-13 | Kodumudi | A | Printer power cable damaged due to rat bite | Breakdown | Thirumalaisamy | 2023-04-13 | - | Printer wire serviced and reconnected - working fine - Resolved
CL3318 | 2023-04-14 | Velachery | D | B side point jumping complaint | Breakdown | Suneel Sagar | 2023-04-14 | - | Filter cleaned - Preset working - Kept under observation - Rectified
CL3319 | 2023-04-14 | Devakottai | A | Automation installation | New Project | Madhavan | 2023-04-14 | - | Automation installed and data available online in KR admin app - Completed
CL3320 | 2023-04-14 | Dharmapuri | D | B side pressure gauge leakage | Breakdown | Prabu | 2023-04-14 | - | Leakage arrested by refitting - Damaged nozzle rope replaced - Testing A side : 10 Ltrs and B side : 10 Ltrs - Resolved
CL3321 | 2023-04-15 | Attur | D | A nozzle product jumping | Breakdown | Prabu | 2023-04-15 | - | High flow low flow solenoid valve cleaned - A side display cable wiring reconnected - Testing : 14.34 Ltrs - Working fine - Rectified
CL3322 | 2023-04-16 | Villapuram | D | Dispenser A and B side retraction rope damaged | Breakdown | Kathiresan | 2023-04-16 | - | Both side retraction rope replaced - Tank area damaged dispensing air hose changed - Working fine - Resolved
CL3323 | 2023-04-16 | Devakottai | D | Site visit | New Project | Pandi Durai | 2023-04-16 | - | All equipments working fine - No leakage found - Master data collected - Completed
CL3324 | 2023-04-17 | Ammapet | G | Unloading and unloading training | Preventive | Prabu | 2023-04-17 | - | Unloading done - Unloading training provided - HLA and ATG working fine - Tank area leakage checked - Attended
CL3325 | 2023-04-17 | Hosur | G | Fire extinguisher service | Preventive | Suresh | 2023-04-17 | - | Fire extinguisher 75kg, 9kg and Co2 serviced - Fire safety training done - Attended
CL3326 | 2023-04-18 | Bathlagundu | c | Calibration and stamping work | Certification | Vigneshwaran | 2023-04-18 | - | Calibration and stamping work done - A side yenen keypad 1 No replaced - Resolved
CL3327 | 2023-04-18 | Udumalpet | G | Site visit | Preventive | Gowtham | 2023-04-18 | - | General check and leakage completed - Unloading air hose partially replaced - Site visit done - Completed
CL3328 | 2023-04-18 | Paramathivelur | D | B nozzle 5m dispensing hose damaged | Breakdown | Thirumalaisamy | 2023-04-18 | - | 5m dispensing hose replaced - Compressor oil replaced - Automation maintenance done - Completed
CL3329 | 2023-04-18 | Avadi | G | Fire extinguisher service | Preventive | Suneel Sagar | 2023-04-18 | - | Fire extinguisher 75kg, 9kg and Co2 serviced - Fire safety training done - Attended
CL3330 | 2023-04-18 | Uthamasolapuram | D | A side nozzle and hose draged by customer car due to pump staff carelessness | Breakdown | Prabu | 2023-04-18 | 20 Mins (A nozzle) | Nozzle hoses and ropes reconnected - Working fine - Testing : 0.82 Ltrs - Resolved
CL3331 | 2023-04-19 | Musiri | C | Stamping work | Certification | Nepolean and Dharmesh | 2023-04-19 | - | DL stamping done - K factor : A side : 10200 B side ; 10200 Testing: A side : 153.64 Ltrs B side: 157.62 Ltrs Control panel master solenoid coil cleaned and refitted to arrest the air leakage - Completed
CL3332 | 2023-04-19 | Thuraiyur | C | Stamping work | Certification | Nepolean and Dharmesh | 2023-04-19 | - | DL stamping done - A side : 101600 B side : 104000 New k factor: A side : 101600 B side : 100000 Testing: A side : 162.88 lit B side : 421.15 lit - Completed
CL3333 | 2023-04-19 | Thiruvaiyaru | G | Dispensing pump and motor not working in genset mode | Breakdown | Chandrasekar | 2023-04-19 | - | Genset voltage settings changed - Motor working in genset mode - Rectified
CL3334 | 2023-04-19 | Rasipuram | R | Control panel not working porperly | Breakdown | Prabu | 2023-04-19 | - | Wiring reconnected completely - Kept under observation - A side keypad 1 No replaced - Working fine - Resolved
CL3335 | 2023-04-19 | Vadivelan Nagar | G | Fire extinguisher service | Preventive | Suneel Sagar | 2023-04-19 | - | New 9kg ABC fire extinguishers 2 Nos replaced - 75Kg extinguisher hose replaced - Completed
CL3336 | 2023-04-19 | Saravanampatty | T | Unloading vapour ball valve LPG leakage | Breakdown | Gowtham | 2023-04-19 | - | Ball valve leakage arrested by tightening the nut - Rectified
CL3337 | 2023-04-19 | T.V.Kovil | D | B side nozzle on/off switch defect | Breakdown | Vigneshwaran | 2023-04-19 | - | B side nozzle on/off switch replaced - Working fine - Testing : 2.12 Ltrs - Resolved
CL3338 | 2023-04-19 | Avinashi | D | A nozzle slow delivery | Breakdown | Gowtham | 2023-04-19 | - | Plunger cleaned and angular valve adjusted to increase the flow of LPG - Found satisfactory - Resolved
CL3339 | 2023-04-20 | Virudhunagar | C | Calibration and stamping work | Certification | Dharmesh and Kathiresan | 2023-04-20 | - | Calibration and stamping done - " K" factor no changes. "A" side = 10200 "B" side = 10200 Calibration reports: "A" side 10 ltrs = 9.95 "B" side 10 ltrs = 9.93 Testing reports : "A" side = 191.84 "B" side = 159.68 Total testing = 351.52 ltrs Compressor pressure switch replaced - Working fine - Completed
CL3340 | 2023-04-20 | Krishnagiri | D | Dispenser A side 5m dispensing hose damaged | Breakdown | Prabu | 2023-04-20 | - | Dispenser A nozzle 5m dispensing hose replaced - Tank area vapour line ROV replaced due to leakage - Unloading and unloading training done - A side Testing : 1.76 Ltrs - Completed
CL3341 | 2023-04-20 | Thuraiyur | A | Automation installation | New Project | Madhavan, Prakash, Nepolean and Chandrasekar | 2023-04-20 | - | Outlet automated and data available in KR admin app - Completed
CL3342 | 2023-04-20 | Melur | C | Recalibration work | Certification | Dharmesh and Kathiresan | 2023-04-20 | - | Recalibration done - New K factor "A" side Old 'K' = 10150 "A" side New'K' = 10180 "B" side Old 'K' = 10150 "B" side New'K' = 10180 Testing : "A" side = 582.63 "B" side = 298.50 Total = 881.13 ltrs Tank area dispensing line air hose changed - Online UPS error 57 resolved - Under observation - Completed
CL3343 | 2023-04-21 | T.V.Kovil | D | A nozzle leakage due to teeth problem | Breakdown | Vigneshwaran | 2023-04-21 | - | A nozzle hammer teeth 4 Nos replaced - Working fine - Resolved
CL3344 | 2023-04-21 | Thuraiyur | A | Automation training | Preventive | Nivas | 2023-04-21 | - | Automation training provided - Unloading liquid ball valve LPG leakage arrested by tightening the nut - Working fine - Rectified
CL3345 | 2023-04-22 | Tiruchengode | A | Dispenser went offline due to RS485 to USB converter board worn out of power fluctuation | Breakdown | Prabu | 2023-04-22 | - | RS485 to USB converter board spare board replaced - Communication wire reconnected - Automation maintenance done - Dispenser back online - Working fine - Resolved
CL3346 | 2023-04-22 | Sulur | T | Unloading motor not working due to phase reverse and OLR relay tripped to Manual mode | Breakdown | Gowtham | 2023-04-22 | - | Phase interchanged - OLR relay changed to auto mode - Working good - Completed
CL3347 | 2023-04-22 | Avadi | D | Dispenser A and B side on/off switch defect | Breakdown | Suneel Sagar | 2023-04-22 | - | Both side on/off switch replaced by new - All 4 nozzles in operation - Rectified
CL3348 | 2023-04-22 | Villapuram | D | A nozzle LPG leakage | Breakdown | Kathiresan | 2023-04-22 | - | Nozzla hammer teeth 4 nos and front O ring replaced - Leakage arrested - Working fine - Resolved
CL3349 | 2023-04-23 | Devakottai | G | Unloading work | Preventive | Chandrasekar | 2023-04-23 | - | Unloading done - All area leakage checked - EB power alarm bell fitted - Completed
CL3350 | 2023-04-23 | Tenkasi | R | Control panel not working due to voltage scanner relay defect | Breakdown | Kathiresan | 2023-04-24 | 3.45 Hours | VSR bypassed which is to be replaced - Control panel booted - Dispensing line 40 NB ball valve LPG leakage arrested by tightening the nut and teflon applied - Rectified temporarily
CL3351 | 2023-04-24 | Uthamapalayam | G | Canopy and Facia light SMPS defect | Breakdown | Kamaraj | 2023-04-24 | - | New SMPS replaced - Working fine - Dispensing motor spider replaced - General check up done - Completed
CL3352 | 2023-04-24 | Avinashi | T | Motor spider damaged | Breakdown | Gowtham | 2023-04-24 | - | Spider replaced - pump with motor working fine - Rectified
CL3353 | 2023-04-25 | Tirunelveli | D | Dispensing pressure dropped | Breakdown | Kathiresan | 2023-04-25 | - | Pressure valve adjusted to increase the pressure - Automation wiring reconnected - STP turbo drive panel connection checked and pressure is 12kg - Dispenser working fine - Under observation - Resolved
CL3354 | 2023-04-25 | Kattupakkam | T | Tank 2 dispensing liquid ROV stuck up | Breakdown | Suneel Sagar | 2023-04-25 | - | ROV replaced - Working fine - Resolved
CL3355 | 2023-04-26 | Ayothiyapattinam | D | Dispenser display not visible due to water droplets formed inside the display | Breakdown | Prabu | 2023-04-26 | - | Water droplets cleaned - Reconnected dispenser cables - Kept under observation - Working fine - Rectified
CL3356 | 2023-04-26 | Villapuram | G | sales stopped Meenakshi Amman arrival near pump | Preventive | Kathiresan | 2023-04-26 | 4 Hours | Sales started - Completed
CL3357 | 2023-04-27 | Saravanampatty | C | Rule 19 work | Certification | Prakash, Dharmesh, Chandrasekar, Pandi Durai & Gowtham | 2023-04-29 | 1.5 Days | Rule 19 done - Sales started with automation - Working fine - Completed
CL3358 | 2023-04-27 | Tirunelveli | D | Dispensing auto cut off problem | Breakdown | Kathiresan | 2023-04-27 | - | Dispenser flow rating valve adjusted - Kept under observation for 2 days - Working fine - Tank 1 dispensing vapour line 40NB ball valve LPG leakage arrested by tightening the nut and teflon applied - Working good - Rectified
CL3359 | 2023-04-27 | Erode | G | Compressor pressure switch NRV air leakage | Breakdown | Thirumalaisamy | 2023-04-27 | - | Pressure switch ordered in Frank - Pump running in alternate compressor - Unloading vapour ball valve with ROV LPG leakage arrested by tightening the nut and teflon appiled - Tanker earth wire new leg replaced - Control panel RY indicator light changed - Automation maintenance done - Resolved
CL3360 | 2023-04-28 | Rasipuram | R | Control panel not working properly | Breakdown | Prabu | 2023-04-28 | - | Control panel transformer fuse 1 no replaced - Transformer input voltage changed to 400V - Control panel working fine - Rectified
CL3361 | 2023-04-28 | Velachery | T | Unloading front vapour ROV with ballvalve gland package leakage | Breakdown | Suneel Sagar | 2023-04-28 | - | ROV with ballvalve gland package leakage arrested by teflon applied - Rectified
CL3362 | 2023-04-28 | Tirunelveli | D | A side keypad defect | Breakdown | Kathiresan | 2023-04-28 | - | Keypads interchanged - Working fine - Dipenser cutoff is under observation - Working fine - Completed
CL3363 | 2023-04-28 | Eral | G | Safety bollard installation | Preventive | Kathiresan | 2023-04-28 | - | Dispenser area safety bollard installed - Total leakage tested - Dispenser bottom ROV leakage arrested by tightening the nut - Resolved
CL3364 | 2023-04-29 | Thiruvaiyaru | D | Dispenser B side metering unit noise | Breakdown | Nepolean | 2023-04-29 | - | Angle needle valve adjusted - Noise arrested - Under observation - Rectified
CL3365 | 2023-04-29 | Chinnasalem | G | Canopy light flickering | Breakdown | Prabu | 2023-04-29 | - | Light flickering adjusted - Automation, UPS and compressor oil maintenance done - Attended
CL3366 | 2023-04-30 | Udumalpet | T | Cathodic protection checking | Preventive | Gowtham | 2023-04-30 | - | Cathodic protection checked by new portable electrode along with CP technician - Rule 19 material list noted - Pump love joy coupling spider replaced - Completed
CL3367 | 2023-04-30 | Avinashi | T | Cathodic protection checking | Preventive | Gowtham | 2023-04-30 | - | Cathodic protection checked by new portable electrode along with CP technician - Rule 19 material list noted - Completed
CL3368 | 2023-05-01 | Thiruvaiyaru | D | Batchen dispenser B side metering unit problem | Breakdown | Nepolean | 2023-05-01 | - | B side bearing and oil seal kit replaced with new - Working fine - Kept under observation - Testing B side : 57.55 Ltrs - Rectified
CL3369 | 2023-05-01 | Namakkal 3 | T | Tank area dispensing line ROV inside leakage | Breakdown | Prabu | 2023-05-01 | - | ROV interchanged with unloading line - Working fine - Attended
CL3370 | 2023-05-01 | Manapparai | A | Mobile network problem | Breakdown | Chandrasekar | 2023-05-01 | - | New TP Link installed - B side new keypad replaced - Network working fine - Resolved
CL3371 | 2023-05-01 | Villapuram | R | Offline UPS battery output voltage problem | Breakdown | Kathiresan | 2023-05-03 | - | UPS battery 2 Nos replaced - Working fine - Rectified
CL3372 | 2023-05-01 | Eral | A | Dispenser going offline due to RS485 to USB converter board defect | Breakdown | Kathiresan | 2023-05-01 | - | Automation cables and RS485 to USB converter board replaced - Working fine - Dispenser back online - Completed
CL3373 | 2023-05-02 | Vellakovil | D | Batchen dispenser B side slow delivery | Breakdown | Thirumalaisamy | 2023-05-02 | - | B side solenoid valve high flow low flow coil cleaned - Testing : 10 Ltrs - Working fine - Rectified
CL3374 | 2023-05-02 | Cantonment | D | B nozzle 5m dispensing hose damaged | Breakdown | Chandrasekar | 2023-05-02 | - | New 5m dispensing hose replaced - No leakage found - B side Testing : 1.10 Ltrs - Working fine - Resolved
CL3375 | 2023-05-02 | Vedachandur | D | Dispenser to control panel air hose damaged | Breakdown | Kamaraj | 2023-05-02 | - | Dispenser to control panel air hose replaced - General check up done - Rectified
CL3376 | 2023-05-02 | Kattupakkam | D | Differential pressure valve spring damage at D side | Breakdown | Suneel Sagar | 2023-05-02 | - | Differential pressure valve spring changed - Working fine - Attended
CL3377 | 2023-05-02 | Ariyamangalam | D | B and D side nozzle teeth damage | Breakdown | Nepolean | 2023-05-02 | - | 4 hammer teeth replaced each side - Working fine - Resolved
CL3378 | 2023-05-02 | Karur | D | D nozzle swirl broken | Breakdown | Thirumalaisamy | 2023-05-02 | - | Spare nozzle replaced - Working good - Testing : 0.89 Ltrs - Rectified
CL3379 | 2023-05-03 | Tiruchengode | G | Compressor oil leakage due to glass damage | Breakdown | Prabu | 2023-05-03 | - | Glass replaced - Oil changed for both compressors - Unloading done - Completed
CL3380 | 2023-05-04 | Ariyamangalam | D | B nozzle leakage | Breakdown | Nivas | 2023-05-04 | - | Spare nozzle replaced - Testing : 1.10 Ltrs - Working fine - Rectified
CL3381 | 2023-05-05 | Thuraiyur | D | B side on/off switch not working properly | Breakdown | Nivas | 2023-05-05 | - | On/Off switch cleaned and refitted - Unloading liquid line 1 1/2" ball valve with ROV LPG leakage arrested by applying teflon and tightening the nut - Testing : 1 Ltr - Resolved
CL3382 | 2023-05-05 | Erode | G | Compressor pressure switch NRV air leakage | Breakdown | Thirumalaisamy | 2023-05-05 | - | Compressor pressure switch with NRV replaced with new - Rectified
CL3383 | 2023-05-05 | Rasipuram | R | Control panel not working properly | Breakdown | Prabu | 2023-05-05 | - | Changeover and MCB refitted - Kept under observation - Resolved
CL3384 | 2023-05-06 | Thanjavur | T | Unloading work | Preventive | Pandi Durai | 2023-05-06 | - | Unloading done - Completed
CL3385 | 2023-05-06 | Ariyamangalam | A | Dispenser going offline due to automation equipment maintenance | Breakdown | Madhavan | 2023-05-06 | - | Maintenance done - Dispenser back online - Completed
CL3386 | 2023-05-06 | T.V.Kovil | G | Compressor oil changing | Preventive | Vigneshwaran | 2023-05-06 | - | Oil changed for both compressors - Attended
CL3387 | 2023-05-07 | Cantonment | D | F side keypad defect | Breakdown | Chandrasekar | 2023-05-07 | - | New keypad replaced - Working fine - Resolved
CL3388 | 2023-05-08 | Tenkasi | T | Dispensing motor defect | Breakdown | Kathiresan | 2023-05-08 | - | Dispensing motor pump alignment done - Impeller refitted - Completed pump reassembled - Rectified
CL3389 | 2023-05-08 | Dharmapuri | G | Safety bollard installation | Preventive | Prabu | 2023-05-08 | - | Bollard installation done - Total leakage tested - Completed
CL3390 | 2023-05-08 | Kodumudi | G | Fire extinguisher service | Preventive | Thirumalaisamy | 2023-05-08 | - | Fire extinguisher service done - Fire and safety training provided to pump staffs - Attended
CL3391 | 2023-05-08 | Aravakurichi | G | Fire extinguisher service | Preventive | Thirumalaisamy | 2023-05-08 | - | 2 nos of 75 kg and CO2 fire extinguishers serviced - 2 nos of ABC 9 kg fire extinguishers provided - Fire and safety training provided to pump staffs - Attended
CL3392 | 2023-05-08 | Palayam | G | Fire extinguisher service | Preventive | Thirumalaisamy | 2023-05-08 | - | 75kg CO2 cylinder replaced - 1 no of ABC 9 kg fire extinguisher provided - Fire and safety training provided to pump staffs - Attended
CL3393 | 2023-05-08 | Chengalpattu | G | Site visit | Preventive | Suneel Sagar | 2023-05-08 | - | General check up done - Attended
CL3394 | 2023-05-09 | T.V.Kovil | C | DL stamping work | Certification | Nepolean | 2023-05-09 | - | DL stamping done - Testing: A side : 150.12 lit B side : 535.77 lit C side: 150.02 lit D side: 149.91lit Total: 985.82 lit. Old k factor: A side : 100360 B side: 100840 C side: 10100 D side: 10000. New k factor: A side: 100360 B side: 101000 C side: 10100 D side: 10000. B side only k factor changed. A side 10 lit- 9.97 lit B side. 10lit - 9.99 lit C side 10 lit - 9.98 lit D side 10 lit - 10.04 lit - Completed
CL3395 | 2023-05-09 | Namakkal 1 | A | RS485 to USB converter board damaged due to rain fall and thunder | Breakdown | Prabu | 2023-05-09 | - | New RS 485 to USB converter board replaced - Dispenser working online - Resolved
CL3396 | 2023-05-10 | Manapparai | A | Automation CPU maintenance | Preventive | Chandrasekar | 2023-05-10 | - | Automation maintenance done - Completed
CL3397 | 2023-05-10 | Devakottai | G | Service road cheveron marking | Preventive | Avinash | 2023-05-10 | - | Cheveron marking done - Attended
CL3398 | 2023-05-10 | Velachery | T | Fill point indicator not working | Breakdown | Suneel Sagar | 2023-05-10 | - | Fill point indicator cleaned and reassembled - Working fine - Rectified
CL3399 | 2023-05-11 | Tiruchengode | T | Unloading and automation maintenance | Preventive | Prabu | 2023-05-11 | - | Unloading done - Automation and UPS maintenance done - Completed
CL3400 | 2023-05-11 | Ariyamangalam | G | Mass flow meter testing at D side | Preventive | Nepolean | 2023-05-11 | - | Endress+Hauser Mass flow meter tested at D side - Testing : 48.01 Ltrs - Completed
CL3401 | 2023-05-12 | Uthamapalayam | G | Camera not working at dispensing side | Breakdown | Kamaraj | 2023-05-12 | - | Camera cable replaced - Working fine - Rectified
CL3402 | 2023-05-12 | Namakkal 3 | T | Tank area vapour line ROV leakage | Breakdown | Prabu | 2023-05-12 | - | ROV serviced from Vamaja and refitted - Total leakage test done - Control panel working in genset mode - EB phase problem rectified after 16 hours - Resolved
CL3403 | 2023-05-12 | Ellis Nagar | D | A keypad not working | Breakdown | Kathiresan | 2023-05-15 | - | Interchanged with B side keypad on 12.05.2023 - B keypad to be replaced - New keypad replaced at B side - Working fine - Completed
CL3404 | 2023-05-13 | Tharamangalam | D | Error E10 occurred | Breakdown | Thirumalaisamy | 2023-05-13 | 4.15 Hours | Dispenser restarted to clear the error E10 - Hang up cleared - Kept under observation - Resolved
CL3405 | 2023-05-13 | Cantonment | G | Compressor oil replacing | Preventive | Chandrasekar | 2023-05-13 | - | Oil changed for both compressors - Attended
CL3406 | 2023-05-13 | Villapuram | D | C nozzle leakage | Breakdown | Kathiresan | 2023-05-13 | - | Nozzle teeth 4 nos replaced - Front O ring changed - Working fine - Rectified
CL3407 | 2023-05-15 | Hosur | D | A side keypad problem | Breakdown | Suresh | 2023-05-15 | - | Keypad replaced with new - Working good - Completed
CL3408 | 2023-05-16 | Thuraiyur | T | Unloading liquid and vapour line ballvalve with ROV LPG leakage | Breakdown | Nivas | 2023-05-16 | - | Ball valve with ROV LPG leakage arrested by tightening the nut and teflon applied - Resolved
CL3409 | 2023-05-16 | Virudhunagar | G | Solar power not working | Breakdown | Kathiresan | 2023-05-16 | - | Solar power inverter relay and PCB wiring refitted - Changeover switch serviced - Working fine - Automation maintenance done - Rectified
CL3410 | 2023-05-16 | Sankari | D | Nozzle leakage at both side | Breakdown | Prabu | 2023-05-16 | - | 6 nos of nozzle hammer teeth and rubber bush replaced - Working fine - Dispensing motor cooling to be replaced - Resolved
CL3411 | 2023-05-17 | Sankari | G | Fire extinguisher pressure decreased | Breakdown | Prabu | 2023-05-19 | - | 9 kg fire extinguisher 1 no replaced - Working fine - Rectified
CL3412 | 2023-05-17 | Namakkal 3 | G | 10 kg DCP fire extinguisher pressure decreased to zero | Breakdown | Krishna Bhalaji | 2023-05-17 | - | 10 kg DCP fire extinguisher replaced from Namakkal 2 - Resolved
CL3413 | 2023-05-17 | Ariyamangalam | D | A nozzle On/Off switch problem | Breakdown | Nepolean | 2023-05-17 | - | On/off switch replaced with new - Working fine - C nozzle hammer teeth 4 nos replaced - Rectified
CL3414 | 2023-05-19 | Ramnad | A | Dispenser going offline due to automation jerking issue | Breakdown | Kathiresan | 2023-05-19 | - | Permission updated at database - Dispenser back online - Resolved
CL3415 | 2023-05-19 | Aravakurichi | A | Dispenser going offline due to automation system CPU heating issue | Breakdown | Thirumalaisamy | 2023-05-19 | - | CPU serviced - Outlet back online - Kept under observation - Automation equipement maintenance done - Compressor oil changed - ATG 3V battery changed with new - Resolved
CL3416 | 2023-05-19 | Chinnasalem | G | Fire extinguisher service | Preventive | Prabu | 2023-05-19 | - | Fire extinguisher service done - Fire and safety training provided to pump staffs - Attended
CL3417 | 2023-05-19 | Velachery | T | Fill point indicator not working properly | Breakdown | Suneel Sagar | 2023-05-19 | - | Fill point indicator DIS-50 refixed properly - ATG shows tank levels - Working fine - Rectified
CL3418 | 2023-05-19 | Virudhunagar | G | Genset program key set alteration | Preventive | Kathiresan | 2023-05-19 | - | Genset program key set alteration done - Panel wiring changed - On/off push button replaced - Genset emergency switch element replaced - Working fine - Completed
CL3419 | 2023-05-19 | Attur | G | Fire extinguisher service and Training | Preventive | Prabu | 2023-05-19 | - | Fire extinguisher service done - Fire and safety training provided to pump staffs - Attended
CL3420 | 2023-05-20 | Chengalpattu | C | Stamping and calibration work | Certification | Chandrasekar and Dharmesh | 2023-05-20 | - | Calibration and stamping done "A" side 10 ltrs = 9.93 "B" side 10 ltrs = 9.94 "K" Factor reports: "A" side 'K' factor = 10040 "B" side 'K' factor= 10010 K factor no change Testing A side - 152.68 B side - 192.63 Total testing - 345.31 - Completed
CL3421 | 2023-05-20 | Avinashi | G | Fire extinguisher service and Training | Preventive | Gowtham | 2023-05-20 | 4.30 pm to 5.30 pm | Fire extinguisher service done - Fire and safety training provided to pump staffs - New 10kg ABC fire extinguishers provided - Outlet panel and stabilizer affected by power surge - Rebooted both the equipments - Working fine - Attended
CL3422 | 2023-05-20 | Neelambur | G | Fire extinguisher service and Training | Preventive | Gowtham | 2023-05-20 | - | Fire extinguisher service done - Fire and safety training provided to pump staffs - Attended
CL3423 | 2023-05-20 | Palladam 1 | G | Fire extinguisher service and Training | Preventive | Gowtham | 2023-05-20 | - | Fire extinguisher service done - Fire and safety training provided to pump staffs - New 10kg ABC fire extinguishers provided -Attended
CL3424 | 2023-05-20 | Palladam 2 | G | Fire extinguisher service and Training | Preventive | Gowtham | 2023-05-20 | - | Fire extinguisher service done - Fire and safety training provided to pump staffs - Attended
CL3425 | 2023-05-20 | Hosur | D | Dispenser B side diaphragm defect | Breakdown | Prabu | 2023-05-20 | 4 Hours (B side) | New diaphragm replaced at B side - Working good - Testing : 6.41 Ltrs - Resolved
CL3426 | 2023-05-20 | Ariyamangalam | D | Dispenser 1 LED light defect and on/off switch not working | Breakdown | Nepolean | 2023-05-20 | - | LED light replaced and on/off switch replaced - Working fine - Completed
CL3427 | 2023-05-20 | Avadi | C | Stamping and calibration work | Certification | Chandrasekar and Dharmesh | 2023-05-20 | - | Stamping and calibration done Calibration reports : "A" side 10 ltrs = 10.00 "B" side 10 ltrs = 9.99 "C" side 10 ltrs = 9.95 "D" side 10 ltrs = 9.97 "K" Factor reports: "A" side 'K' factor = 10000 "B" side 'K' factor= 10000 "C" side 'K' factor =10000 "D" side 'K' factor =10000 "K" Factor no change C&D side nozzle switch changed - Printer cable alteration work done - Working fine - Completed
CL3428 | 2023-05-21 | Ariyamangalam | G | Online UPS not working properly | Breakdown | Nivas | 2023-05-21 | - | Stand by UPS replaced - Resolved
CL3429 | 2023-05-21 | Krishnagiri | D | Dispenser both side cut off problem | Breakdown | Prabu | 2023-05-21 | - | LPG flow valve adjusted - Cut off working properly - Rectified
CL3430 | 2023-05-21 | Vadivelan Nagar | A | Automation CPU problem | Breakdown | Suneel Sagar | 2023-05-21 | - | CPU replaced - Outlet back online - Completed
CL3431 | 2023-05-22 | Thiruvaiyaru | D | Dispenser B side metering unit problem | Breakdown | Nepolean | 2023-05-22 | - | Metering unit seal kit replaced - High flow low flow valve cleaned - One day under observation - Testing at B side : 73.10 L - Resolved
CL3432 | 2023-05-23 | Palladam 1 | D | C side keypad defect | Breakdown | Gowtham | 2023-05-23 | - | Keypad replaced with new one - Attended
CL3433 | 2023-05-23 | Kattupakkam | C | Stamping and calibration work | Certification | Dharmesh | 2023-05-23 | - | Stamping and calibration done - Calibration reports : "A" side 10 ltrs = 10.13 "B" side 10 ltrs = 10.13 "C" side 10 ltrs = 10.14 "D" side 10 ltrs = 10.15 "K" Factor reports: "A" side 'K' factor = 9842 "B" side 'K' factor= 9842 "C" side 'K' factor =9820 "D" side 'K' factor =9820 "K" Factor no change Testing liter A - 163.98 B - 209.86 C - 202.08 D - 214.19 Total testing - 790.11 ltr - Completed
CL3434 | 2023-05-24 | Vadivelan Nagar | C | PNGRB - ERDMP mock drill | Certification | Prakash | 2023-05-24 | - | Mock drill program completed - Attended
CL3435 | 2023-05-25 | Vellakovil | D | Batchen dispenser A nozzle slow delivery | Breakdown | Thirumalaisamy | 2023-05-25 | - | High flow low flow solenoid valve solenoid valve cleaned - Filter cleaned - Testing : A side : 31 L; B side - 15 L - Working fine - Rectified
CL3436 | 2023-05-25 | Virudhunagar | G | Servo stabilizer PCB short circuited | Breakdown | Kathiresan | 2023-05-25 | - | PCB replaced by Mothish service person - Working fine - Completed
CL3437 | 2023-05-25 | Cantonment | D | Outlet running in genset mode due to the failure of EB transformer | Breakdown | Vigneshwaran | 2023-05-26 | - | EB problem resolved - Outlet running in EB mode - Attended
CL3438 | 2023-05-25 | Tiruchengode | G | Unloading and unloading training | Preventive | Thirumalaisamy | 2023-05-25 | - | Unloading done - Unloading training provided to all pump staffs - Attended
CL3439 | 2023-05-26 | Paramathivelur | T | Dispensing motor love joy coupling spider damage | Breakdown | Thirumalaisamy | 2023-05-26 | - | Love joy coupling spider replaced - Working fine - Resolved
CL3440 | 2023-05-26 | Villapuram | T | Dispensing air hose damaged | Breakdown | Kathiresan | 2023-05-26 | - | EB room to dispenser pneumatic hose replaced with new - Rectified
CL3441 | 2023-05-26 | T.V.Kovil | D | D nozzle defect | Breakdown | Avinash | 2023-05-26 | - | Nozzle serviced and tested - Testing : 1.02 Ltrs - Completed
CL3442 | 2023-05-27 | Namakkal 3 | R | Control panel not booting | Breakdown | Prabu | 2023-05-27 | 30 Mins | Panel transformer fuse replaced - Panel booted - Working fine - Resolved
CL3443 | 2023-05-27 | Ariyamangalam | D | B nozzle lock defect | Breakdown | Nepolean | 2023-05-27 | - | B nozzle lock set replaced with new - Nozzle working good - Rectified
CL3444 | 2023-05-27 | Ellis Nagar | D | All 4 nozzle teeth to be replaced as it is running over 400000 L | Preventive | Kathiresan | 2023-05-27 | - | All4 nozzle's hammer teeth replaced - Working good - Totalizer Reading : " A " side = 426164.10 " B " side = 455374.82 " C " side = 302405.76 " D " side = 396620.24 - Tank 1 dispensing line 40NB ballvalve LPG leakage arrested by tightening the nut and teflon applied - Completed
CL3445 | 2023-05-30 | Thanjavur | T | Unloading and unloading training | Preventive | Pandi Durai | 2023-05-30 | - | Unloading done - Unloading training provided to pump staffs - Attended
CL3446 | 2023-05-30 | Villapuram | T | Tank area to EB room dispensing line pneumatic hose changing | Preventive | Kathiresan | 2023-05-30 | - | Tank area to EB room dispensing line pneumatic hose replaced for 35 mtrs - Working fine - Completed
CL3447 | 2023-05-30 | T.V.Kovil | D | Yenen D nozzle leakage | Breakdown | Vigneshwaran | 2023-05-30 | - | Nozzle serviced - Testing : 1.03 Ltrs - Rectified
CL3448 | 2023-05-31 | Chinnasalem | C | PNGRB - ERDMP mock drill arrangements | Certification | Prabu | 2023-05-31 | - | PNGRB - ERDMP mock drill arrangements partially done - Attended
CL3449 | 2023-05-31 | Virudhunagar | D | B nozzle leakage | Breakdown | Kathiresan | 2023-05-31 | - | Nozzle teeth 4 nos replaced - Front O ring changed - Working fine - Spare nozzle serviced - Rectified
CL3450 | 2023-05-31 | Bodi | G | Fire extinguisher service | Preventive | Kamaraj | 2023-05-31 | - | All extinguisher checked - Total leakage tested - Completed
CL3451 | 2023-05-31 | Uthamapalayam | G | Fire extinguisher service | Preventive | Kamaraj | 2023-05-31 | - | 75 kg fire extinguisher damaged hose replaced with new - All extinguisher checked - Total leakage tested - Completed
CL3452 | 2023-05-31 | Vadivelan Nagar | R | Dispensing solenoid defect | Breakdown | Suneel Sagar | 2023-05-31 | - | Tank 2 dispensing solenoid replaced - D side nozzle hammer teeth 4 Nos and front bush replaced - Working fine - Resolved
CL3453 | 2023-05-31 | Kodungaiyur | D | B side 5 mtr dispensing hose damaged and On/off switch disconnected | Breakdown | Suneel Sagar | 2023-06-02 | 2 Days and 1 Hour (B Nozzle) | 5m dispensing hose replaced with new - Working fine - Rectified
CL3454 | 2023-06-01 | Chinnasalem | C | PNGRB - ERDMP mock drill arrangements | Certification | Avinash, Dharmesh and Prabu | 2023-06-01 | - | PNGRB - ERDMP mock drill arrangements done - Attended
CL3455 | 2023-06-02 | Cantonment | D | C nozzle LPG leakage | Breakdown | Chandrasekar | 2023-06-02 | - | Nozzle serviced - Testing : 0.85 Ltrs - Rectified
CL3456 | 2023-06-03 | Chinnasalem | C | PNGRB - ERDMP mock drill | Certification | Prabu | 2023-06-03 | - | ERDMP mock drill done - Completed
CL3457 | 2023-06-03 | Palayam | R | EB room to dispenser pneumatic hose damaged | Breakdown | Thirumalaisamy | 2023-06-03 | - | EB room to dispenser pneumatic hose replaced with new - Automation maintenance done - Rectified
CL3458 | 2023-06-03 | Tharamangalam | G | EB improper supply | Breakdown | Prabu | 2023-06-03 | - | DG mode working for 3 hours - EB supply working properly - Working fine - Attended
CL3459 | 2023-06-03 | Bhavani | A | Dispenser going offline due to RS485 to USB converter board damaged | Breakdown | Prabu | 2023-06-04 | - | RS485 to USB converter board spare board replaced - Dispenser back online - Working fine - Resolved
CL3460 | 2023-06-04 | Villapuram | A | Automation CPU not working properly | Breakdown | Kathiresan | 2023-06-04 | - | CPU serviced - Dispenser back online - Day shift closing Time was extended - Working fine - Completed
CL3461 | 2023-06-05 | Palladam 1 | C | Rule 19 work | Certification | Kathiresan | 2023-06-09 | 2 Days | Tank closing- 5.5% Closing Reading A side - 108.10 B side - 4426.92 C side - 1891030.76 D side - 1705623.71 N2 holding pressure - 10 kg/cm2. - Automation work partially done - Above ground motor pump welding and hydro tested - Completed
CL3462 | 2023-06-05 | Virudhunagar | A | Dispenser going offline due to solar inverter problem | Breakdown | Kathiresan | 2023-06-05 | - | Solar inverter replaced - Solar panel wiring changed - Dispenser back online - Resolved
CL3463 | 2023-06-05 | Bhavani | G | Chemical earth installation | Preventive | Prabu | 2023-06-05 | - | Chemical earth 3 Nos installed - Control panel indicator 2 nos changed - Compressor oil changed - UPS battery water level topped up - Automation maintenance done - Total leakage tested - Completed
CL3464 | 2023-06-06 | Thanjavur | G | Unloading and unloading training | Preventive | Pandi Durai | 2023-06-06 | - | Unloading done - Unloading training provided to pump staffs - Attended
CL3465 | 2023-06-08 | Namakkal 3 | R | Control panel transformer fuse holder burnt due to high EB voltage | Breakdown | Prabu | 2023-06-08 | - | Fuse replaced - PMR done - Resolved
CL3466 | 2023-06-08 | Tharamangalam | D | Dispensing motor spider damaged | Breakdown | Prabu | 2023-06-08 | - | Spider replaced - Pump with motor working fine - A nozzle O ring and teeth replaced to arrest the leakage - Working fine - Rectified
CL3467 | 2023-06-09 | Vadivelan Nagar | R | Control panel not working | Breakdown | Suneel Sagar | 2023-06-09 | - | Surge arrester defective elements replaced - Panel working fine - Resolved
CL3468 | 2023-06-09 | Villapuram | D | D nozzle leakage | Breakdown | Kathiresan | 2023-06-09 | - | D nozzle hammer teeth replaced - Working fine - Completed
CL3469 | 2023-06-09 | Ellis Nagar | T | Tank 2 pressure increased to 9.5 kg and dispensing pressure to 15.2 kg | Breakdown | Kathiresan | 2023-06-09 | - | Dispensing bypass valve adjusted and equalizer valve adjusted to 14 kg - Working fine - Rectified
CL3470 | 2023-06-09 | T.V.Kovil | D | A nozzle LPG leakage | Breakdown | Dharmesh | 2023-06-09 | - | A nozzle hammer teeth replaced - Working fine - Resolved
CL3471 | 2023-06-10 | Ariyamangalam | R | Compressor oil changing | Preventive | Pandi Durai | 2023-06-10 | - | Compressor oil changed for both compressors - Attended
CL3472 | 2023-06-11 | Villapuram | D | Dispenser going offline due to A and B side RS485 to USB converter board defect | Breakdown | Kathiresan | 2023-06-11 | - | RS485 to USB converter board replaced - Dispenser back online - Working fine - Rectifed
CL3473 | 2023-06-11 | Rasipuram | D | Dispenser A side On / Off switch, hammer teeth and nozzle front O ring defect | Breakdown | Prabu | 2023-06-11 | - | Dispenser A side On / Off switch, hammer teeth and nozzle front O ring replaced - PMR done - Completed
CL3474 | 2023-06-11 | Ariyamangalam | D | B nozzle leakage | Breakdown | Pandi Durai | 2023-06-11 | - | B nozzle hammer teeth 4 Nos replaced - D side nozzle front O ring 1 No changed - Working fine - Resolved
CL3475 | 2023-06-13 | Krishnagiri | T | Tank area unloading ROV leakage | Breakdown | Prabu | 2023-06-13 | - | Unloading ROV leakage arrested by tightening the nut - A side On/Off switch replaced - Nozzle serviced - Working fine - Rectified
CL3476 | 2023-06-13 | Theni | D | Batchen dispenser A side display not working properly | Breakdown | Kamaraj | 2023-06-13 | - | Mother board display cable interchanged - Working fine - Dispensing motor pressure gauge 1 No replaced - General check up done - Completed
CL3477 | 2023-06-14 | Dharapuram | R | Dispensing solenoid coil air leakage | Breakdown | Kamaraj | 2023-06-14 | - | Air leakage arrested by tightening the fittings and teflon applied - All ROV checked - General check up done - Resolved
CL3478 | 2023-06-14 | Villapuram | G | Online UPS back up problem | Breakdown | Kathiresan | 2023-06-14 | - | 12V battery 3 Nos replaced - Working fine with back up time of 14 minutes - Completed
CL3479 | 2023-06-15 | Ammapet | D | Dispenser reading reverse due to power supply issue | Breakdown | Prabu | 2023-06-15 | - | Permission updated at database - A nozzle reverse - 812.26 liters B nozzle reverse - 594.05 liters - Dispenser back online - Resolved
CL3480 | 2023-06-16 | Aravakurichi | A | CPU heating issue | Breakdown | Thirumalaisamy | 2023-06-16 | - | Spare CPU replaced - Working fine - Attended
CL3481 | 2023-06-16 | Kodumudi | A | CPU heating issue | Breakdown | Thirumalaisamy | 2023-06-16 | - | Spare CPU replaced - Working fine - Attended
CL3482 | 2023-06-16 | Cantonment | D | Dispenser C and E side keypad not working | Breakdown | Chandrasekar | 2023-06-16 | - | Both keypads replaced - Working fine - Attended
CL3483 | 2023-06-16 | T.V.Kovil | R | Offline UPS battery low voltage problem | Breakdown | Vigneshwaran | 2023-06-16 | - | New battery replaced - Working fine - Rectified
CL3484 | 2023-06-16 | Villapuram | G | Fire extinguihser service and training | Breakdown | Kathiresan | 2023-06-16 | - | 75 kg fire extinguisher CO2 replaced - Fire safety training provided to pump staffs - Completed
CL3485 | 2023-06-16 | Ellis Nagar | G | Fire extinguihser service and training | Breakdown | Kathiresan | 2023-06-16 | - | Fire safety training provided to pump staffs - Completed
CL3486 | 2023-06-17 | Omalur | T | Tank hydro test | New Project | Avinash and Prabu | 2023-06-17 | - | Hydro test done - Completed
CL3487 | 2023-06-18 | Villapuram | G | Working in genset mode due to EB transformer short circuit | Breakdown | Kathiresan | 2023-06-18 | - | Transformer problem attended - Working in EB - Resolved
CL3488 | 2023-06-18 | Tirunelveli | D | Dispenser auto cut off | Breakdown | Kathiresan | 2023-06-18 | - | Dispenser flow rating valve adjusted - Kept under observation for a week - A side keypad replaced - Nozzle teeth 4 nos changed - Automation maintenance done - Working good - Rectified
CL3489 | 2023-06-18 | Ayothiyapattinam | T | Unloading cannot be performed | Breakdown | Prabu | 2023-06-18 | - | Excess flow valve released - Tank area to EB room spare air hose replaced - Resolved
CL3490 | 2023-06-18 | Bathlagundu | D | A nozzle not working properly | Breakdown | Kamaraj | 2023-06-18 | - | A nozzle serviced - Testing : 1.39 L - General check up done - Working good - Completed
CL3491 | 2023-06-18 | Omalur | T | CP installation | New Project | Prabu | 2023-06-18 | - | Cathodic protection installed - R1 C1- 0.65 R1 C2- 0.66 R1 A1 -1.68 R1 A2 -1.72 R1 A3 -1.70 R1 A4 -1.68 Total -1.14 - Completed
CL3492 | 2023-06-19 | Cantonment | D | E nozzle swivel joint leakage | Breakdown | Chandrasekar | 2023-06-19 | - | Spare nozzle replaced - Testing : 0.89 L - Working fine - Resolved
CL3493 | 2023-06-19 | Ellis Nagar | T | Tank 1 unloading ballvalve with ROV LPG leakage | Breakdown | Kathiresan | 2023-06-19 | - | Leakage arrested by tightening the nut and teflon applied - Ttaol outlet LPG leakage tested - PMR done - Working good - Rectified
CL3494 | 2023-06-20 | Chinnasalem | C | Calibration and stamping work | Certification | Vigneshwaran and Prabu | 2023-06-20 | - | Calibration and stamping done - Calibration reports : "A" side 10 ltrs = 9.96 "B" side 10 ltrs = 9.94 "K" Factor reports: "A" side 'K' factor = 10000 "B" side 'K' factor= 10000 "K" Factor no change Testing liter A - 100.00 B - 100.00 Total testing - 200.00 L - Attended
CL3495 | 2023-06-20 | Cantonment | G | Air inflator not working | Breakdown | Chandrasekar | 2023-06-20 | - | New air inflator installed - Working fine - Completed
CL3496 | 2023-06-20 | Velachery | C | PMR and PNGRB general inspection | Certification | Suneel Sagar | 2023-06-20 | - | PMR and PNGRB general inspection done - Completed
CL3497 | 2023-06-21 | Paramathivelur | C | Calibration and stamping work | Certification | Vigneshwaran and Thirumalaisamy | 2023-06-21 | - | Calibration and stamping done - "A" side 10 ltrs =10.01 "B" side 10 ltrs = 9.98 "K" Factor reports: "A" side 'K' factor = 10000 "B" side 'K' factor= 10000 "K" Factor no change Testing liters A -283.05litters B -222.35litters Total testing-505.40litters - A nozzle replaced - Completed
CL3498 | 2023-06-21 | Krishnagiri | T | Unloading liquid line hose adapter broken | Breakdown | Prabu | 2023-06-21 | - | Liquid line hose adaptor replaced - Unloading done - Resolved
CL3499 | 2023-06-21 | Palladam 2 | G | Outlet reopening | Renovation | Krishna Bhalaji | 2023-06-21 | 23 Days | Outlet reopened - Attended
CL3500 | 2023-06-21 | Palayam | C | Calibration and stamping work | Certification | Vigneshwaran and Thirumalaisamy | 2023-06-21 | - | Calibration and stamping done - "A" side 10 ltrs =10.00 "B" side 10 ltrs = 10.01 "K" Factor reports: "A" side 'K' factor = 10000 "B" side old 'K' factor= 10000 B side new 'K' factor=10010 Testing liters A -142.19litters B -223.41litters Total testing-365.60litters - Completed
CL3501 | 2023-06-22 | Paramathivelur | D | A nozzle mount leakage | Breakdown | Thirumalaisamy | 2023-06-22 | - | Nozzle mount O ring replaced - Leakage arrested - Testing : 1.66 L - Working good - Rectified
CL3502 | 2023-06-22 | Omalur | G | Earth pipe installation and rule 33 data collection | New Project | Prakash & Prabu | 2023-06-22 | - | Tank flanges liquid line pipe lines welding done - EF valve and flanges fixed - Earthing pipe installed - Rule 33 data collected - Completed
CL3503 | 2023-06-22 | Tirunelveli | A | Dispenser going offline due to totalizer reverse problem - Dispenser Cut off | Breakdown | Kathiresan | 2023-06-23 | - | Automation alternative program installed - Dispenser back online - Working fine - C side 5m dispensing hose replaced - Kept under observation - Testing : 0.80 L - Resolved
CL3504 | 2023-06-22 | Ariyamangalam | D | B nozzle lock defect | Breakdown | Nepolean | 2023-06-22 | - | Nozzle lock replaced - Working fine - Resolved
CL3505 | 2023-06-22 | Musiri | R | Control panel indicator defect | Breakdown | Nivas | 2023-06-22 | - | Panel indicator replaced - Dispenser A side nozzle teeth replaced - Unloading vapour line ballvalve with ROV LPG leakage arrested by tightening the nut - Rectified
CL3506 | 2023-06-22 | Cantonment | R | Online UPS battery defect | Breakdown | Chandrasekar | 2023-06-22 | - | Online UPS battery 3 Nos replaced - Completed
CL3507 | 2023-06-22 | Kattupakkam | C | PMR and PNGRB general inspection | Certification | Suneel Sagar | 2023-06-22 | - | PMR and PNGRB general inspection done - Completed
CL3508 | 2023-06-23 | Dharapuram | R | Unloading solenoid valve defect | Breakdown | Gowtham | 2023-06-23 | - | Filter with regulator and unloading solenoid valve replaced - Lovejoy coupling spider replaced - PMR done - Rectified
CL3509 | 2023-06-23 | Ariyamangalam | D | D side nozzle servicing (Nozzle from Bathlagundu) | Preventive | Nepolean | 2023-06-23 | - | Nozzle serviced - NRV O ring and Hammer teeth 4 Nos replaced - D side testing : 1.51 Ltr - Resolved
CL3510 | 2023-06-24 | Kodumudi | A | System power fluctuation due to power cable adapter problem - Dispenser went offline | Breakdown | Thirumalaisamy | 2023-06-24 | - | New CPU power cable replaced - CPU replaced with spare - Outlet back online - Working fine - Completed
CL3511 | 2023-06-24 | T.V.Kovil | R | Compressor V belt defect | Breakdown | Vigneshwaran | 2023-06-24 | - | Compressor V belt has been replaced - Working fine - Rectified
CL3512 | 2023-06-25 | Palladam 2 | D | A nozzle slow delivery | Breakdown | Vigneshwaran | 2023-06-25 | - | Nozzle O ring breadth adjusted - Kept under observation - Testing : 79.61 L - Resolved
CL3513 | 2023-06-26 | Virudhunagar | G | Camera NVR hard disk defect | Breakdown | Kathiresan | 2023-07-16 | - | DB panel MCB replaced - NVR SMPS sent to HO on 13.07.2023 - Dispensing line 40 NB Ball Valve stem leakage arrested by tightnining - NVR total assembly replaced on 16.07.2023 - Automation maintenance done - General civil work done - Completed
CL3514 | 2023-06-26 | Saravanampatty | R | Control panel to tank area air hose defect | Breakdown | Gowtham | 2023-06-26 | - | Control panel to tank area air hose replaced - Panel operator switch newly installed - Dispensing line 40 NB ROV interchanged to resolve air leak - PMR done - A side keypad replaced - Working fine - Completed
CL3515 | 2023-06-26 | Musiri | T | Unloading liquid line ROV air leakage | Breakdown | Nivas | 2023-08-07 | - | Unloading fill point ROV replaced - No leakage found - Unloading training provided to pump staffs - Completed
CL3516 | 2023-06-26 | T.V.Kovil | C | PMR work | Certification | Vigneshwaran | 2023-06-26 | - | PMR done - Completed
CL3517 | 2023-06-27 | Tharamangalam | D | Dispenser bottom ROV top leakage | Breakdown | Prabu | 2023-06-27 | - | Leakage arrested by tightening the nut and teflon applied - Tank area air hose replaced - Working good - Rectified
CL3518 | 2023-06-29 | Musiri | T | Unloading work | Preventive | Nivas | 2023-06-29 | - | Unloading done - Attended
CL3519 | 2023-06-29 | Avadi | C | PMR and PNGRB general inspection | Certification | Suneel Sagar | 2023-06-29 | - | PMR and PNGRB general inspection done - Completed
CL3520 | 2023-06-29 | Villapuram | D | D nozzle slow delivery | Breakdown | Kathiresan | 2023-06-29 | - | Dispenser high flow solenoid valve 1.5A fuse replaced - Working good - Rectified
CL3521 | 2023-06-29 | T.V.Kovil | D | D nozzle hammer teeth defect | Breakdown | Vigneshwaran | 2023-06-29 | - | Hammer teeth 4 nos replaced at D nozzle - Attended
CL3522 | 2023-06-29 | Krishnagiri | G | Offline UPS backup problem | Breakdown | Prabu | 2023-06-29 | - | Offline UPS replaced - A side keypad replaced - Working good - Rectified
CL3523 | 2023-06-30 | Cantonment | D | C nozzle swivel joint leakage | Breakdown | Chandrasekar | 2023-06-30 | - | Old nozzle replaced - Working fine - Testing C side : 1 L - Completed
CL3524 | 2023-07-03 | Bhavani | R | Control panel dispensing solenoid coil air leakage | Breakdown | Prabu | 2023-07-03 | - | Both dispensing and unloading air solenoid coil replaced - FRL 1 unit replaced - Control panel RYB indicator light replaced - Working fine - Resolved
CL3525 | 2023-07-03 | Chengalpattu | C | PMR and PNGRB general inspection | Certification | Suneel Sagar | 2023-07-03 | - | PMR and PNGRB general inspection done - Completed
CL3526 | 2023-07-04 | Tenkasi | G | Genset mode not working | Breakdown | Kathiresan | 2023-07-04 | - | Genset AVR frequency increased and program settings changed - Genset mode working - Control panel VSR replaced with new one - B side keypad replaced - Working fine - Rectified
CL3527 | 2023-07-04 | Kodumudi | A | Totalizer reversed due to voltage fluctuation | Breakdown | Thirumalaisamy | 2023-07-04 | - | Voltage fluctuation adjusted - Attended
CL3528 | 2023-07-05 | Ariyamangalam | T | Fill point emergency not working | Breakdown | Nepolean | 2023-07-05 | - | Fill point emergency line cable replaced - Working fine - Attended
CL3529 | 2023-07-05 | T.V.Kovil | D | Batchen dispenser B nozzle teeth damage | Breakdown | Vignesh | 2023-07-05 | - | Hammer teeth 4 nos replaced at B nozzle - Attended
CL3530 | 2023-07-05 | Omalur | C | Third party inspection | New Project | Prabu | 2023-07-05 | - | Third party inspection done - Pipeline welding and canopy work in process - Completed
CL3531 | 2023-07-05 | Vadivelan Nagar | D | A and B nozzle hoses defect | Breakdown | Suneel Sagar | 2023-07-05 | - | recrimped hoses replaced - No leakage found at 15kg - Rectified
CL3532 | 2023-07-05 | Kodumudi | R | Offline UPS battery defect | Breakdown | Thirumalaisamy | 2023-07-05 | - | Offline UPS battery replaced - Earth pit alteration done - Resolved
CL3533 | 2023-07-06 | Namakkal 2 | R | Online UPS not working properly | Breakdown | Prabu | 2023-07-06 | - | Online UPS battery 3 Nos replaced - A nozzle serviced - Control panel RYB indicator light replaced - Completed
CL3534 | 2023-07-06 | Renganathan Gas Bunk | R | Control panel booting problem | Breakdown | Vigneshwaran | 2023-07-06 | - | SMPS newly replaced - Working fine - Completed
CL3535 | 2023-07-07 | Udumalpet | C | Rule 19 work | Certification | Chandrasekar, Nivas, Gowtham and Sureshkumar | 2023-07-13 | - | Rule 19 done - Tank 1 sales stopped for 43 hours - Tank 1 commissioning done on 09.07.2023 - Tank 2 sales stopped for 48 hours - CP installation done for both tanks - Automation installation and electrical maintenance in process - Completed
CL3536 | 2023-07-07 | Villapuram | D | Dispenser display glass damaged at A and B side | Breakdown | Kathiresan | 2023-07-07 | - | Display glass replaced for both sides - Working fine - Resolved
CL3537 | 2023-07-08 | Ariyamangalam | D | Batchen dispenser tube lights defect | Breakdown | Pandi Durai | 2023-07-08 | - | C and D side new tube lights replaced - Attended
CL3538 | 2023-07-08 | Chengalpattu | D | Dispenser display glass damaged | Breakdown | Suneel Sagar | 2023-07-08 | - | Display glass replaced at B side - Working fine - Resolved
CL3539 | 2023-07-08 | Neelambur | D | A nozzle teeth worn out | Breakdown | Gowtham | 2023-07-08 | - | Nozzle hammer teeth 4 Nos replaced - Working good - Rectified
CL3540 | 2023-07-09 | Paramathivelur | A | Outlet going offline due to automation system heating issue | Breakdown | Thirumalaisamy | 2023-07-09 | - | Spare CPU replaced - Dispenser back online - B nozzle lock replaced - Working fine - Attended
CL3541 | 2023-07-09 | Omalur | T | Welding work and hydro testing | New Project | Prabu | 2023-07-09 | - | Dispensing and unloading liquid & vapour pipe line welding done - Hydro test done - Completed
CL3542 | 2023-07-10 | Avadi | A | Outlet going offline due to power fluctuation | Breakdown | Suneel Sagar | 2023-07-10 | - | Dispensers went offline for 12 Hours - Automation connections refitted - Working fine - Resolved
CL3543 | 2023-07-10 | Villapuram | C | Calibration and stamping work | Certification | Kathiresan | 2023-07-10 | - | Calibration and stamping done - Calibration report: "A" side 10 ltrs = 9.94 "B" side 10 ltrs = 9.94 "C" side 10 ltrs = 9.99 "D" side 10 ltrs = 9.95 "K" factor report; ' A ' side old K = 10150 ' A ' side new K = 10130 ' B ' side old K. = 10150 ' B ' side new K = 10130 ' C ' side old K = 10400 ' C ' side new K = 10400 ' D ' side old K = 10150 ' D ' side new K = 10130 Thank you. Testing ltrs = 538.17 - Completed
CL3544 | 2023-07-11 | Dharmapuri | D | A nozzle leakage and keypad one side not working | Breakdown | Prabu | 2023-07-11 | - | Nozzle teeth replaced for both nozzles - Nozzle end O rings changed - EB line indicator replaced - Completed
CL3545 | 2023-07-11 | Melur | C | Calibration and stamping work | Certification | Kathiresan | 2023-07-11 | - | Calibration and Stamping done - Calibration report: "A" side 10 ltrs = 9.90 "B" side 10 ltrs = 9.91 "K" factor report : "A" side = 10180 "B" side = 10180 Testing = 269.44 ltrs - Completed
CL3546 | 2023-07-11 | Omalur | G | Electrical work | New Project | Prabu | 2023-07-11 | - | Electrical conduit trench and pipeline laying work completed - Attended
CL3547 | 2023-07-12 | Ellis Nagar | C | Calibration and stamping work | Certification | Kathiresan | 2023-07-12 | - | Calibration and Stamping done - Calibration report: "A" side 10 ltrs = 9.96 "B" side 10 ltrs = 9.96 "C" side 10 ltrs = 9.98 "D" side 10 ltrs = 9.97 "K" factor report; ' A ' side K = 10000 ' B ' side K. = 10000 ' C ' side K = 10000 ' D ' side K = 10000 Testing = 595.06 ltrs - Resolved
CL3548 | 2023-07-13 | Salem 2 | G | Site visit | New Project | Prakash | 2023-07-13 | - | Site visit done - Completed
CL3549 | 2023-07-13 | Omalur | G | Site visit | New Project | Prakash | 2023-07-13 | - | Site visit done - Completed
CL3550 | 2023-07-14 | Dindigul | D | Dispenser B nozzle hose LPG leakage | Breakdown | Kamaraj | 2023-07-14 | - | New hose replaced - Working fine - Testing : 0.88 Ltrs - Resolved
CL3551 | 2023-07-15 | Palladam 1 | G | Site recommissioning | Preventive | Prakash and Vigneshwaran | 2023-07-15 | - | Site recommissioning done - Batchen dispenser sales started with online - Yenen sales started with offline billing - Completed
CL3552 | 2023-07-16 | Palladam 1 | A | Yenen dispenser automation installation | New Project | Madhavan | 2023-07-16 | - | Both dispenser working in online - Completed
CL3553 | 2023-07-17 | Ramnad | R | Online UPS battery defect | Breakdown | Kathiresan | 2023-07-17 | - | 12V 7AH battery 3 Nos replaced - Unloading solenoid valve replaced - Control panel indicator 2 Nos replaced - Dispenser display glass 2 Nos replaced - Working fine - Resolved
CL3554 | 2023-07-17 | Udumalpet | G | General site visit | Renovation | Gowtham | 2023-07-17 | - | Site visit done - Completed
CL3555 | 2023-07-18 | Eral | T | Dispensing and discanting can't be done due to 25 NB decanting ballvalve with ROV failure | Breakdown | Kathiresan | 2023-07-18 | - | ROV removed and to be replaced - Working in manual mode - Decanting done - Dispensing motor bypass valve adjusted - Pump working pressure is 12 kg/cm2 - Serviced ROV refitted on 11.10.2023 - Attended
CL3556 | 2023-07-18 | Palladam 1 | D | Batchen dispenser error 61 occurred, A side preset not working and metering unit problem | Breakdown | Nepolean | 2023-07-20 | - | EEPROM IC D4 5.7 replaced - On/off switch replaced - A and C side nozzle teeth 4 Nos replaced - Batchen testing A : 46.21 L; B : 42.79 L - Resolved
CL3557 | 2023-07-18 | Chinnasalem | D | Dispenser nozzle leakage and both side keypads not working properly | Breakdown | Prabu | 2023-07-18 | - | Nozzle serviced and reconnected - A side keypad replaced - Working fine - Rectified
CL3558 | 2023-07-18 | Neelambur | R | Online UPS line filter burnt due to sudden spike in input voltage | Breakdown | Gowtham | 2023-07-18 | - | Online UPS line filter to be replaced - Online UPS directed - Working good - Online UPS line filter and battery 3 Nos replaced on 21.08.2023 - Resolved
CL3559 | 2023-07-18 | Palladam 2 | A | RS485 to USB converter board replacement | New Project | Gowtham | 2023-07-18 | - | Network boards replaced instead of RS485 to USB converter board - Working fine - Attended
CL3560 | 2023-07-19 | Aravakurichi | D | Dispenser nozzle leakage | Breakdown | Thirumalaisamy | 2023-07-19 | - | Nozzle hammer teeth 4 Nos replaced - Unloading liquid hose brass adapter leakage arrested - Attended
CL3561 | 2023-07-19 | Ariyamangalam | D | A nozzle leakage | Breakdown | Nepolean | 2023-07-19 | - | A nozzle teeth 4 Nos and nozzle lock replaced - Working fine - Resolved
CL3562 | 2023-07-19 | Paramathivelur | R | Offline UPS board defect | Breakdown | Thirumalaisamy | 2023-11-21 | - | Dispenser working in online UPS supply - Serviced offline UPS installed - Working fine - Recitified
CL3563 | 2023-07-20 | Palladam 1 | A | Dispenser going offline due to internal server error | Breakdown | Gowtham | 2023-07-20 | - | Mobile restarted - Wifi connected - Outlet back online - Recitifed
CL3564 | 2023-07-20 | Hosur | T | Unloading cant be done due to unloading liquid hose damage | Breakdown | Prabu | 2023-07-21 | - | Krishnagiri outlet liquid hose used for unloading - Attended
CL3565 | 2023-07-20 | Ellis Nagar | D | D nozzle lock spring defect | Breakdown | Kathiresan | 2023-07-20 | - | Nozzle lock spring set replaced - Working fine - Rectified
CL3566 | 2023-07-20 | Villapuram | T | Unloading air hose leakage | Breakdown | Kathiresan | 2023-07-20 | - | Unloading air hose replaced - Leakage arrested - Resolved
CL3567 | 2023-07-20 | Erode | R | Compressor starter defect | Breakdown | Thirumalaisamy | 2023-07-27 | - | Compressor starter replaced - Working fine - Attended
CL3568 | 2023-07-23 | Ayothiyapattinam | R | Compressor running continuously due to EB room to tank area air hose leakage | Breakdown | Prabu | 2023-07-23 | - | EB room to tank area air hose replaced - Compressor working fine - Completed
CL3569 | 2023-07-24 | T.V.Kovil | A | B nozzle not working due to error | Breakdown | Nepolean | 2023-07-24 | - | Error cleared in back end - Resolved
CL3570 | 2023-07-24 | Cantonment | G | N2 machine On/off switch not working | Breakdown | Chandrasekar | 2023-07-24 | - | N2 machine on/off switch replaced - Working fine - Resolved
CL3571 | 2023-07-24 | Palladam 1 | A | Automation yenen network board connection to offline UPS | Preventive | Gowtham | 2023-07-24 | - | Yenen network board connected to offline UPS - Completed
CL3572 | 2023-07-25 | Vedachandur | A | Network issue | Breakdown | Thirumalaisamy | 2023-07-25 | - | Data enabled - Working fine - Resolved
CL3573 | 2023-07-26 | Palladam 1 | D | Nozzle leakage | Breakdown | Thirumalaisamy | 2023-07-26 | - | Nozzle serviced - Training provided to pump staffs - Attended
CL3574 | 2023-07-26 | Bodi | T | ROV stem LPG leakage | Breakdown | Kamaraj | 2023-07-27 | - | 25 NB ballvalve with ROV replaced to arrest leakage - ROV stem leakage arrested - Dispensing air hose spare line replaced - Pump operating training provided to pump staffs - Completed
CL3575 | 2023-07-26 | Avadi | R | Online UPS battery defect | Breakdown | Suneel Sagar | 2023-07-26 | - | Online UPS battery 3 Nos replaced - No earth issue found - Completed
CL3576 | 2023-07-26 | Villapuram | R | Compressor oil replacing | Preventive | Kathiresan | 2023-07-26 | - | Compressor oil changed - NRV cleaned - Air filter changed - Working fine - Resolved
CL3577 | 2023-07-26 | Palladam 2 | A | Yenen interface board connection | New Project | Thirumalaisamy | 2023-07-26 | - | Yenen interface board connected - Completed
CL3578 | 2023-07-27 | Perundurai | D | A side not working due high flow solenoid valve defect | Breakdown | Thirumalaisamy | 2023-07-28 | - | Solenoid coil replaced - Working fine - Resolved
CL3579 | 2023-07-27 | T.V.Kovil | G | Fire extinguisher service | Preventive | Nepolean | 2023-07-27 | - | Fire extinguisher service done - completed
CL3580 | 2023-07-28 | Avinashi | C | Rule 19 work and automation installation | Certification | Chandrasekar, Gowtham and Suresh Kumar | 2023-08-03 | - | Tank 1 sales stopped at 5.45 pm on 28.07.2023 - Tank 2 sales stopped at 7.10 pm on 31.07.2023 - Rule 19 done - New ATG installed - Automation installed - All equipments working fine - Completed
CL3581 | 2023-07-28 | Ariyamangalam | D | Nozzle testing and servicing at D side | Preventive | Nepolean | 2023-07-28 | - | Nozzles serviced and tested at D side - Testing Litres : 2.24 L - Completed
CL3582 | 2023-07-28 | Kodungaiyur | C | PMR work | Certification | Suneel Sagar | 2023-07-28 | - | PMR done and earth pits generated - Completed
CL3583 | 2023-07-28 | Kangeyam | D | A nozzle slow delivery | Breakdown | Thirumalaisamy | 2023-07-28 | - | High flow low flow solenoid valved cleaned - Working fine - Kept under observation - Attended
CL3584 | 2023-07-28 | Karur | D | C and D nozzle leakage | Breakdown | Thirumalaisamy | 2023-07-28 | - | C and D side nozzle teeth replaced - Leakage arrested - Working good - Rectified
CL3585 | 2023-07-29 | Avadi | D | B nozzle dispensing hose puncture | Breakdown | Suneel Sagar | 2023-07-31 | 2 Days (B nozzle) | New dispensing hose replaced at B side - Old hose crimped and kept as spare - Working fine - Attended
CL3586 | 2023-07-30 | Melur | T | Dispensing line air hose damaged at tank area | Breakdown | Kathiresan | 2023-07-30 | - | Tank area to EB room dispensing line pneumatic hose replaced for 38 mtrs - Dispensing is fine - Completed
CL3587 | 2023-07-31 | Ammapet | D | Dispenser nozzle leakage | Breakdown | Prabu | 2023-07-31 | - | Nozzle leakage arrested by servicing - Tank area DP switch SS tube leakage arrested - Total leakage test done - Training provided for pump staffs - Resolved
CL3588 | 2023-07-31 | Sankari | A | Automation and camera maintenance | Preventive | Prabu | 2023-07-31 | - | Automation and camera maintenance done - Camera view checked - Completed
CL3589 | 2023-08-01 | Cantonment | A | Outlet going offline for automation wiring maintenance | Preventive | Madhavan | 2023-08-01 | - | IP interface board tested - Completed
CL3590 | 2023-08-02 | Udumalpet | A | Automation installation | Preventive | Gowtham, Prakash, Madhavan, Vigneshwaran and Arul Rayappan | 2023-08-03 | - | Automation installation done - Yenen is online and batchen is offline - Completed
CL3591 | 2023-08-02 | Omalur | T | N2 testing work | New Project | Prabu | 2023-08-02 | - | Tank N2 testing done - Holding pressure 10 kg/cm2 - Completed
CL3592 | 2023-08-03 | Chengalpattu | A | Preset is not working in mobile | Breakdown | Suneel Sagar | 2023-08-03 | - | Correction done in software database - Preset working fine - Resolved
CL3593 | 2023-08-04 | Namakkal 3 | T | Tank area vapour line ROV inside air leakage | Breakdown | Prabu and Nivas | 2023-08-20 | - | Ball valve with ROV sent to Vamaja - ROV serviced and fitted - Working fine - Rectified
CL3594 | 2023-08-04 | Vedachandur | G | Fire extinguiser refill and training | Preventive | Kamaraj | 2023-08-04 | - | Fire extinguisher refilling done - Fire safety training provided to pump staffs - General check up done - Attended
CL3595 | 2023-08-04 | Villapuram | T | ATG backup battery defect | Breakdown | Kathiresan | 2023-08-04 | - | 3V battery replaced with new - Working fine - Resolved
CL3596 | 2023-08-04 | Ellis Nagar | A | Dispenser A and B side bill printer not working | Breakdown | Kathiresan | 2023-08-21 | - | AB bill printer mother board replaced and 12V motor roller changed - Printer working fine - Resolved
CL3597 | 2023-08-04 | Cantonment | D | Yenen D nozzle leakage | Breakdown | Vigneshwaran | 2023-08-04 | - | Nozzle teeth 4 nos replaced - F nozzle front O ring replaced - Leakage arrested - Rectified
CL3598 | 2023-08-04 | Dharapuram | G | 3HP compressor pressure switch defect | Preventive | Thirumalaisamy | 2023-08-04 | - | Pressure switch cleaned and serviced - Working fine - Rectified
CL3599 | 2023-08-05 | Dharapuram | G | Fire extinguiser refill and training | Preventive | Gowtham | 2023-08-05 | - | Fire extinguisher serviced - One new 75 kg fire extinguisher provided - Fire safety training provided to pump staffs - All dispensing air hoses replaced - ALDS equipments working fine - Completed
CL3600 | 2023-08-05 | Vellakovil | G | Fire extinguiser refill and training | Preventive | Thirumalaisamy | 2023-08-05 | - | Fire extinguisher serviced - Fire safety training provided to pump staffs - General check up done - ALDS equipments working fine - Completed
CL3601 | 2023-08-06 | Avinashi | A | Batchen dispenser automation reconfiguration | Preventive | Gowtham | 2023-08-06 | - | Batchen dispenser automation configuration and ATG configuration done - Working good - Completed
CL3602 | 2023-08-06 | T.V.Kovil | D | C nozzle leakage | Breakdown | Avinash | 2023-08-06 | - | Nozzle teeth 4 nos replaced - Leakage arrested - Working fine - Resolved
CL3603 | 2023-08-06 | Omalur | G | Fire extinguisher installation | New Project | Prabu | 2023-08-06 | - | Fire extinguisher unloading, filling and checkup done - Fire safety training provided to pump staffs - Attended
CL3604 | 2023-08-06 | Sankari | G | Fire extinguisher service | Preventive | Prabu | 2023-08-06 | - | Fire extinguisher serviced - Fire safety training provided to pump staffs - Completed
CL3605 | 2023-08-07 | Udumalpet | A | Batchen dispenser automation reconfiguration | Preventive | Gowtham | 2023-08-07 | - | Automation reconfiguration done for Batchen dispenser - D nozzle hammer teeth 4 Nos replaced - Working fine - Attended
CL3606 | 2023-08-07 | T.V.Kovil | A | Yenen dispenser going offline for automation rewiring for changing the interface | New Project | Madhavan | 2023-08-07 | - | Both Yenen and Batchen dispenser communication interface changed from (RS485 to USB for Yenen and RS232 to USB for Batchen) interface to IP interface - Dispenser back online - Under observation - Completed
CL3607 | 2023-08-08 | Hosur | T | Unloading hose adapter replacing | Breakdown | Prabu | 2023-08-08 | - | Unloading hose adapter replaced - Leakage checked - Unloading done - Resolved
CL3608 | 2023-08-08 | Dindigul | C | Rule 18 work | Certification | Nepolean and Avinash | 2023-08-09 | - | Rule 18 done - SRV replaced with new one - Unloading fill point vapour ball valve replaced to arrest the leakage - Total area leakage checked - PMR done - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3609 | 2023-08-08 | Sulur | T | Dispensing motor running continuously in RUN mode due to NC element failure | Breakdown | Gowtham | 2023-08-08 | - | Dispensing and unloading selector switch NC element 2 nos, push button NO element 1 no replaced - Working fine - Udumalpet veeder root display installed - Nozzle hammer teeth 4 Nos replaced - Completed
CL3610 | 2023-08-08 | Ellis Nagar | R | Master solenoid valve in control panel defect | Breakdown | Kathiresan | 2023-08-08 | - | Master solenoid valve replaced - Surge arrester neutal changed - Working fine - Rectified
CL3611 | 2023-08-08 | Ariyamangalam | A | Batchen dispenser going offline to change IP communication interface from RS232 to USB interface | New Project | Madhavan | 2023-08-09 | - | IP interface changed - Testing : 74.73 L - Completed
CL3612 | 2023-08-08 | Krishnagiri | D | Dispenser cut off problem | Breakdown | Prabu | 2023-08-08 | - | Both side on/off switch replaced by new - Liquid flow valve adjusted - Tetsing : 18.99 L - Rectified
CL3613 | 2023-08-08 | Avinashi | T | Tank 2 unloading vapour ROV LPG leakage | Breakdown | Gowtham | 2023-08-08 | - | Unloading vapour ROV LPG leakage arrested by tightening the stem - Completed
CL3614 | 2023-08-09 | Avinashi | T | Unloading vapour hose brass adapter defect | Breakdown | Gowtham | 2023-08-09 | - | Brass adapater fixed at unloading vapour hose - Attended
CL3615 | 2023-08-09 | Villapuram | A | Dipenser going offline due to error 55 in Online UPS | Breakdown | Kathiresan | 2023-08-23 | - | Online UPS board short circuited - Sent to Mothish - Outlet back online with Offline UPS - Booster card and 7ah battery 3 Nos replaced in Online UPS - Working fine - Resolved
CL3616 | 2023-08-09 | Devakottai | G | Genset is flickering while turning it on sometimes | Breakdown | Nepolean | 2023-09-20 | - | Genset oil service done - AVR tuned and fixed - Kept under observation - Attended
CL3617 | 2023-08-09 | Ariyamangalam | A | C and D dispenser going offline | Breakdown | Madhavan | 2023-08-09 | - | Rewiring done - Dispenser back online - Rectified
CL3618 | 2023-08-09 | Vadivelan Nagar | R | Servo stabilzer Y phase control card problem | Breakdown | Suneel Sagar | 2023-08-10 | - | Y phase control card replaced - Performance is satisfactory - Resolved
CL3619 | 2023-08-09 | Ariyamangalam | G | Fire extinguisher service | Preventive | Nepolean | 2023-08-09 | - | Fire extinguisher service done - Completed
CL3620 | 2023-08-09 | Vedachandur | C | Rule 18 work | Certification | Nepolean and Avinash | 2023-08-09 | - | Rule 18, calibration and stamping done - stamping report: A side k factor: 10080 B side k factor: 10100 K factor No changes. A side 10 lit _ 9.96 lit B side 10 lit _. 9.97 lit Testing report: A side _ 143.48 lit B side _ 279.93 lit Total = 423.41 lit - Dispensing motor spider replaced - Leakage tested - PMR done - Total area leakage checked - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3621 | 2023-08-10 | Ariyamangalam | A | CD Dispenser going offline due to communication error | Breakdown | Madhavan | 2023-08-10 | - | Additional resistence added at the interface board end - Dispenser back online - Rectified
CL3622 | 2023-08-10 | Virudhunagar | R | Compressor running continuously | Breakdown | Kathiresan | 2023-08-10 | - | Dispensing solenoid valve plunger replaced and air hose replaced for 15 mtrs - Compressor working fine - N2 machine 6mm fittings 3 Nos replaced - Resolved
CL3623 | 2023-08-10 | Cantonment | D | B side On/Off switch not working | Breakdown | Chandrasekar | 2023-08-10 | - | New On/Off switch replaced - Working fine - Testing : 0.93 L - Rectified
CL3624 | 2023-08-10 | Aravakurichi | C | Rule 18 work | Certification | Nepolean and Avinash | 2023-08-10 | - | Rule 18 done - Both tank and dispensers leakage test done - PMR done - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3625 | 2023-08-10 | Rasipuram | A | Totalizer reversed due to voltage fluctuation | Breakdown | Madhavan | 2023-08-10 | - | Fluctuation adjusted and permission given - Resolved
CL3626 | 2023-08-11 | Kattupakkam | G | Sales stopped due to EB power failure and Genset battery down | Breakdown | Suneel Sagar | 2023-08-11 | 45 Mins | Genset battery recharged - Sales started - Attended
CL3627 | 2023-08-11 | Palladam | D | A and B nozzle defect | Breakdown | Gowtham | 2023-08-11 | - | Both nozzles interchanged - Unloading motor belt 2 Nos replaced - Testing : 0.93 Ltrs - Rectified
CL3628 | 2023-08-12 | Cantonment | D | C side nozzle latch broken | Breakdown | Chandrasekar | 2023-08-12 | - | C nozzle latch replaced - D side keypad replaced - Display housing front glass changed - Completed
CL3629 | 2023-08-12 | Mulanur | C | Rule 18 work | Certification | Nepolean and Avinash | 2023-08-12 | - | Rule 18 done - Both tank and dispensers leakage test done - PMR done - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3630 | 2023-08-12 | Vellakovil | C | Rule 19 data collection | Preventive | Nepolean and Avinash | 2023-08-12 | - | Material requirments and data for Rule 19 taken - Attended
CL3631 | 2023-08-12 | Palayam | C | Rule 18 work | Certification | Nepolean, Thirumalaisamy and Avinash | 2023-08-12 | - | Rule 18 done - Both tank and dispensers leakage test done - PMR done - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3632 | 2023-08-13 | Avinashi | T | Tank 1 unloading cant be done due to liquid line ROV leakage | Breakdown | Prabu | 2023-08-13 | - | Liquid line ROV leakage arrested by tightening the stem - Dispenser C side nozzle rope replaced - Unloading done - Completed
CL3633 | 2023-08-13 | Velachery | G | sales stopped due to R phase input wire loose contact in panel terminal | Breakdown | Suneel Sagar | 2023-08-13 | 1 Hour | Wiring reconnected - ALDS can be operated in both EB and DG - Rectified
CL3634 | 2023-08-13 | Ariyamangalam | D | B side nozzle lock defect | Breakdown | Pandi Durai | 2023-08-13 | - | Nozzle lock replaced at B side - Working fine - Resolved
CL3635 | 2023-08-15 | Tiruvaiyaru | R | Servo stabilizer not working properly when EB one phase not detected | Breakdown | Nepolean and Vignesh | 2023-08-15 | - | Servo stabilizer coil serviced - Working fine - Resolved
CL3636 | 2023-08-15 | Erode | R | Compressor cut off not working | Breakdown | Thirumalaisamy | 2023-08-15 | - | Compressor pressure switch replaced - compressor oil changed - A nozzle 5 Mtr dispensing hose replaced - Nozzle hammer teeth replaced to arrest leakage - Online UPS topped up with distilled water - PMR done - Automation equipment maintenance done - Completed
CL3637 | 2023-08-15 | Rasipuram | G | Fire extinguisher service | Preventive | Prabu | 2023-08-15 | - | Fire extinguisher service done - Safety training provided to pump staff - Completed
CL3638 | 2023-08-15 | Ayothiyapattinam | G | Fire extinguisher service | Preventive | Prabu | 2023-08-15 | - | Fire extinguisher service done - Safety training provided to pump staff - Completed
CL3639 | 2023-08-15 | Madurai 3 - Sivagangai Road | T | Tank area and pit marking | New Project | Kathiresan | 2023-08-15 | - | Tank area and tank pit marking done - Attended
CL3640 | 2023-08-16 | Tiruchengode | C | Stamping work | Certification | Nepolean and Avinash | 2023-08-17 | - | Stamping work done - Calibration report A side k factor: 10000 B side k factor : 10000 A side 10 lit =9.98 lit B side 10 lit = 9.97 lit Testing A side : 145.37 lit B side : 145.66 lit K factor No changes - Completed
CL3641 | 2023-08-16 | Paramathivelur | G | Fire extinguisher service | Preventive | Thirumalaisamy | 2023-08-16 | - | Fire extinguisher service done - Safety training provided to pump staff - Completed
CL3642 | 2023-08-16 | Pudukottai | G | EB RYB phase short circuited | Breakdown | Pandi Durai | 2023-08-16 | - | EB phase reconnected by TNEB person - B nozzle hammer teeth 4 Nos replaced - Air machine clip connector replaced - Decanting liquid line ROV leakage arrested by tightening the stem - Resolved
CL3643 | 2023-08-16 | Velachery | R | Control panel terminal connectors loose contact | Preventive | Suneel Sagar | 2023-08-16 | - | Control panel terminal connectors replaced - Attended
CL3644 | 2023-08-17 | Sankari | C | Stamping work | Certification | Nepolean and Avinash | 2023-08-17 | - | Stamping work done - Calibration report A side k factor: 10100 B side k factor : 10100 A side 10 lit= 9.95 lit B side 10 lit = 9.96 lit Testing: A side : 135.17 lit B side : 150.15 lit K factor No changes - Complted
CL3645 | 2023-08-18 | Virudhunagar | D | Dispenser bottom ROV not working | Breakdown | Kathiresan | 2023-08-18 | - | Dispenser bottom air hose replaced for 35 Mtrs - Spare line installed - NVR hard disk replaced - Resolved
CL3646 | 2023-08-18 | Velachery | T | Dispensing motor spider damaged | Breakdown | Suneel Sagar | 2023-08-18 | - | Spider replaced - Dispensing motor working fine - Rectified
CL3647 | 2023-08-18 | Madurai 3 - Sivagangai Road | T | Tank installation and concrete work | New Project | Kathiresan | 2023-08-18 | - | Tank installed and concrete foundation work done - Completed
CL3648 | 2023-08-18 | Kangeyam | C | DL Stamping and Rule 18 work | Certification | Nepolean and Avinash | 2023-08-18 | - | DL Stamping and Rule 18 done - Completed
CL3649 | 2023-08-18 | Dharapuram | C | DL Stamping and Rule 18 work | Certification | Nepolean and Avinash | 2023-08-18 | - | DL Stamping and Rule 18 done - Completed
CL3650 | 2023-08-18 | Vellakovil | C | DL Stamping work | Certification | Nepolean and Avinash | 2023-08-18 | - | DL Stamping done - Completed
CL3651 | 2023-08-19 | Ellis Nagar | R | Spark at B phase winding servo stabilzer | Breakdown | Kathiresan | 2023-08-19 | - | Step up motor refitted and new carbon bush replaced - Stabilizer working finr - Resolved
CL3652 | 2023-08-19 | Palladam 1 | C | Rule 18 work | Certification | Nepolean, Gowtham and Avinash | 2023-08-19 | - | Rule 18 done - Completed
CL3653 | 2023-08-19 | Palladam 2 | C | DL Stamping and Rule 18 work | Certification | Nepolean, Gowtham and Avinash | 2023-08-19 | - | DL Stamping and Rule 18 done - Completed
CL3654 | 2023-08-19 | Avinashi | C | DL Stamping work | Certification | Nepolean, Gowtham and Avinash | 2023-08-19 | - | DL Stamping done - Completed
CL3655 | 2023-08-20 | Thanjavur | T | Unloading work | Preventive | Pandi Durai | 2023-08-20 | - | Unloading done - Unloading training provided to pump staffs - PMR done - Attended
CL3656 | 2023-08-21 | Tharamangalam | D | Motherboard hanging - Error 21 occurred | Breakdown | Prabu | 2023-08-21 | - | Mother board cables and power cable reconnected - Error cleared - Rectified
CL3657 | 2023-08-21 | Pudukottai | A | Dispenser going offline due to CPU fan issue | Breakdown | Madhavan | 2023-08-21 | - | Spare CPU replaced - Dispenser back online - Working fine - Attended
CL3658 | 2023-08-22 | Sulur | C | DL Stamping and Rule 18 work | Certification | Nepolean, Gowtham and Avinash | 2023-08-22 | - | DL Stamping and Rule 18 done - Completed
CL3659 | 2023-08-22 | Neelambur | C | DL Stamping and Rule 18 work | Certification | Nepolean, Gowtham and Avinash | 2023-08-22 | - | DL Stamping and Rule 18 done - Completed
CL3660 | 2023-08-22 | Salem 2 | G | Site visit | New Project | Prakash, Vigneshwaran and Krishnabalaji | 2023-08-22 |  | Marking instructions provided - Site visit done - Completed
CL3661 | 2023-08-22 | Namakkal 2 | C | PMR work | Preventive | Nivas | 2023-08-22 | - | PMR done - Completed
CL3662 | 2023-08-22 | Saravanampatty | C | Stamping and Rule 18 work | Certification | Nepolean, Gowtham and Avinash | 2023-08-22 | - | Stamping and Rule 18 done - Completed
CL3663 | 2023-08-23 | Thuraiyur | C | PMR work | Certification | Nivas | 2023-08-23 | - | PMR done - Completed
CL3664 | 2023-08-23 | Udumalpet | C | Rule 18 work | Certification | Nepolean and Avinash | 2023-08-23 | - | Rule 18 done - Completed
CL3665 | 2023-08-24 | Mulanur | A | Automation maintenance | Preventive | Thirumalaisamy | 2023-08-24 | - | Online Ups inbuilt battery 3 Nos and offline UPS battery 1 No replaced due to back up issue - Equipment maintenance done - Working fine - Rectified
CL3666 | 2023-08-24 | Perambalur | A | Firewall power cable not working | Breakdown | Avinash | 2023-08-24 | - | Power cable replaced - Working fine - Resolved
CL3667 | 2023-08-24 | Rasipuram | A | Automation maintenance and PMR work | Preventive | Nivas | 2023-08-24 | - | Automation maintenance done - PMR done - Collected the data of required materials for Rule 19 - Attended
CL3668 | 2023-08-24 | Cantonment | G | N2 air machine nozzle defect | Breakdown | Chandrasekar | 2023-08-24 | - | N2 machine nozzle replaced - Completed
CL3669 | 2023-08-24 | Madurai 3 - Sivagangai Road | T | Tank hydro test | New Project | Kathiresan | 2023-08-24 | - | Hydro test done at pressure 29 Kg cm2 - Completed
CL3670 | 2023-08-25 | Ayothiyapattinam | C | Stamping and Rule 18 work | Certification | Vignesh, Prabu and Lingeshwaran | 2023-08-25 | - | Stamping and Rule 18 done - K factors no change. A side 10000 B side 10000 A side 10= 9.96 lit B side 10= 10.05lit - Both tank and dispensers leakage test done - PMR done - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3671 | 2023-08-25 | Kumbakonam | D | Dispenser bottom liquid line ROV air leakage | Breakdown | Pandi Durai | 2023-08-25 | - | Dispenser bottom liquid line ROV replaced with new - Leakage arrested - Working fine - Resolved
CL3672 | 2023-08-25 | T.V.Kovil | D | A nozzle teeth worn out | Breakdown | Suresh Kumar | 2023-08-25 | - | Nozzle hammer teeth 4 Nos replaced - Working good - Rectified
CL3673 | 2023-08-25 | Tharamangalam | C | Stamping and Rule 18 work | Certification | Vignesh, Prabu and Lingeshwaran | 2023-08-25 | - | Stamping and Rule 18 done - K factors no change. A side 10250 B side 10250 A side 10= 9.97 lit B side 10= 10.01lit Testing A side 141.77 B side 100.07 Total testing 241.84lit - Both tank and dispensers leakage test done - PMR done - Earth generated - Automation maintenance done - Safety training provided - Completed
CL3674 | 2023-08-26 | Attur | D | Batchen dispenser metering unit LPG leakage | Breakdown | Nivas | 2023-08-26 | - | Metering unit bearing, seal kit and center O ring replaced - LPG leakage arrested - Rectified
CL3675 | 2023-08-26 | Pudukottai | D | B side keypad not working properly | Breakdown | Pandi Durai | 2023-08-26 | - | New keypad replaced - Working fine - Resolved
CL3676 | 2023-08-27 | Thanjavur | D | B side flow jumping | Breakdown | Chandrasekar | 2023-08-27 | - | DP valve diaphragm replaced with new and spring tension adjusted - A. Side testing. 5 L - B. Side testing. 10 L - Resolved
CL3677 | 2023-08-27 | Dharmapuri | C | Stamping and Rule 18 work | Certification | Prabu | 2023-08-27 | - | Rule 18 done - Both tank and dispensers leakage test done - PMR done - Earth generated - Both compressor oil level and battery water level topped up - Automation maintenance done - Safety training provided - Completed
CL3678 | 2023-08-28 | Madurai 3 - Sivagangai Road | T | CP installation | New Project | Kathiresan | 2023-08-28 | - | CP installation done - Report: R1 - C1 = -0.712 R1 - C2 = -0.718 R1 - A1 = -1.565 R1 - A2 = -1.568 R1 - A3 = -1.555 R1 - A4 = -1.553 After Looping = -1.372 - Completed
CL3679 | 2023-08-28 | Krishnagiri | C | Stamping and Rule 18 work | Certification | Prabu | 2023-08-28 | - | Rule 18 done - Both tank and dispensers leakage test done - PMR done - Earth generated - Both compressor oil level and battery water level topped up - Automation maintenance done - Safety training provided - A nozzle replaced due to defect - K factors - A side 10000 B side 10000 Testing A side 155.24 B side 150.01 Total testing 305.25lit - Completed
CL3680 | 2023-08-29 | Villapuram | D | C nozzle leakage due to nozzle mount defect | Breakdown | Kathiresan | 2023-08-29 | - | Spare nozzle replaced - Working good - Rectified
CL3681 | 2023-08-29 | Kumbakonam | R | Dispensing air solenoid coil leakage | Breakdown | Suresh Kumar | 2023-08-29 | - | Air solenoid coil replaced - Air leakage arrested - Working fine - Resolved
CL3682 | 2023-08-29 | KR Gases | C | Ammonia tank SRV and unloading hose testing | Certification | Prabu | 2023-08-29 | - | Ammonia tank SRV and unloading hose testing done - Completed
CL3683 | 2023-08-29 | Hosur | C | Dispenser stamping and Rule 18 work | Certification | Prabu | 2023-08-29 | - | Dispenser calibration and stamping done - Rule 18 done - Tank and dispensers leakage test done - PMR done - Earth generated - Both compressor oil level and battery water level topped up - Automation maintenance done - Safety training provided - K factors not changed. A side 9600 B side 9950 Testing A side 289.71 B side 149.62 Total testing 439.36lit - Completed
CL3684 | 2023-08-29 | Chennai - Madhavaram | G | Site civil marking | New Project | Prakash | 2023-08-29 | - | Civil marking done - Attended
CL3685 | 2023-08-30 | Tiruvaiyaru | D | A side keypad preset not working due to loose contact | Breakdown | Suresh Kumar | 2023-08-30 | - | Keypad cable reconnected - Working fine - Rectified
CL3686 | 2023-08-30 | Bathlagundu | D | A nozzle defect | Breakdown | Kamaraj | 2023-08-30 | - | Nozzle teeth serviced - Dispenser bottom ROV stem LPG leakage arrested by tightening the stem - General check up done - Completed
CL3687 | 2023-08-30 | Ariyamangalam | D | Metering unit stuck up | Breakdown | Chandrasekar | 2023-08-30 | - | Oil poured inside metering unit to avoid friction - Testing : 30.86 L - Resolved
CL3688 | 2023-08-30 | Bodi | R | Offline UPS battery drained | Breakdown | Kamaraj | 2023-08-31 | - | Offline UPS battery replaced with new - Automation maintenance done - Attended
CL3689 | 2023-08-30 | Sulur | D | Dispensing area air hose leakage | Breakdown | Gowtham | 2023-08-30 | - | Air hose partially replaced at dispenser side - Air leakage not found and compressors working fine - Attended
CL3690 | 2023-08-30 | Uthamapalayam | C | Rule 18 work | Certification | Prabu | 2023-08-30 | - | Rule 18 done - Tank and dispensers leakage test done - PMR done - Earth generated - Both compressor oil level and battery water level topped up - Automation maintenance done - Safety training provided - Completed
CL3691 | 2023-08-31 | Velachery | T | Dispensing motor winding short | Breakdown | Suneel Sagar | 2023-08-31 | - | Dispensing motor replaced with new - Resolved
CL3692 | 2023-08-31 | Erode | G | PMR and Safety training | Preventive | Avinash | 2023-08-31 | - | PMR done - Safety training provided to pump staffs - Completed
CL3693 | 2023-08-31 | Salem | C | Rule 18 work | Certification | Prabu | 2023-08-31 | - | Rule 18 done - Tank and dispensers leakage test done - PMR done - Earth generated - Both compressor oil level and battery water level topped up - Automation maintenance done - Safety training provided - Completed
CL3694 | 2023-08-31 | Uthamapalayam | T | Dispensing motor spider damaged and dispensing air hose leakage | Breakdown | Kamaraj | 2023-08-31 | - | Dispensing motor spider replaced with new - Dispensing air hose replaced - Air compressor oil changed - Defected canopy light sent to classic cables - Leakage tested completely - Resolved
CL3695 | 2023-09-01 | Ariyamangalam | D | D side metering unit stuck up | Breakdown | Nepolean | 2023-09-01 | - | Metering unit bearing and seal kit replaced - D side Testing : 16.27 L - Resolved
CL3696 | 2023-09-01 | Namakkal 1 | T | Unloading liquid line ROV with ball valve LPG leakage | Breakdown | Nivas | 2023-09-01 | - | ROV with ball valve LPG leakage by tightening the stem - PMR done - Rectified
CL3697 | 2023-09-01 | Madurai 3 - Sivagangai Road | G | Site marking | New Project | Kathiresan | 2023-09-01 | - | Decanting and dispensing motor marking done - Attended
CL3698 | 2023-09-02 | Tiruchengode | T | Dispensing motor noise due to misalignment | Breakdown | Avinash | 2023-09-02 | - | Motor alignment done - PMR done - Safety training given to pump staffs - Completed
CL3699 | 2023-09-02 | Mulanur | G | Unloading training | Preventive | Thirumalaisamy | 2023-09-02 | - | Unloading training done - Attended
CL3700 | 2023-09-03 | Ammapet | G | Outlet visit | Preventive | Avinash | 2023-09-02 | - | PMR done - Problematic printer sent to Chennai for servicing - Printer received on 09.09.2023 - Safety training given to pump staffs - Completed
CL3701 | 2023-09-03 | Aravakurichi | R | Panel not working in stabilizer mode | Breakdown | Thirumalaisamy | 2023-09-03 | - | R and B phase fuse replaced - Complaint logged to Infonet that the IP camera was not working - Dispenser running in stabilizer mod - Rectified
CL3702 | 2023-09-04 | Devakottai | G | Nitrogen machine air compressor problem | Breakdown | Nepolean | 2023-09-04 | - | DOL starter coil Amps increased - Working fine - Resolved
CL3703 | 2023-09-04 | Thanjavur | R | Dispensing compressor running continuously | Breakdown | Pandi Durai | 2023-09-04 | - | Dispensing line air hose damaged line replaced with new line - Compressor running smoothly - Attended
CL3704 | 2023-09-04 | Viruthachalam | T | Dispensing motor love joy coupling spider damage | Breakdown | Suresh Kumar | 2023-09-04 | - | Love joy coupling spider replaced - Working fine - Resolved
CL3705 | 2023-09-04 | Melur | G | Fire extinguisher service | Preventive | Kathiresan | 2023-09-04 | - | Fire extinguisher service done - Fire safety training provided - Completed
CL3706 | 2023-09-05 | Bodi | T | Dispensing motor not working in run mode | Breakdown | Kamaraj | 2023-09-05 | - | W1 contactor interchanged in control panel - Working in run mode - Rectified
CL3707 | 2023-09-05 | Ariyamangalam | C | Calibration work | Certification | Nepolean | 2023-09-05 | - | Calibration done - Testing litres A side - 123.39 B side - 137.59 C side - 159.80 D side - 151.77 Total testing litres - 572.55 - Completed
CL3708 | 2023-09-06 | Paramathivelur | G | Bore well process | Breakdown | Thirumalaisamy | 2023-09-06 | 2.30 Hours | Bore well process done - Attended
CL3709 | 2023-09-06 | Ariyamangalam | D | D nozzle low flow and slow delivery | Breakdown | Nepolean | 2023-09-06 | - | Low flow high flow solenoid valve cleaned - Working fine - Testing : 6.84 L - Resolved
CL3710 | 2023-09-06 | Madurai 3 - Sivagangai Road | G | Site marking | New Project | Kathiresan | 2023-09-06 | - | Dispenser and trench marking done - Canopy piller marking done - Attended
CL3711 | 2023-09-06 | Theni | T | Dispensing and decanting air hose damaged | Breakdown | Kamaraj | 2023-09-06 | - | Dispensing and decanting air hose replaced with new - 1 KVA online UPS battery 3 Nos replaced on - General check up done - Rectified
CL3712 | 2023-09-06 | Erode | R | Offline UPS battery back up problem | Breakdown | Avinash | 2023-09-06 | - | 12V 7AH battery 3 Nos replaced - B nozzle 4 Nos replaced - Working fine - Resolved
CL3713 | 2023-09-07 | Musiri | R | Error 15 occurred on Online UPS | Breakdown | Nivas | 2023-09-07 | - | Online UPS wirings and boards cleaned and reconnected - Automation maintenance done - PMR done - Working fine - Rectified
CL3714 | 2023-09-07 | Udumalpet | A | New automation board installation for Batchen dispenser | Preventive | Gowtham | 2023-09-07 | - | New automation board installed - Dispenser preset cut off problem kept under observation - Working fine - Resolved
CL3715 | 2023-09-07 | Thanjavur | D | Dispenser flow jumping at B side | Breakdown | Chandrasekar | 2023-09-07 | - | Differential pressure valve spring changed - B side Testing : 5 L - Working fine - Attended
CL3716 | 2023-09-07 | Ariyamangalam | C | DL Stamping | Certification | Nepolean | 2023-09-07 | - | DL Stamping done - Testing at C side : 50.82 L - Completed
CL3717 | 2023-09-07 | Ellis Nagar | D | C side keypad not working properly | Breakdown | Kathiresan | 2023-09-07 | - | C side keypad is interchanged with D side keypad - C side is now working fine - D side keypad to be replaced - Attended
CL3718 | 2023-09-08 | Sankari | G | Online UPS battery back up problem | Preventive | Avinash | 2023-09-08 | - | 12V 7AH battery 3 Nos replaced - PMR done - Working fine - Completed
CL3719 | 2023-09-08 | Hosur | G | Genset not working due to battery drained | Breakdown | Prabu | 2023-09-08 | 20 Minutes | Genset battery replaced - Working in Genset mode - Resolved
CL3720 | 2023-09-08 | Thuraiyur | D | Batchen dispenser A side low flow and slow delivery | Breakdown | Nivas | 2023-09-08 | - | Differential pressure valve cleaned to increase the speed of delivery - Working fine - Tank area liquid line ROV with ball valve stuck up released - A side testing : 3.67 L - Working fine - Resolved
CL3721 | 2023-09-08 | Vadivelan Nagar | T | Temperature gauge not working | Breakdown | Suneel Sagar | 2023-09-08 | - | Temperature gauge cleaned and adjusted as per ATG temperature - Working fine - Resolved
CL3722 | 2023-09-08 | Ariyamangalam | D | New sample teeth fitting on B and D side | Preventive | Nepolean | 2023-09-08 | - | Nozzle teeth replaced on both the nozzles for testing purpose - Attended
CL3723 | 2023-09-08 | Aravakurichi | C | Calibration and stamping work | Certification | Thirumalaisamy and Chandrasekar | 2023-09-08 | - | Calibration and stamping done - "A" side 10 ltrs =9.94 "B" side 10 ltrs = 9.95 "K" Factor reports:- "A" side 'K' factor = 10100 "B" side 'K' factor= 10100 "K" Factor no change Testing liters:- A-Nozzle:113.25 L B-Nozzle:151.16 L Total testing: 264.41L - Completed
CL3724 | 2023-09-08 | Puliyur | C | Calibration and stamping work | Certification | Thirumalaisamy and Chandrasekar | 2023-09-08 | - | Calibration and stamping done - "A" side 10 ltrs =9.95ltrs "B" side 10 ltrs = 9.95ltrs "K" Factor reports:- "A" side 'K' factor = 10050 "B" side 'K' factor= 10050 "K" Factor no change Testing liters:- A-Nozzle:110.99 L B-Nozzle:107.47 L Total testing:218.46 L - Completed
CL3725 | 2023-09-08 | Tiruchengode | T | ATG hanging | Breakdown | Avinash | 2023-10-09 | - | SSR file in SD card corrupted - New SD card installed with new program - Resolved
CL3726 | 2023-09-09 | Nasiyanur | G | General outlet visit | Preventive | Avinash | 2023-09-09 | - | PMR done - Automation maintenance done - Safety training provided to pump staffs - Attended
CL3727 | 2023-09-09 | Kumbakonam | T | Dispensing vapour line ROV not working properly | Breakdown | Pandi Durai | 2023-09-09 | - | Dispensing vapour line ROV serviced and refitted - decanting vapour line ROV leakage arrested by tightening the stem - Dispensing and decanting line pneumatic hose replaced - Working fine - Completed
CL3728 | 2023-09-11 | Ammapet | T | ATG signal cable damaged due to rat bite | Breakdown | Avinash | 2023-09-11 | - | Signal cable rewiring done - Cable covered with PVC hose - ATG is live - Rectified
CL3729 | 2023-09-11 | Bhavani | G | General outlet visit | Preventive | Avinash | 2023-09-11 | - | Offline UPS battery back up battery replaced - PMR done - Control panel B phase indicator light replaced - Rule 19 material requirement data collected - Completed
CL3730 | 2023-09-11 | Cantonment | D | Nozzle hose sleeve damage | Breakdown | Chandrasekar | 2023-09-11 | - | C nozzle 5m dispensing hose and 1/2m dispensing hose replaced - Testing : 0.82 L - Resolved
CL3731 | 2023-09-11 | Thiruvaiyaru | D | Dispenser light starter problem | Breakdown | Pandi Durai | 2023-09-11 | - | Dispenser light starter 2 Nos replaced - PMR done - Completed
CL3732 | 2023-09-12 | Cantonment | D | Batchen B side on/off switch not working | Breakdown | Nepolean | 2023-09-12 | - | New On/Off switch replaced - Working fine - Testing : 3.46 L - Rectified
CL3733 | 2023-09-12 | Cantonment | D | Batchen dispenser metering unit pressure gauge top leakage | Breakdown | Nepolean | 2023-09-12 | - | New pressure gauge replaced - Working fine - Resolved
CL3734 | 2023-09-13 | Vadivelan Nagar | C | Calibration and Rule 18 work | Certification | Chandrasekar and Suresh Kumar | 2023-09-13 | - | Calibration and Rule 18 done - A.side old k factor.10110 A.side new k factor.10070 B.side old k factor.10160 B.side new k factor.10070 C.side old k factor.10160 C.side new k factor.10080 D.side old k factor.10100 D.side new k factor.10080 All pump k factor changed. A.Testing.234.27 B.Testing.182.07 C.Testing.145.35 D.Testing.107.50 Total Testing.669.19 Sales A.10=10.14 B.10=10.15 C.10=10.14 D.10=10.16 - Completed
CL3735 | 2023-09-13 | Velachery | C | Calibration and Rule 18 work | Certification | Chandrasekar and Suresh Kumar | 2023-09-13 | - | Calibration and Rule 18 done - AB.Dispenser Density changed. Old Density.0.562 New Density.0.550 CD.Dispenser Density changed. Old Density.0.542 New Density.0.535 Density changed only for Kalvacha Dispenser A.Testing.365.10 B.Testing.195.95 C.Testing.87.95 D.Testing.90.80 Total Testing.739.80 Sales A.10=10.12 B.10=10.16 C.10=10.16 C.10=10.15 Thank you
CL3736 | 2023-09-13 | Perundurai | G | PMR and Automation maintenance work | Preventive | Avinash | 2023-09-13 | - | PMR done - Automation maintenance done - Tank area dispensing line vapour ROV ball valve LPG leakage arrested by tightening the stem - Safety training provided to pump staffs - Completed
CL3737 | 2023-09-13 | Kattupakkam | C | Rule 18 work | Certification | Chandrasekar and Suresh Kumar | 2023-09-13 | - | Rule 18 work done - Attended
CL3738 | 2023-09-14 | Madurai 3 - Sivagangai Road | T | Tank flanges removal and EFV fitting | New Project | Kathiresan | 2023-09-14 | - | Tank big and small flanges removed and Excess Flow Valve fitted - Completed
CL3739 | 2023-09-14 | Tirunelveli | T | Tank 1 vapour ball valve with ROV not working | Breakdown | Kathiresan | 2023-09-15 | - | 40 NB Ballvalve with ROV replaced with new - Insulation gasket replaced - No leakage found - Automation camera CAT 6 cable to be replaced - Rectified
CL3740 | 2023-09-14 | Dharmapuri | T | Unloading ROV not working properly | Breakdown | Prabu | 2023-09-15 | - | Unloading solenoid coil block removed - ROV working now and unloading done - Canopy light replaced - Resolved
CL3741 | 2023-09-14 | Kodungaiyur | C | Rule 18 work | Certification | Chandrasekar and Suresh Kumar | 2023-09-14 | - | Rule 18 work done - Attended
CL3742 | 2023-09-14 | Avadi | C | Rule 18 work | Certification | Chandrasekar and Suresh Kumar | 2023-09-14 | - | Rule 18 work done - Attended
CL3743 | 2023-09-15 | Chengalpattu | C | Rule 18 work | Certification | Chandrasekar and Suresh Kumar | 2023-09-15 | - | Rule 18 work done - Attended
CL3744 | 2023-09-15 | Krishnagiri | D | Dispenser display cable defect | Breakdown | Prabu | 2023-09-15 | - | Display cable replaced - Working fine - Rectified
CL3745 | 2023-09-15 | Ariyalur | D | B nozzle lock defect | Breakdown | Pandi Durai | 2023-09-15 | - | B nozzle lock set replaced with new - Nozzle working good - Rectified
CL3746 | 2023-09-15 | Thuraiyur | R | Compressor running continuously | Breakdown | Nivas | 2023-09-16 | - | Dispenser bottom damaged air hose replaced for 30 Mtrs - Spare line installed for dispensing line - Resolved
CL3747 | 2023-09-16 | Perambalur | R | Isolator switch defect | Breakdown | Pandi Durai | 2023-09-16 | - | Switch looped - Transformer input voltage adjusted - Resolved temporarily | Isolator switch to be replaced
CL3748 | 2023-09-17 | Bhavani | T | CP testing | Preventive | Avinash | 2023-09-17 | - | CP found failure - Checked with CP person - CP reading . A1R1=1.359 A2R1=0.260 A3R1=0.383 A4R1=1.206 R1C1=0.338 R1C2=0.339 After looping=0.395 | CP to be replaced at Rule19
CL3749 | 2023-09-17 | Aravakurichi |  | CP testing | Preventive | Thirumalaisamy | 2023-09-17 | - | CP found satisfactory - Checked with CP person - CP readings : A1R1=-1.414 A2R1=-1.371 A3R1=-1.438 A4R1=-1.482 R1C1=-0.475 R1C2=-0.475 After looping=-1.027 - Attended
CL3750 | 2023-09-18 | Avinashi | T | Dispensing motor suction problem due to high pressure developed | Breakdown | Gowtham | 2023-09-18 | - | Bypass valve cleaned and equalizer valve adjusted - Kept under observation - Testing ltr A side -117.01 ltr - Working fine - Resolved
CL3751 | 2023-09-18 | Madurai 3 - Sivagangai Road | T | Tank area welding work | New Project | Kathiresan | 2023-09-18 | - | Tank area welding work done - Canopy piller foundation work done - Rule 33 data collected - Attended
CL3752 | 2023-09-19 | Nasiyanur | G | Unloading training | Preventive | Avinash | 2023-09-19 | - | Unloading done and unloading training provided to pump staffs - Completed
CL3753 | 2023-09-19 | Namakkal 3 | C | Calibration and stamping work | Certification | Chandrasekar and Nivas | 2023-09-19 | - | Calibration and stamping done - Calibration details: "A" side 10 ltrs = 9.99 "B" side 10ltrs = 10.01 "K" Factor reports: A side k Factor= 10150 B side K Factor= 10150 K Factor No change Testing liters: A -Nozzle : 118.61 ltrs B- Nozzle : 139.22 ltrs Total testing : 257.83 ltrs - Completed
CL3754 | 2023-09-19 | Udumalpet | A | Automation training | Preventive | Gowtham | 2023-09-19 | - | Automation Online and Offline operation mode changing with working process explained to dealer alongwith incharge - Yenen dispenser Automation (CAT 6) bed switch cable damaged. So bed switch directly installed in dispenser - Completed
CL3755 | 2023-09-19 | Thanjavur | C | Dispensing not working in genset mode | Certification | Pandi Durai | 2023-09-19 | - | Genset frequency adjusted for run mode -Working fine - Completed
CL3756 | 2023-09-19 | Cantonment | D | C nozzle lock defect | Breakdown | Nepolean | 2023-09-19 | - | C nozzle yenen lock set replaced - Working fine - Rectified
CL3757 | 2023-09-19 | Namakkal 1 | T | Unloading liquid hose brass adapter LPG leakage | Breakdown | Nivas | 2023-09-19 | - | Liquid hose brass adapter LPG leakage arrested by applying araldite and refitted - Kept under observation untill next unloading - Attended
CL3758 | 2023-09-20 | Saravanampatty | D | Dispenser slow delivery due to pressure drop | Breakdown | Gowtham | 2023-09-20 | - | Bypass valve serviced - Pressure increased upto 14.5 kg/cm2 - Compressor oil changed - Completed
CL3759 | 2023-09-20 | Bathlagundu | G | General outlet visit | Preventive | Kamaraj | 2023-09-20 | - | All leakage checked - Completed
CL3760 | 2023-09-20 | Kodungaiyur | D | Breakaway coupling rope damaged | Breakdown | Suneel Sagar | 2023-09-20 | - | New breakaway coupling replaced - Working fine - Resolved
CL3761 | 2023-09-20 | Ariyamangalam | D | B nozzle LPG leakage | Breakdown | Nepolean | 2023-09-20 | - | Serviced nozzle replaced at B side - Working fine - Testing : 1.11 Ltrs - Resolved
CL3762 | 2023-09-20 | Madurai 3 - Sivagangai Road | D | Dispenser installation | New Project | Kathiresan | 2023-09-20 | - | Dispenser installed - Pipeline hydro test done - Testing pressure 48 kg/cm2 - Found satisfactory - Canopy piller foundation done - Completed
CL3763 | 2023-09-20 | Neelambur | D | D nozzle hammer teeth defect | Breakdown | Gowtham | 2023-09-20 | - | Hammer teeth 4 Nos replaced - Attended
CL3764 | 2023-09-20 | Sulur | D | Dispensing solenoid valve not working properly | Breakdown | Gowtham | 2023-09-20 | - | Dispensing solenoid valve replaced - Working fine - Rectified
CL3765 | 2023-09-21 | Vellakovil | C | Rule 19 work started and sales stopped | Certification | Chandrasekar. Thirumalaisamy and Lingeshwaran | 2023-09-23 | From 21.09.2023 - 6.30pm to 23.09.2023 3.40am | Rule 19 done - Tank commissioning done - Sales started - Rule 18 done - ATG installation and automation installation partially done - All equipments working fine - Completed
CL3766 | 2023-09-21 | Velachery | D | A nozzle 5m dispensing hose and D nozzle 0.5m dispensing hose defect | Breakdown | Suneel Sagar | 2023-09-21 | - | A nozzle 5m dispensing hose and D nozzle 0.5m dispensing hose replaced - B, C and D dispensing hose recrimped and tested @ 12kg - Found satistactory - All 4 nozzle breakaway coupling serviced - Unloading filter cleaned - Working fine - Resolved
CL3767 | 2023-09-21 | Cantonment | D | Nozzle replacement | Preventive | Nepolean | 2023-09-21 | - | Nozzle replaced at B, C and D sides - A side nozzle replaced with old service nozzle - Found no leakage - Testing litres: B side : 1.14 C side: 0.92 D side: 0.97 A side: 1.19 Total: 4.22 L - Rectified
CL3768 | 2023-09-22 | Thanjavur | G | Fire extinguisher service work | Preventive | Pandi Durai | 2023-09-22 | - | 9 kg fire extinguisher hose replaced - Service done - Fire safety training provided to pump staffs - Completed
CL3769 | 2023-09-22 | Velachery | G | Fire extinguisher hose damaged | Preventive | Suneel Sagar | 2023-09-22 | - | Fire extinguisher hose replaced - Attended
CL3770 | 2023-09-22 | Namakkal 3 | C | PMR work | Preventive | Nivas | 2023-09-22 | - | PMR done - Completed
CL3771 | 2023-09-22 | Tharamangalam | D | B nozzle leakage | Breakdown | Prabu | 2023-09-22 | - | B nozzle serviced and fixed - Tank area unloading air hose replaced - Attended
CL3772 | 2023-09-23 | Thuraiyur | D | Dispenser A side on/off switch defect | Breakdown | Nivas | 2023-09-23 | - | On/off switch replaced at A side - Hammer teeth 4 Nos replaced - Resolved
CL3773 | 2023-09-23 | Kumbakonam | T | Dispensing motor love joy coupling spider defect | Breakdown | Pandi Durai | 2023-09-23 | - | Damaged lovejoy coupling spider replaced in dispensing motor - Working good - Rectified
CL3774 | 2023-09-23 | Attur | C | PMR work | Preventive | Nivas | 2023-09-23 | - | PMR done - Completed
CL3775 | 2023-09-24 | Avinashi | D | Batchen dispenser metering unit problem and dispensing motor abnormal noise | Breakdown | Gowtham | 2023-09-25 | - | Dispensing above ground motor base realignment done - Noise and vibration arrested - Batchen dispenser B side metering unit serviced and made DP valve blind condition - Total testing ltr -756.61 Ltrs - Rectified | If problem occurred in Metering unit, it needs to be changed
CL3776 | 2023-09-24 | Perundurai | D | A side keypad wiring damaged | Breakdown | Avinash | 2023-09-24 | - | A side keypad changed - Working fine - Resolved | One Billing mobile hanging. Safety checklist not maintained. First Aid box all medicine expired and unloading instruction Board faded,Informed incharge to refill medicine
CL3777 | 2023-09-25 | Cantonment | D | A nozzle 5m dispensing hose and 0.5m dispensing hose defect | Breakdown | Nepolean | 2023-09-25 | - | 5m dispensing hose and 0.5m dispensing hose replaced - No leakage found - Testing : 1.08 Ltrs - Attended
CL3778 | 2023-09-26 | Vellakovil | T | Unloading motor bed base concret work | Preventive | Thirumalaisamy | 2023-09-26 | - | Unloading motor fixed - Concrete work done - PMR done - Safety training provided - Completed
CL3779 | 2023-09-26 | Thuraiyur | T | Unloading motor fly wheel cotter pin damaged | Breakdown | Nivas | 2023-09-26 | - | Cotter pin replaced - Unloading motor working fine - Completed
CL3780 | 2023-09-26 | Perambalur | R | Control panel isolator rotary switch defect | Breakdown | Pandi Durai | 2023-09-26 | - | New isolator rotary switch replaced - Unloading earth cable extended - Control panal transformer fuse holder replaced - Attended
CL3781 | 2023-09-26 | T.V.Kovil | D | A nozzle teeth worn out | Breakdown | Nepolean | 2023-09-26 | - | Nozzle teeth 4 nos replaced - Working fine - Resolved
CL3782 | 2023-09-26 | Uthamasolapuram | T | Control panel unloading solenoid coil not working | Breakdown | Prabu | 2023-09-26 | - | Control panel unloading solenoid coil replaced and control panel RYB indicator light replaced - Working fine - Rectified
CL3783 | 2023-09-27 | Virudhunagar | D | A nozzle 5m dispensing hose leakage | Breakdown | Kathiresan | 2023-09-27 | - | Dispensing hose 5m and 0.5m replaced - No leakages - Working fine - Testing : 0.84 L - Completed
CL3784 | 2023-09-28 | Thiruvaiyaru | T | Dispensing line pneumatic hose T joint defect | Breakdown | Pandi Durai | 2023-09-28 | - | Dispensing line pneumatic hose T joint changed - Decanting line fill point liquid ROV is not working properly - Sent to HO - Batchen A side keypad cable reconnected - Working fine - Resolved | Decanting line fill point liquid ROV is not working properly - Sent to HO
CL3785 | 2023-09-28 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2023-09-28 | - | Old nozzle serviced and tested - Oil changed for both compressors - Testing : 2.31 L - Completed
CL3786 | 2023-09-29 | Villapuram | D | Dispensing motor run time program error | Breakdown | Kathiresan | 2023-09-29 | - | Dispensing motor run time program changed - Working fine - Rectified
CL3787 | 2023-09-29 | Tiruchengode | G | Fire extinguisher service and renewal | Preventive | Avinash | 2023-09-29 | - | Fire extinguisher renewal and service done - Fire safety training provided to pump staffs - Completed
CL3788 | 2023-09-29 | Namakkal 3 | G | Fire extinguisher hose damaged | Breakdown | Nivas | 2023-09-29 | - | 75 Kg fire extinguisher hose replaced - 9 kg sent for servicing - Fire safety training provided to pump staffs - Completed
CL3789 | 2023-09-29 | Namakkal 1 | G | Fire extinguisher service and renewal | Preventive | Nivas | 2023-09-29 | - | 9 kg ABC fire extinguisher replaced - Fire safety training provided to pump staffs - Completed
CL3790 | 2023-09-30 | T.V.Kovil | D | B nozzle leakage | Breakdown | Pandi Durai | 2023-09-30 | - | Spare nozzle replaced - A nozzle front O ring replaced - Air machine clip connector changed - B side Testing : 1.19 L - Rectified
CL3791 | 2023-09-30 | Salem | D | 5m dispensing hose damaged | Breakdown | Prabu | 2023-09-30 | - | Dispensing hose 5m replaced - Testing : 1.03 L - Resolved | SRV not changed. SRV opening and closing pressure Rule18 certificate after change. Tank SRV1 only working condition.SRV2 battom side Ball valve closed.
CL3792 | 2023-09-30 | Madurai 3 - Sivagangai Road | G | Earth installation | New Project | Kathiresan | 2023-09-30 | - | Earth installation done - Cable laying done - Earth flat welding done - Completed
CL3793 | 2023-10-01 | Cantonment | D | Metering unit stuck up at B side | Breakdown | Chandrasekar | 2023-10-01 | - | Metering unit bearing and oil seal kit replaced - Working fine - B side testing : B.Testing Day shift.2.18 litre Night shift.37.82 litre A.Testing Night shift.4.00 litre - Completed
CL3794 | 2023-10-01 | Paramathivelur | D | A side dispensing hose breakaway coupling disconnected because of human error | Breakdown | Thirumalaisamy | 2023-10-01 | - | Breakaway coupling refitted - No leakage found - Safety training provided to pump staffs - Resolved
CL3795 | 2023-10-01 | Cantonment | D | B side metering unit service and calibration | Breakdown | Nepolean | 2023-10-01 | - | B side metering unit service and calibration done - Day shift Testing at B side : 148.57 L - Rectified
CL3796 | 2023-10-02 | Salem 2 | G | Site visit | New Project | Prakash | 2023-10-02 | - | Site visit done - Completed
CL3797 | 2023-10-02 | Kodungaiyur | R | Stabilizer is not working due to R phase variac defect | Breakdown | Suneel Sagar | 2023-10-03 | - | Circuit capacitor replaced by Mothish service person - Stabilizer working fine - Resolved
CL3798 | 2023-10-02 | Aravakurichi | T | Unloading training | Preventive | Thirumalaisamy | 2023-10-02 | - | Unloading and safety training provided to pump staffs - Attended
CL3799 | 2023-10-02 | Ellis Nagar | D | D nozzle leakage | Breakdown | Kathiresan | 2023-10-02 | - | Nozzle teeth replaced - Leakage arrested - Working fine - Attended
CL3800 | 2023-10-02 | Velachery | T | Dispensing motor rewinding | Breakdown | Suneel Sagar | 2023-10-02 | - | Dispensing motor rewinding completed and tested without load - Found satisfactory - Completed
CL3801 | 2023-10-02 | Uthamasolapuram | R | Compressor running continuously due to dispensing air hose leakage | Breakdown | Prabu | 2023-10-02 | - | Dispensing air hose replaced - Compressor working good - Resolved
CL3802 | 2023-10-03 | Kangeyam | G | PMR work | Preventive | Gowtham | 2023-10-03 | - | B nozzle serviced and fixed - Tesing : 3.56 L - PMR done - Rectified | Dispensing hose assembly to be changed
CL3803 | 2023-10-03 | T.V.Kovil | D | B nozzle LPG leakage | Breakdown | Nepolean | 2023-10-03 | - | B side serviced nozzle replaced - Working fine - Testing : 1.17 L - Attended
CL3804 | 2023-10-04 | Cantonment | D | B side metering unit stuck up | Breakdown | Chandrasekar | 2023-10-04 | - | Metering unit piston replaced - Testing Day shift.4.15 litre Night shift.17.61 litre - and Kept under observation - Testing : 113.92 L at Day shift Completed
CL3805 | 2023-10-04 | Vellakovil | G | Outlet visit | Preventive | Thirumalaisamy | 2023-10-04 | - | Pipe line painting work partially done - Attended
CL3806 | 2023-10-04 | Chinnasalem | T | Unloading motor not working | Breakdown | Pandi Durai | 2023-10-04 | - | DOL starter OLR relay changed from manual to automatic mode - Working fine - Rectified
CL3807 | 2023-10-04 | Cantonment | G | Oil dispenser nozzle defect | Breakdown | Chandrasekar | 2023-10-04 | - | Oil dispenser nozzle replaced with new - Resolved
CL3808 | 2023-10-05 | Namakkal 3 | D | A side keypad is not working | Breakdown | Nivas | 2023-10-05 | - | New keypad replaced - Working fine - Resolved
CL3809 | 2023-10-05 | Namakkal 2 | A | TP link router power adapter defect | Breakdown | Nivas | 2023-10-05 | - | TP link router power adapter replaced - Working fine - Rectified
CL3810 | 2023-10-06 | Thanjavur | C | DL stamping work | Certification | Nepolean and Vignesh | 2023-10-06 | - | DL Stamping done - Completed
CL3811 | 2023-10-06 | Namakkal 1 | A | Automation system CPU heating issue | Breakdown | Nivas | 2023-10-06 | - | Spare CPU replaced - Working fine - Attended | Defected CPU sent to HO for service
CL3812 | 2023-10-06 | Villapuram | D | C side metering unit noise and slow delivery | Breakdown | Kathiresan | 2023-10-06 | - | Metering unit middle magnetic piston rod cleaned and serviced - Working properly - Testing : 167.09 L - Completed
CL3813 | 2023-10-07 | Thuraiyur | T | Unloading motor abnormal noise | Breakdown | Nivas and Nepolean | 2023-10-12 | - | Pump serviced at both sides - Shaft O ring two nos replaced - No leakage found - Unloading pump working fine - Unloading done - Kept under observation untill next unloading - Rectified
CL3814 | 2023-10-09 | Melur | C | Rule 18 work | Certification | Chandrasekar and Kathiresan | 2023-10-09 | - | Rule 18 done - Total leakage tested - Earth value tested - All equipments working fine - Completed
CL3815 | 2023-10-09 | Madhavaram | T | Site marking | New Project | Suneel Sagar | 2023-10-09 | - | Tank pit and office room marking done - Completed
CL3816 | 2023-10-09 | Villapuram | C | Rule 18 work | Certification | Kathiresan | 2023-10-09 | - | Rule 18 done - Total leakage tested - Earth value tested - All equipments working fine - Completed
CL3817 | 2023-10-09 | Ellis Nagar | C | Rule 18 work | Certification | Kathiresan | 2023-10-09 | - | Rule 18 done - Total leakage tested - Earth value tested - All equipments working fine - Completed
CL3818 | 2023-10-10 | Viruthachalam | T | Dispensing motor lov joy coupling cotter pin disconnected | Breakdown | Pandi Durai | 2023-10-10 | - | Dispensing motor lov joy coupling cotter pin reconnected Dispensing and decanting spare pneumatic hose 2 Nos replaced - Working fine - Rectified
CL3819 | 2023-10-10 | Pudukottai | G | Fire extinguisher service | Preventive | Nepolean | 2023-10-10 | - | Fire extinguisher service done - Attended
CL3820 | 2023-10-10 | Ariyamangalam | D | C nozzle teeth worn out | Breakdown | Nepolean | 2023-10-10 | - | C nozzle teeth 4 Nos changed - Air hose replaced for dispenser main line and spare line - Dispenser side ROV cleaned, serviced and refitted - Working fine - Resolved
CL3821 | 2023-10-10 | Erode | R | Control panel booting problem | Breakdown | Prabu | 2023-10-10 | - | UPS connection and Panel board input wirings reconnected - Control panel working fine - Rectified
CL3822 | 2023-10-11 | Erode | G | Fire extinguisher service | Preventive | Avinash | 2023-10-11 | - | Fire extinguisher service, renewal and safety training done - CO2 hose replaced - Attended
CL3823 | 2023-10-11 | Nasiyanur | G | Fire extinguisher service | Preventive | Avinash | 2023-10-11 | - | Fire extinguisher service, renewal and safety training done - Attended
CL3824 | 2023-10-11 | Eral | C | Rule 18, Calibration and stamping work | Certification | Kathiresan | 2023-10-11 | - | Calibration and stamping done - Rule 18 work done - Calibration Report : " A" side 10 ltr = 9.95 " B" side 10 ltr = 9.96 K factor Report : "A" side = 10050 "B" side = 10050 Testing litrs = 322.52 ltrs - Completed
CL3825 | 2023-10-11 | Tirunelveli | C | Rule 18 work | Certification | Kathiresan | 2023-10-11 | - | Rule 18 done - Electrical earth copper pipe newly replaced - D side dispensing hose replaced - Total leakage test done - Resolved | 10 KG fire extinguisher failure - EB power voltage drop problem - Informed to dealer and EB office
CL3826 | 2023-10-12 | Cantonment | D | A and B nozzle teeth replacement | Preventive | Nepolean | 2023-10-12 | - | Nozzle teeth replaced at both nozzles for testing purpose - Completed
CL3827 | 2023-10-12 | Ariyamangalam | D | A nozzle teeth replacement | Preventive | Nepolean | 2023-10-12 | - | Nozzle teeth replaced at both nozzles for testing purpose - Completed
CL3828 | 2023-10-12 | Tenkasi | C | Rule 18 work | Certification | Kathiresan | 2023-10-12 | - | Rule 18 done - All equipment tested - Earth regenerated - Completed
CL3829 | 2023-10-12 | Virudhunagar | C | Rule 18 work | Certification | Kathiresan and Chandrasekar | 2023-10-12 | - | Rule 18 done - Earth copper rod installed newly - All equipments tested - anker truck earth clips changed - Completed
CL3830 | 2023-10-13 | Dharapuram | R | Control panel not working properly | Breakdown | Gowtham | 2023-10-13 | - | Dispensing bypass valve serviced and thread leakage arrested by sealant - Fill point Emergency Stop Switch cable replaced - Control panel working in bypass power supply from Servo stabilizer - Online UPS not working - Resolved temporarily | Online UPS sent for service
CL3831 | 2023-10-13 | T.V.Kovil | D | C nozzle teeth replacement and N2 machine E2 error occurred | Preventive | Nepolean | 2023-10-13 | - | Nozzle teeth replaced at both nozzles for testing purpose - N2 machine coils and sensor cleaned - Error cleared - Completed
CL3832 | 2023-10-13 | Avadi | D | Dispenser ROV pnuematic connectors defect | Breakdown | Suneel Sagar | 2023-10-13 | - | Dispenser ROV pnuematic connectors replaced - Working fine - Rectified
CL3833 | 2023-10-13 | Bodi | C | Rule 18 work | Certification | Kamaraj | 2023-10-13 | - | Rule 18 done - Dispensing motor spider replaced - Total leakage tested - Earth regenerated - Completed
CL3834 | 2023-10-13 | Uthamapalayam | C | Rule 18 work | Certification | Kamaraj | 2023-10-13 | - | Rule 18 done - Unloading vapour line adapter serviced and fitted - Total leakage tested - Completed
CL3835 | 2023-10-14 | Avinashi | G | Dispenser hose damaged and servo stabilizer power supply data collection | Breakdown | Gowtham | 2023-10-14 | - | Dispenser A side dispensing hose recrimped at nozzle end to seal the damage - Attended | Stabilizer to be replaced with new
CL3836 | 2023-10-14 | Theni | C | Rule 18 work | Certification | Kamaraj | 2023-10-14 | - | Rule 18 done - Total leakage tested - Earth regenerated - Completed | Outlet unloading vapour and liquid line hose demaged - Needs to be replaced
CL3837 | 2023-10-14 | Bathlagundu | C | Rule 18 work | Certification | Kamaraj | 2023-10-14 | - | Rule 18 done - Total leakage tested - Earth regenerated - Completed
CL3838 | 2023-10-15 | Perundurai | T | Tank area dispensing air hose damaged | Breakdown | Avinash | 2023-10-15 | - | Spare hose replaced - Co2 fire extinguisher damaged hose replaced with new - Resolved
CL3839 | 2023-10-15 | Thuraiyur | T | Unloading work | Breakdown | Nivas | 2023-10-15 | - | Unloading done - No leakage found - Working fine - Completed
CL3840 | 2023-10-16 | Namakkal 2 | D | Dispenser bottem liquid line ROV with ball valve LPG leakage | Breakdown | Nivas | 2023-10-16 | - | Dispenser bottem liquid line ROV with ball valve LPG leakage arrested by tightening the stem - Working fine - Rectified
CL3841 | 2023-10-16 | Pudukottai | C | DL stamping work | Certification | Nepolean and Suresh Kumar | 2023-10-16 | - | DL stamping done - Testing A side : 166.86 L B side : 153.84 L Total : 320.70 L - Completed
CL3842 | 2023-10-16 | Mettupalayam | G | PMR work | Preventive | Gowtham | 2023-10-16 | - | PMR work done - Rule 19 material list collected - Attended
CL3843 | 2023-10-17 | Sulur | R | Turbo drive power off due to sudden surge in input | Breakdown | Gowtham | 2023-10-17 | - | Power fluctuation adjusted - Resolved
CL3844 | 2023-10-17 | Uthamasolapuram | C | Calibration and stamping work | Certification | Chandrasekar and Prabu | 2023-10-17 | - | Calibration and stamping work done - No changes in K factor - A side K Factor - 10010 B side K Factor - 10010 A side Testing : 124.37 L B side Testing : 130.37 L - Completed
CL3845 | 2023-10-17 | Krishnagiri | D | A nozzle slow delivery | Breakdown | Chandrasekar and Prabu | 2023-10-18 | - | Excess flow valve directed due to center shaft defect - Automation rewiring done - Rectified | 3/4" excess flow valve to be replaced
CL3846 | 2023-10-17 | T.V.Kovil | T | Unloading vapour hose defect | Breakdown | Nepolean | 2023-10-17 | - | Vapour hose replaced with new - No leakage found - Rectified
CL3847 | 2023-10-18 | Virudhunagar | A | Automation network issue due to CAT 6 cable defect | Breakdown | Kathiresan | 2023-10-18 | - | Firewall CAT6 cable replaced for 10 meters - Resolved
CL3848 | 2023-10-18 | Thuraiyur | R | Servo stabilizer service work | Breakdown | Nepolean | 2023-10-18 | - | Contactor replaced with 3 Nos - Capacitor replaced with new one - Servo stabilizer working normally - Attended
CL3849 | 2023-10-19 | Dharapuram | A | Online UPS service | Breakdown | Gowtham | 2023-10-19 | - | Online UPS serviced and new battery 3 nos replaced by service technician - Completed
CL3850 | 2023-10-19 | Kodungaiyur | G | Sales stopped due to EB power failure and Genset battery down due to internal wire damage by rat bite | Breakdown | Suneel Sagar | 2023-10-20 | 6.40 pm to 7.20 pm | Genset issue resolved by Kirloskar technician - Attended
CL3851 | 2023-10-20 | Ellis Nagar | D | C nozzle leakage due to nozzle teeth defect | Breakdown | Kathiresan | 2023-10-20 | - | Nozzle teeth 4 nos replaced - Leakage arrested - Working fine - Resolved
CL3852 | 2023-10-20 | Velachery | T | Dispensing motor contactor add on block defect | Breakdown | Suneel Sagar | 2023-10-20 | - | Dispensing motor contactor add on block replaced - Working good - Rectified
CL3853 | 2023-10-21 | Krishnagiri | D | Excess flow valve replacement | Breakdown | Prabu | 2023-10-21 | - | Dispenser nozzle 0.5m hose, excess flow valve and pressure gauge replaced - Found satisfactory - Attended
CL3854 | 2023-10-21 | Musiri | D | Nozzle leakage | Breakdown | Nivas | 2023-10-21 | - | A and B nozzle cleaned and serviced - Working fine - Testing A side : 0.86 L; B side : 0.91 L - Resolved
CL3855 | 2023-10-21 | Manapparai | A | Automation hard disk defect | Breakdown | Pandi Durai | 2023-10-21 | - | Spare hard disk adapter changed - Working fine - Resolved | Defected hard disk sent to HO for service
CL3856 | 2023-10-21 | Hosur | A | Dispenser UPS battery back up issue | Breakdown | Prabu | 2023-10-21 | - | New UPS battery changed - Completed
CL3857 | 2023-10-21 | Tiruchengode | A | CPU hanging issue | Breakdown | Avinash | 2023-10-21 | - | Sytem rewiring done and rebooted - Outlet running online - Unloading training provided to pump staffs - Rectified
CL3858 | 2023-10-22 | Aravakurichi | D | Dispenser low flow | Breakdown | Thirumalaisamy | 2023-10-22 | - | Dispensing motor filter cleaned - LPG flow adjusted - Working fine - Attended
CL3859 | 2023-10-24 | Karur | D | Dispenser to EB room pneumatic hose air leakage | Breakdown | Thirumalaisamy | 2023-10-24 | - | Air hose replaced to arrest leakage - Completed
CL3860 | 2023-10-25 | Kangeyam | D | Kalvacha dispenser A side metering unit problem | Breakdown | Gowtham | 2023-10-25 | From 25-10-2023 - 12 pm - A nozzle only | A nozzle sales stopped - B side breakaway coupling and dispensing hose assembly replaced - Y and B phase indicator replaced in panel board - Compressor oil changed - Rectified
CL3861 | 2023-10-25 | Dindigul | T | Unloading vapour hose ACME adapter leakage | Breakdown | Thirumalaisamy | 2023-10-25 | - | ACME adapter LPG leakage arrested by tightening with teflon - No leakage found - Resolved
CL3862 | 2023-10-25 | T.V.Kovil | G | Oil dispenser hose damaged | Breakdown | Nepolean | 2023-10-25 | - | Oil dispenser hose replaced - Oil testing : 0.5 L - Attended
CL3863 | 2023-10-26 | Manapparai | C | Rule 18 work | Certification | Nepolean and Pandi Durai | 2023-10-26 | - | Rule 18 work done - Dispenser 5m hose replaced at A and B side - Unloading earth cable extended to 5m - A side nozzle teeth 4 Nos replaced - Dispensing line vapour ROV leakage arrested by tightening the stem - Manapparai station testing: A side: 1.76 L B side: 0.89 L - Attended
CL3864 | 2023-10-26 | Salem 2 | G | Site visit | New Project | Prakash, Venkatesh and Prasath | 2023-10-26 | - | Site visit done - Completed
CL3865 | 2023-10-26 | Cantonment | R | Compressor oil replacing | Preventive | Chandrasekar | 2023-10-26 | - | Compressor oil replaced - Attended
CL3866 | 2023-10-26 | Ellis Nagar | R | Servo stabilizer R phase winding melted and spark produced | Breakdown | Kathiresan | 2023-11-02 | - | Servo stabilizer directed - Resolved temporarily - Stabilizer R phase winding serviced and replaced - Working fine - Voltage "R" = 238 (v) "Y" = 239 (v) "B" = 239 (v) - Stabilizer working in servo mode - Completed | Stabilizer serviced by Mothish
CL3867 | 2023-10-26 | Ariyamangalam | G | Outlet running in Genset mode due to EB supply is in single phase | Breakdown | Nepolean | 2023-10-26 | - | EB person serviced the transformer jumper - Outlet running in EB mode - Rectified
CL3868 | 2023-10-27 | Thuraiyur | T | Dispensing pump motor flywheel pully dislocated | Breakdown | Nivas | 2023-10-27 | - | Cotter pin thickness increased to locate the flywheel - A bolt provided to hold the shaft - Pump working fine - Resolved
CL3869 | 2023-10-27 | Avinashi | R | Compressor running continuously | Breakdown | Gowtham | 2023-10-27 | - | Batchen dispenser air hose replaced - and spare hose provided - Compressor working fine - Completed
CL3870 | 2023-10-27 | Pudukottai | C | Rule 18 work | Certification | Nepolean and Pandi Durai | 2023-10-27 | - | Rule 18 work done - Earth regenerated - Unloading earth cable extended to 5m - A side nozzle teeth 4 Nos replaced - Dispensing line vapour ROV leakage arrested by tightening the stem - Manapparai station testing: A side: 1.76 L B side: 0.89 L - Attended | Tank area pipe line and flanges corroded - Painting has to be done
CL3871 | 2023-10-27 | Kodungaiyur | C | Stamping work | Certification | Suneel Sagar | 2023-10-27 | - | Stamping done - Completed
CL3872 | 2023-10-29 | Palayam | R | Compressor running continuously | Breakdown | Thirumalaisamy | 2023-10-29 | - | EB room to dispenser and EB room to tank area pneumatic line replaced - A nozzle hose rope replaced - PMR done - Automation equipment maintenance done - Resolved
CL3873 | 2023-10-29 | Palladam | D | Dispensing hose breakaway removed from dispenser due to the moving of vehicle | Breakdown | Gowtham | 2023-10-29 | - | Dispensing hose breakaway connected - Operational Instructions and short brief about safety measures provided to staff - Testing : 0.76 L - Attended
CL3874 | 2023-10-30 | Rasipuram | D | A nozzle leakage | Breakdown | Nivas | 2023-10-30 | - | Nozzle cleaned and serviced - Testing : 0.85 L - Leakage arrested - Working fine - Rectified
CL3875 | 2023-10-30 | Cantonment | G | Fire extinguisher service | Preventive | Chandrasekar | 2023-10-30 | - | 75 Kg fire extinguisher powder refilled - New hose replaced - Co2 extinguisher replaced dut to pressure drop - PRV replaced with new one - All fire extinguisher painting done - Safety training provided to pump staffs - Resolved
CL3876 | 2023-10-30 | Palladam 1 | G | Safety and unloading training | Preventive | Gowtham | 2023-10-30 | - | Safety and unloading training provided to pump staffs - Attended
CL3877 | 2023-10-30 | Palladam 2 | G | Safety and unloading training | Preventive | Gowtham | 2023-10-30 | - | Safety and unloading training provided to pump staffs - Attended
CL3878 | 2023-10-30 | Villapuram | R | Dispensing solenoid valve not working properly | Breakdown | Kathiresan | 2023-10-30 | - | New solenoid valve replaced - Working fine - Completed
CL3879 | 2023-10-31 | Thiruvaiyaru | C | Rule 18 work | Certification | Nepolean and Pandi Durai | 2023-10-31 | - | Rule 18 work done - Attended
CL3880 | 2023-10-31 | Cantonment | G | New FRL and keypad replacement for testing purpose | Preventive | Chandrasekar | 2023-10-31 | - | New FRL replaced and C nozzle keypad replaced for testing purpose - Completed
CL3881 | 2023-10-31 | T.V.Kovil | G | Keypad replacement for testing purpose | Preventive | Chandrasekar | 2023-10-31 | - | C nozzle keypad replaced for testing purpose - Completed
CL3882 | 2023-10-31 | Kumbakonam | C | Rule 18 work | Certification | Nepolean and Pandi Durai | 2023-10-31 | - | Rule 18 work done - Attended
CL3883 | 2023-10-31 | Thanjavur | C | Rule 18 work | Certification | Nepolean and Pandi Durai | 2023-10-31 | - | Rule 18 work done - Attended
CL3884 | 2023-11-01 | Palayam | G | Internet issue | Breakdown | Thirumalaisamy | 2023-11-01 | - | Fiber net issue resolved by rewiring - Online UPS battery 3 Nos replaced due to backup issue - Rectified
CL3885 | 2023-11-01 | Avadi | R | Pneumatic line air leakage and stabilizer output high voltage issue | Breakdown | Suneel Sagar | 2023-11-01 | - | Pneumatic connecter replaced and stabilizer cleaned and serviced- Working fine - Resolved
CL3886 | 2023-11-01 | Villapuram | D | B nozzle leakage | Breakdown | Kathiresan | 2023-11-01 | - | B nozzle teeth replaced - Working fine - "B" Side Reading= 1161322.14- Completed | A and B side 5m dispensing hose to be replaced
CL3887 | 2023-11-01 | Ellis Nagar | D | A and B nozzle teeth replacement | Preventive | Kathiresan | 2023-11-01 | - | Nozzle teeth replaced at both side to avoid leakage as it is been on for more than 2 Lakh Litres - "A" Side = 661020.71 "B" Side = 722409.61.- Attended
CL3888 | 2023-11-02 | Karur | R | Unloading air solenoid air leakage | Breakdown | Thirumalaisamy | 2023-11-02 | - | New air solenoid valve replaced - Leakage arrested - B nozzle lock replaced - Rectified
CL3889 | 2023-11-03 | Ammapet | G | Generator MOL error | Breakdown | Avinash | 2023-11-03 | - | PLC A2 and A4 loop removed - Kept under observation - Resovled
CL3890 | 2023-11-03 | Vadivelan Nagar | D | B side keypad defect | Breakdown | Suneel Sagar | 2023-11-03 | - | New keypad replaced - Working fine - Resolved
CL3891 | 2023-11-03 | Ellis Nagar | D | C side keypad defect | Breakdown | Kathiresan | 2023-11-03 | - | New keypad replaced - Working fine - Resolved
CL3892 | 2023-11-04 | Ariyalur | C | Rule 18 work | Certification | Chandrasekar and Pandi Durai | 2023-11-04 | - | Rule 18 work done - A side keypad replaced - All equipments working fine - Total leakage checked - Earth value checked - Completed | B side keypad to be replaced
CL3893 | 2023-11-04 | Perambalur | C | Rule 18 work | Certification | Chandrasekar and Pandi Durai | 2023-11-04 | - | Rule 18 work done - PMR done - All equipments working fine - Total leakage checked - Earth value checked - Completed
CL3894 | 2023-11-04 | Villapuram | D | A and B nozzle dispensing hose replacement | Breakdown | Kathiresan | 2023-11-04 | - | New 5m dispensing hose replaced at both nozzles - Damaged hose crimped and kept as a spare - C side spare nozzle replaced - Readings : "A" Side = 1044096.54 "B" Side = 1165280.17 "C" Side = 566163.43 Testing Litres : "A" Side = 0.86 "B" Side = 0.90 "C" Side = 0.86 - Completed
CL3895 | 2023-11-04 | Viruthachalam | C | Rule 18 work | Certification | Chandrasekar and Pandi Durai | 2023-11-04 | - | Rule 18 work done - PMR done - All equipments working fine - Total leakage checked - Earth value checked - Completed
CL3896 | 2023-11-05 | Bhavani | G | Earth issue in dispenser due to canopy wire short circuit | Breakdown | Avinash | 2023-11-05 | - | Light power supply disconnected and temporary earth connection given to canopy - Resolved | B side 5m dispensing hose to be replaced
CL3897 | 2023-11-05 | Attur | C | Rule 18 work | Certification | Nivas, Chandrasekar and Pandi Durai | 2023-11-06 | - | Rule 18 work done - Unloading earth cable extended to 5 Mtrs - Earth value tested - All leakage tested - Dispenser bottom ROV air leakage arrested - Batchan dispenser both side 5 mtr and 0.5 mtr hose changed - Chemical earth rod installed - Working fine - Testing : A - 5 L and B - 5 L - Attended
CL3898 | 2023-11-05 | Ellis Nagar | D | B side DP valve diaphragm puncture | Breakdown | Kathiresan | 2023-11-05 | 4 Hours | New diaphragm replaced at B side - Working good - Testing : 15 Ltrs - Resolved
CL3899 | 2023-11-05 | Nasiyanur | G | Unloading training | Preventive | Avinash | 2023-11-05 | - | Unloading done and unloading training provided to pump staffs - Completed
CL3900 | 2023-11-05 | Chinnasalem | C | Rule 18 work | Certification | Chandrasekar and Pandi Durai | 2023-11-05 | - | Rule 18 work done - Both compressor oil changed - Unloading earth cable extended to 5 Mtrs - Dispenser bottom ROV air leakage arrested - Attended
CL3901 | 2023-11-06 | Sankari | C | Rule 18 work | Certification | Avinash | 2023-11-06 | - | Rule 18 work done - PMR done - Unloading earth cable extended to 5 Mtrs - Earth value tested - All leakage tested - Dispenser bottom ROV air leakage arrested - Batchan dispenser both side 5 mtr and 0.5 mtr hose changed - Chemical earth rod installed - Working fine - Testing : A - 5 L and B - 5 L - Attended
CL3902 | 2023-11-06 | T.V.Kovil | D | Nozzle replacement for testing purpose | Preventive | Nepolean | 2023-11-06 | - | Nozzle teeth 12 nos replaced at A, B and D side - Working fine - Rectified
CL3903 | 2023-11-06 | Velachery | G | Fire extinguisher renewal and training | Preventive | Suneel Sagar | 2023-11-06 | - | Fire extinguishers renewed and fire safety training provided - Attended
CL3904 | 2023-11-06 | Vadivelan Nagar | G | Fire extinguisher renewal and training | Preventive | Suneel Sagar | 2023-11-06 | - | Fire extinguishers renewed and fire safety training provided - Attended
CL3905 | 2023-11-06 | Chengalpattu | G | Fire extinguisher renewal and training | Preventive | Suneel Sagar | 2023-11-06 | - | Fire extinguishers renewed and fire safety training provided - Attended
CL3906 | 2023-11-07 | Ariyalur | T | Vapour line ROV leakage | Breakdown | Suresh Kumar | 2023-11-07 | - | Leakage arrested by tightening the nut - Recitified
CL3907 | 2023-11-07 | Tiruchengode | C | Rule 18 work | Certification | Avinash | 2023-11-07 | - | Rule 18 work done - PMR done - Earth regenerated - Earth value and leakage test done - SS bolts and nuts are replaced in all earth pits - Completed
CL3908 | 2023-11-07 | Namakkal 1 | C | Rule 18 work | Certification | Nivas | 2023-11-07 | - | Rule 18 work done - Earth regenerated - Earth value and leakage test done - CP junction box SS bolt new changed - Unloading earth cable new SS bolt and leg changed - Dispenser vapour line ROV LPG leak arrested - Dispenser Bottem side ROV LPG leak arrested - Dispenser A side Nozzle hose 5 mtr changed - Dispenser A side DP valve diaphragm spring tension adjusted - Tank area inside need the cleaning - A side Testing 0.88 L - A side 10 lit = 10.01 B side 10 lit = 10.00 K factor reports: A side k factor = 10150 B side k factor = 10150 K factor no change Testing liters: A side = 122.55 B side = 125.34 Total = 247.89 - Completed
CL3909 | 2023-11-08 | Ammapet | A | RS 485 to to USB converter board damaged due to thunderstorm | Breakdown | Avinash | 2023-11-08 | - | RS 485 to to USB converter board replaced - Working online - Resolved
CL3910 | 2023-11-08 | Avadi | A | Outlet going offline due to power cable problem | Breakdown | Suneel Sagar | 2023-11-08 | - | Cable loose contact reconnected - Dispenser back online - Rectified | Dispenser offline from 6.20 am to 10.30 pm
CL3911 | 2023-11-08 | Rasipuram | C | Stamping and calibration work | Certification | Nivas | 2023-11-08 | - | Stamping and calibration done - A side 10 lit = 10.02 B side 10 lit = 09.99 K factor reports: A side k factor = 10150 No change B side old k factor = 10100 B side New k factor=10000 Testing liters: A side = 123.34 B side = 332.28 Total = 455.62 - Completed
CL3912 | 2023-11-08 | Tharamangalam | R | Control panel unloading solenoid coil not working | Breakdown | Prabu | 2023-11-08 | - | Solenoid coil replaced - Both nozzle serviced to arrest leakage - Working fine - Resolved
CL3913 | 2023-11-08 | Ammapet | G | Fire incident | Breakdown | Avinash | 2023-11-08 | - | a fire accident has been occurred at 3.10 PM today . A vehicle came to station for fueling ,after fueling while starting the fire has been occurred due to leak of LPG from Vehicle Tank inlet value spread fully in vehicle . Then incident is seen by Mr vengadesh (Pump staff) and shouted then suddenly Office Room emergency has been operated by Mr Palani(pump staff) and by using one 9Kg fire extinguisher they controled the fire and moved away the vehicle from dispenser, after situation normal sales has been started, Training given to staffs and informed to stand near Dispenser till vehicle move away form dispenser. | There is No IP camera at the station, already informed dealer to install but not yet installed
CL3914 | 2023-11-08 | Ellis Nagar | G | Diesel generator oil service | Preventive | Kathiresan | 2023-11-08 | - | Generator oil service and maintenance done - Engine oil, Diesel filter and oil filter replaced - Working fine - Rectified | Total engine running hours - 30.1 KWH
CL3915 | 2023-11-08 | Mulanur | R | Online UPS error 56 due to input supply problem | Breakdown | Thirumalaisamy | 2023-11-09 | - | Automation input supply connected with offline UPS - Resolved temporarily | Online UPS sent for service to Mothish
CL3916 | 2023-11-08 | Namakkal 3 | C | Rule 18 work | Certification | Nivas | 2023-11-08 | - | Rule 18 work done - Earth regenerated - Earth value tested - All area leakage checked - Unloading earth cable length extended - Atteded
CL3917 | 2023-11-09 | Perambalur | T | ATG not working | Breakdown | Pandi Durai | 2023-11-09 | - | ATG and system looped connection seperated - ATG working fine - B side keypad replaced - Completed
CL3918 | 2023-11-09 | Avadi | R | Stabilizer output high voltage error occurred | Breakdown | Suneel Sagar | 2023-11-09 | - | B phase variac alignment checked by Mothish Service Engineer - Attended | Recommended to replace the variac
CL3919 | 2023-11-09 | Omalur | G | Dispensing, decanting motors, Control panel and ATG commissioning | New Project | Prabu | 2023-11-09 | - | All equipments commissioned - Automation installed and dispensers are online - Completed
CL3920 | 2023-11-10 | Avinashi | R | New servo stablizer installation | Breakdown | Gowtham | 2023-11-10 | - | New stabilizer installed - High low voltages under observation - Found satisfactory on its operation - Resolved
CL3921 | 2023-11-10 | Viruthachalam | R | Dispenser compressor running continuously | Breakdown | Pandi Durai | 2023-11-10 | - | Dispensing liquid line ROV leakage which is interchanged with decanting liquid line ROV - working fine - No air leakage found - Rectified
CL3922 | 2023-11-10 | Namakkal 2 | C | Rule 18 work | Certification | Nivas | 2023-11-10 | - | Rule 18 work done - Earth regenerated - Earth value tested - All area leakage checked - SS bolts and nuts changed in all earth pits - Atteded
CL3923 | 2023-11-10 | Cantonment | D | B nozzle teeth worn out and E nozzle dispensing hose damaged | Breakdown | Nepolean | 2023-11-10 | - | Nozzle teeth 4 Nos replaced - E nozzle 5m dispensing hose replaced - No leakage found - Testing at E side - 0.83 L - Completed
CL3924 | 2023-11-11 | Vadivelan Nagar | T | Tank 1 liquid line ROV not working | Breakdown | Suneel Sagar | 2023-11-11 | - | Tank 1 liquid line ROV replaced by new - Found satisfactory - Resolved
CL3925 | 2023-11-11 | Cantonment | G | Oil sales stopped due to oil dispenser solenoid coil output voltage issue | Breakdown | Chandrasekar | 2023-11-16 | - | Oil dispenser solenoid coil and motherboard charnged - Oil sales started closing old oil reading:9456.60 opening oil reading:0.00 - Completed
CL3926 | 2023-11-11 | Manapparai | A | Dispenser going offline due to CPU fan issue | Breakdown | Madhavan | 2023-11-12 | - | Spare CPU changed - Dispenser back online - Rectified
CL3927 | 2023-11-13 | Avinashi | D | C nozzle not working properly | Breakdown | Gowtham | 2023-11-13 | - | C nozzle cleaned and serviced - Working good for sales - Testing : 1.73 L - Attended
CL3928 | 2023-11-14 | Perambalur | G | Outlet not running in EB mode | Breakdown | Pandi Durai and Nepolean | 2023-11-14 | - | EB phase adjusted - Outlet running fine - Kept under observation - Attended
CL3929 | 2023-11-14 | Omalur | G | Commissioning work | New Project | Chandrasekar, Lingeshwaran and Prabu | 2023-11-14 | - | Unloading, dispensing pump and motor, ATG, Rochester, Dispenser and all other equipments working fine - Automation working fine - Completed
CL3930 | 2023-11-14 | Dharapuram | D | B side dispensing hose pressure gauge damaged and leakage found | Breakdown | Gowtham | 2023-11-14 | - | Pressure gauge removed and made it as blind - No leakage found - Resolved
CL3931 | 2023-11-15 | Neelambur | G | Unloading and unloading training | Preventive | Gowtham | 2023-11-15 | - | Unloading done - Unloading training provided to pump staffs - Attended
CL3932 | 2023-11-15 | Rasipuram | D | Dispenser B side 5m dispensing hose damaged | Breakdown | Nivas | 2023-11-15 | - | Spare dispensing hose replaced - Compressor oil changed - Online UPS bolt nut replaced and battery water topped up - Testing : 0.86 L - Completed
CL3933 | 2023-11-15 | Omalur | C | Dispenser stamping | New Project | Chandrasekar, Lingeshwaran and Prabu | 2023-11-16 | - | Dispenser stamping done - Outlet opened to public - Dispenser opening reading A side 397.71 B side 472.96 Tank opening - 76% - Completed
CL3934 | 2023-11-15 | Viruthachalam | T | Dispensing motor love joy coupling noise and vibrating | Breakdown | Pandi Durai | 2023-11-15 | - | Shaft key cotter pin replaced with new and grease applied - Noise reduced and working fine - Attended
CL3935 | 2023-11-16 | Tenkasi | R | Control panel VSC contactor short circuited | Breakdown | Kathiresan | 2023-11-16 | - | VSC contactor replaced with W2 contactor - Working fine - Resolved | W2 Contactor to be replaced
CL3936 | 2023-11-16 | Perambalur | T | ATG not showing the tank litres | Breakdown | Pandi Durai | 2023-11-16 | - | ATG configuration done - Rectified
CL3937 | 2023-11-16 | T.V.Kovil | R | Servo stabilizer R phase variac bearing damaged and noise occurred | Breakdown | Nepolean | 2023-11-16 | - | Servo stabilizer replaced - Temporarily rectified | Servo stabilizer R phase variac bearing servicing is in process
CL3938 | 2023-11-16 | Bhavani | C | Stamping and calibration work | Certification | Avinash | 2023-11-17 | - | Stamping and calibration done - Reports : A side testing -156.51 B side testing -153.83 Total testing -310.34 K Factor no changes A- 10050 B- 10050 A side 10 Lts =9.95 B side 10 Lts =9.96 - Completed
CL3939 | 2023-11-16 | Avadi | R | Servo stabilizer B phase variac damaged | Breakdown | Suneel Sagar | 2023-11-16 | - | B phase variac replaced by Mothish Service Engineer - Completed
CL3940 | 2023-11-16 | Kattupakkam | D | A side keypad defect | Breakdown | Suneel Sagar | 2023-11-16 | - | Keypad replaced with new - Working good - Completed
CL3941 | 2023-11-17 | Ariyalur | G | Fire extinguisher service | Preventive | Pandi Durai | 2023-11-17 | - | Fire extinguisher service done - DB panel RYB indicator light replaced - Completed
CL3942 | 2023-11-17 | Dharapuram | G | Site visit | Preventive | Gowtham | 2023-11-17 | - | New dispenser installation material list taken - Attended
CL3943 | 2023-11-17 | Mulanur | R | Stabilizer carbon bush damage | Breakdown | Thirumalaisamy | 2023-11-17 | - | Dispenser running in bypass mode - Attended | Carbon bush, holder brush and clip damaged - To be replaced by Mothish
CL3944 | 2023-11-17 | Avinashi | R | Surge arrester replacement | Breakdown | Gowtham | 2023-11-17 | - | R phase surge arrester replaced - Working fine - Resolved
CL3945 | 2023-11-17 | Viruthachalam | G | Fire extinguisher service | Preventive | Pandi Durai | 2023-11-17 | - | Fire extinguisher service done - 75 KG extinguisher refilling done - 9 KG DCP extinguisher changed in to ABC - Painting work done for all extinguishers - A side keypad replaced - Working fine - Completed
CL3946 | 2023-11-17 | Perambalur | G | Fire extinguisher service | Preventive | Pandi Durai | 2023-11-17 | - | Fire extinguisher service done - Control panel RYB phase indicator lights replaced - Attended
CL3947 | 2023-11-17 | Omalur | D | A nozzle inside leakage | Breakdown | Prabu | 2023-11-17 | - | Spare nozzle replaced - Testing : 0.84 Ltrs - Working fine - Rectified
CL3948 | 2023-11-17 | Ammapet | C | Rule 18, stamping and calibration work | Certification | Avinash | 2023-11-17 | - | Rule 18 work completed - Earth value tested and regenerated - Leak checked and calibration done. Calibration report A side testing -151.47 B side testing -151.52 Total testing -302.99 K Factor no changes A- 10000 B- 10000 A side 10 Lts =10.02 B side 10 Lts =10.00 - Completed
CL3949 | 2023-11-17 | Nasiyanur | C | Rule 18, Calibration and stamping work | Certification | Avinash | 2023-11-17 | - | Calibration done - A side testing -152.86 B side testing -159.29 Total testing -312.15 K Factor no changes A- 10000 B- 10000 A side 10 Lts =9.96 B side 10 Lts =9.96 - PMR done - Earth regenerated - Earth value checked - All area leakage tested - All earth pit SS bolts and nuts are changed - Completed
CL3950 | 2023-11-17 | Perundurai | C | Rule 18, Calibration and stamping work | Certification | Avinash | 2023-11-17 | - | Calibration and stamping done - A side testing -238.35 B side testing -146.77 Total testing -385.12 Old K Factor A- 10300 B- 10250 New K Factor A -10200 B- 10200 A side 10 Lts =10.00 B side 10 Lts =9.97 - Completed
CL3951 | 2023-11-17 | Kodumudi | C | Calibration and stamping work | Certification | Avinash | 2023-11-17 | - | Calibration and stamping done - A side testing -170.52 B side testing -175.11 Total testing -345.63 K Factor No changes A- 10300 B- 1030 - PMR done - Earth regenerated - Earth value checked - All area leakage tested - All earth pit SS bolts and nuts are changed Completed
CL3952 | 2023-11-17 | Erode | C | Rule 18, calibration and stamping work | Certification | Avinash | 2023-11-17 | - | Calibration and stamping done - A side testing -155.11 B side testing -155.09 Total testing -310.20 K Factor No changes A- 10100 B- 10100 A side 10 Lts =9.91 B side 10 Lts =10.00 - PMR done - Earth regenerated - Earth value checked - All area leakage tested - All earth pit SS bolts and nuts are changed - Completed
CL3953 | 2023-11-20 | Theni | R | Unloading hose replacement | Breakdown | Kathiresan | 2023-11-20 | - | Unloading liquid and vapour hose replaced - No leakage found - Unloading vent line ball valve serviced and working fine - Unloading done upto 84% of tank - Completed
CL3954 | 2023-11-20 | Perundurai | A | CPU heating issue | Breakdown | Avinash | 2023-11-20 | - | Additional cooling fan installed - CPU issue resolved - Kept under observation - Rectified
CL3955 | 2023-11-20 | Dharapuram | D | New dispenser and control panel installation | Preventive | Prakash, Vignesh, Balaji, Chandrasekar, Gowtham and Suresh Kumar | 2023-11-22 | 8 Hours | New dispenser and control panel installation done - Sales started at 12 am - Automation, Calibration and DOL starter installation done on 23.11.2023 - Opening Reading A side- 369.74 lts B side - 146.69 lts Testing - 454.04 lts. K factor - A & B side - 10000 A side - 10.06 /10 L. B side - 10.03/10 L - Attended | Kalvacha dispenser handed over to dealer
CL3956 | 2023-11-20 | Tharamangalam | D | B nozzle 5m dispensing hose damaged | Breakdown | Prabu | 2023-11-20 | - | 5m spare dispensing hose replaced - Testing : 0.87 L - Completed
CL3957 | 2023-11-21 | Paramathivelur | D | B nozzle LPG leakage | Breakdown | Thirumalaisamy | 2023-11-21 | - | Nozzle mount O ring replaced - Serviced offline UPS installed - Working good - Rectified
CL3958 | 2023-11-22 | Omalur | T | Unloading and unloading training | Preventive | Prabu | 2023-11-22 | - | Unloading done - Unloading training provided to pump staffs - HLA and ATG working at 85% - Tank area leakage checked - Completed
CL3959 | 2023-11-22 | Cantonment | D | B nozzle leakage | Breakdown | Nepolean | 2023-11-22 | - | B nozzle teeth replaced - Working fine -Resolved
CL3960 | 2023-11-23 | Perambalur | G | Unloading training and panel testing | Breakdown | Prakash and Vigneshwaran | 2023-11-23 | - | Unloading training done - Panel High High and Low Low checked - Completed
CL3961 | 2023-11-23 | Kangeyam | D | A side metering unit defect | Breakdown | Gowtham | 2023-11-23 | - | Complete parts serviced - A and B side On/ Off switch replaced - Totalizer reading reversed and came to zero - Kept under observation - Testing : 97.09 L - Rectified
CL3962 | 2023-11-24 | Tiruchengode | T | Unloading ROV not closing properly due to dust formation in unloading solenoid | Breakdown | Avinash | 2023-11-24 | - | ROV cleaned - Working fine - Air compressor NRV removed and refitted to arrest inlet air leakage - Under observation - Resolved
CL3963 | 2023-11-24 | Hosur | G | New office construction | New Project | Prabu | 2023-11-24 | - | New office construction work pooja done and started - Attended
CL3964 | 2023-11-24 | Devakottai | G | Outlet general visit | Preventive | Prasanna Narasimhan, Prasath and Lingeshwaran | 2023-11-24 | - | Camera and automation regular check up done - Completed
CL3965 | 2023-11-24 | Theni | C | Calibration and stamping work | Certification | Suresh Kumar | 2023-11-24 | - | Calibration and stamping done - Calibration details: A side old k- factor:106700 A side new k-factor -103250 B side old k-factor -108500 B side new k-factor -104990 K-factor both side changed A-testing : 265.94 L B-testing : 276.98 L Total testing: 542.92 L - Completed
CL3966 | 2023-11-24 | Bodi | C | Calibration and stamping work | Certification | Suresh Kumar | 2023-11-24 | - | Calibration and stamping done - Calibration details: A side k-factor -10000 B side k-factor -10000 K-factor both side no changed. A-testing : 141.77 L B-testing : 134.13 L Total testing: 275.90 L - Completed
CL3967 | 2023-11-24 | Uthamapalayam | C | Calibration and stamping work | Certification | Suresh Kumar | 2023-11-24 | - | Calibration and stamping done - Calibration details: A side k-factor -10000 B side k-factor -10100 K-factor both side no changed. A-testing : 153.63 L B-testing : 155.34 L Total testing: 308.97 L - Completed
CL3968 | 2023-11-24 | Kangeyam | D | A nozzle defect | Breakdown | Gowtham | 2023-11-24 | - | A nozzle replaced - Working fine - Resolved | Dispensing motor alignment to be done
CL3969 | 2023-11-24 | Ariyamangalam | D | B nozzle lock defect | Breakdown | Nepolean | 2023-11-24 | - | Nozzle lock replaced at B side - Working fine - Rectified
CL3970 | 2023-11-24 | Omalur | G | EB - RYB line B phase wire and fuse carrier burnt | Breakdown | Prabu | 2023-11-24 | - | Direct MCB line connected - Outlet working in EB mode - Attended
CL3971 | 2023-11-25 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2023-11-25 | - | Nozzle from Omalur outlet serviced and tested - Testing at D side : 4.65 L - Completed
CL3972 | 2023-11-25 | Velachery | D | CD dispenser hanging | Breakdown | Suneel Sagar | 2023-11-25 | - | Display cable reconnected - Working fine - Resolved
CL3973 | 2023-11-25 | Kangeyam | T | Dispensing motor alignment | Preventive | Gowtham and Chandrasekar | 2023-11-26 | - | Dispensing pump and motor replaced - Found Satisfactory - Completed
CL3974 | 2023-11-25 | Mulanur | R | Stabilizer R phase carbon bush, holder and clip worn out | Breakdown | Thirumalaisamy | 2023-11-25 | - | Stabilizer R phase carbon bush, holder and clip replaced - Outlet running in stabilizer mode - Rectified
CL3975 | 2023-11-25 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2023-11-25 | - | Omalur nozzle tested at D side - Testing : 4.65 L - Completed
CL3976 | 2023-11-25 | Velachery | D | CD dispenser hanging due to display card or cable disconnect | Breakdown | Suneel Sagar | 2023-11-25 | - | Display cable reconnected - Working fine - Resolved
CL3977 | 2023-11-25 | Vadivelan Nagar | R | 2HP compressor belt worn out | Breakdown | Suneel Sagar | 2023-11-25 | - | Compressor belt replaced with new - Working fine - Attended
CL3978 | 2023-11-25 | Vellakovil | D | C nozzle teeth defect | Breakdown | Thirumalaisamy | 2023-11-25 | - | Nozzle hammer teeth 4 nos replaced - Completed
CL3979 | 2023-11-26 | Cantonment | D | Yenen dispenser C side DP valve diaphragm inspection | Preventive | Chandrasekar | 2023-11-26 | - | DP valve diaphragm condition inspected - Testing : 0.36 L - Attended
CL3980 | 2023-11-27 | Omalur | T | Unloading process | Preventive | Prabu | 2023-11-27 | - | Unloading done - Completed
CL3981 | 2023-11-27 | Dharapuram | T | Unloading bypass valve O ring damaged | Preventive | Gowtham | 2023-11-27 | 4 Hours | Unloading bypass valve O ring replaced to arrest the leakage - Dispensing bypass valve plunger replaced - Both valves working fine - No leakage found - Resolved
CL3982 | 2023-11-27 | Ariyamangalam | D | C nozzle LPG leakage | Breakdown | Nepolean | 2023-11-27 | - | Spare nozzle replaced - D side LPG dispensing hose replaced - C side testing : 1.64 L - D side testing : 3.81 L - Completed
CL3983 | 2023-11-28 | Perundurai | D | Display hang due to dispenser not covered while raining | Breakdown | Avinash | 2023-11-28 | - | New keypad replaced and Display cleaned - Working fine - Resolved
CL3984 | 2023-11-29 | Ramnad | C | Stamping and Rule 18 work | Certification | Chandrasekar and Lingeshwaran | 2023-11-29 | - | Stamping done - Rule 18 done - All equipment tested - Earth regenerated - Calibration reports : "A" Side 10 ltrs= 9.94 "B" Side 10 ltrs= 9.94 "K" Factor No Changes. Testing Reports "A" Side = 218.80 ltrs "B" Side = 234.78 ltrs - Completed | A side keypad to be replaced
CL3985 | 2023-11-29 | Cantonment | D | A side metering unit LPG leakage | Breakdown | Nepolean | 2023-11-29 | - | Bearing and oil seal kit replaced with new - LPG leakage arrested - Kept under observation - A side testing : 4.70 L - Rectified
CL3986 | 2023-11-29 | Ariyamangalam | D | D side On/Off switch defect | Breakdown | Pandi Durai | 2023-11-29 | - | On/off switch replaced at D side - Resolved
CL3987 | 2023-11-30 | Dharmapuri | G | Fire extinguisher service | Preventive | Suresh Kumar | 2023-11-30 | - | Fire extinguisher service done - 9kg ABC extinguisher replaced - Fire safety training provided to pump staffs - Attended
CL3988 | 2023-11-30 | Vadivelan Nagar | T | Dispensing pump spider defect | Breakdown | Suneel Sagar | 2023-11-30 | - | Spider replaced - Dispensing motor working fine - Rectified
CL3989 | 2023-11-30 | Erode | G | Outlet general visit | Preventive | Avinash | 2023-11-30 | - | Compressor oil replaced - Attended
CL3990 | 2023-11-30 | Ariyamangalam | D | Nozzle servicing and testing | Preventive | Nepolean | 2023-11-30 | - | Omalur nozzle tested at D side - Testing : 1.51 L - Completed
CL3991 | 2023-11-30 | Devakottai | C | Rule 18 work | Certification | Chandrasekar | 2023-11-30 | - | Rule 18 work done - Earth regenerated - Earth value checked - Total area leakage tested - All equipments working fine - Resolved
CL3992 | 2023-11-30 | Cantonment | D | B nozzle leakage | Breakdown | Pandi Durai | 2023-11-30 | - | Nozzle hammer teeth replaced - Working good - Rectified
CL3993 | 2023-11-30 | Tharamangalam | G | Fire extinguisher service | Preventive | Suresh Kumar | 2023-11-30 | - | Fire extinguisher service done - 75 kg extinguisher refilling done - 2 hoses replaced - 9kg ABC extinguisher replaced - Painting done - Completed
CL3994 | 2023-11-30 | Uthamasolapuram | G | Fire extinguisher service | Preventive | Suresh Kumar | 2023-11-30 | - | Fire extinguisher service done - 9kg ABC extinguisher replaced - Fire safety training provided to pump staffs - Completed
CL3995 | 2023-12-01 | Sankari | R | Online UPS back up issue due to 12V 7ah battery failure | Breakdown | Avinash | 2023-12-01 | - | A 12V 7ah battery replaced in warranty - Back up seems good - Compressor oil changed - Completed
CL3996 | 2023-12-01 | Ariyamangalam | R | Compressor oil changing | Preventive | Pandi Durai | 2023-12-01 | - | Compressor oil changed - Working fine - Attended
CL3997 | 2023-12-01 | Bhavani | D | B nozzle dispensing hose damaged | Breakdown | Avinash | 2023-12-01 | - | Hose recrimping done and fixed - Compressor oil changed - Rectified
CL3998 | 2023-12-02 | Nasiyanur | G | Unloading training | Preventive | Avinash | 2023-12-02 | - | Unloading done - Unloading training provided to pump staffs - Tank 1 and 2 loop provided - Compressor oil changed - Resolved
CL3999 | 2023-12-02 | Thuraiyur | C | Rule 18 work | Certification | Nepolean, Nivas and Pandi Durai | 2023-12-02 | - | Rule 18 done - All equipment tested - Total leakage tested - Tank area earth pit corroded - New copper steel, SS bolt fixed and earth value checked - Unloading liquid and vapour hose acme adapter correded - corrosion removed and painting done - PMR done - Completed
CL4000 | 2023-12-02 | Ellis Nagar | D | A nozzle latch assembly defect | Breakdown | Kathiresan | 2023-12-02 | - | A nozzle latch assembly and front O ring replaced - Working fine - Rectified
CL4001 | 2023-12-03 | Hosur | D | A nozzle point jumping issue | Breakdown | Prabu | 2023-12-03 | - | A nozzle diaphragm screw adjusted - Display glass cut and cleaned - Both nozzles cleaned and serviced - Testing : A - 5.52 L - Working fine - Resolved
CL4002 | 2023-12-03 | Dharmapuri | A | Noise from CPU | Breakdown | Prabu | 2023-12-03 | - | CPU cleaned and serviced - Kept under observation - Rectified
CL4003 | 2023-12-04 | Perambalur | C | Stamping and calibration work | Certification | Nepolean and Pandi Durai | 2023-12-04 | - | Calibration and stamping done - Calibration Report A side old k- factor: 10000 B side old k-factor: 10000 A side new k-factor: 09900 B side new k-factor: 09900 K-factor both side no changed A side testing : 150.07 B side testing : 150.10 Total testing: 300.17 A side 10 Lts = 10.04 B side 10 Lts = 10.04 - Completed
CL4004 | 2023-12-04 | Neelambur | G | General site visit | Breakdown | Gowtham | 2023-12-04 | - | Online UPS back up time checked - Stand by time is 10 mins - Compressor oil changed - Motor spider replaced - Attended
CL4005 | 2023-12-04 | Ariyalur | C | Stamping and calibration work | Certification | Nepolean and Pandi Durai | 2023-12-04 | - | Calibration and stamping done - Calibration Report A side k-factor -10000 B side k-factor -10000 K-factor both side no changed. A-testing : 150.52 B-testing : 150.50 Total testing: 301.02 A side 10 Lts = 9.97 B side 10 Lts = 9.96 - Completed
CL4006 | 2023-12-05 | Namakkal 1 | D | A nozzle LPG leakage | Breakdown | Nivas | 2023-12-05 | - | Nozzle cleaned and serviced - Testing : 0.82 L - 1 KVA online UPS battery wated topped up and SS bolt nuts changed - Working fine - Rectified
CL4007 | 2023-12-06 | Uthamapalayam | A | RS485 to USB converter board defect | Breakdown | Kamaraj | 2023-12-06 | - | RS485 to USB converter board replaced - Dispenser back online - Working fine - Rectifed
CL4008 | 2023-12-06 | Attur | D | Batchan dispenser power card short circuited | Breakdown | Nivas | 2023-12-06 | From 2 pm | Testing A side : 110.07 L - B side : 14.07 L | A side not working
CL4009 | 2023-12-06 | Villapuram | D | Dispenser program switch defect | Breakdown | Kathiresan | 2023-12-06 | - | AB and CD both dispensers program switch replaced - Working good - Tank 1 motor indicator replaced - Resolved
CL4010 | 2023-12-06 | Ellis Nagar | G | Water dispenser installation | Preventive | Kathiresan | 2023-12-06 | - | Water dispenser installed - Working properly - Attended
CL4011 | 2023-12-07 | Erode | D | A nozzle not working properly | Breakdown | Avinash | 2023-12-07 | - | A nozzle serviced - Testing : 0.94 L - Working fine - Resolved
CL4012 | 2023-12-07 | Mettupalayam | C | Rule 19 and Rule 18 work | Certification | Gowtham | 2023-12-10 | 56 Hours | Rule 19 and Rule 18 work done - Earth regenerated - All equipments working fine - Testing : 17.22 L - Completed | Online UPS to be serviced - Automation is offline due to wamp server problem
CL4013 | 2023-12-07 | Ayothiyapattinam | R | Online UPS battery failure | Breakdown | Prabu | 2023-12-07 | - | New 7 ah battery 3 Nos replaced - Working good with battery back up of 10 mins - Rectified
CL4014 | 2023-12-08 | Dindigul | C | DL stamping work | Certification | Nepolean and Vigneshwaran | 2023-12-08 | - | DL stamping done - Both nozzle teeth replaced - Automation maintenance done - Testing : A side: 295.89 B side 270.10 Total lits : 565.99 lit. Old K factor : A side _ 09800 B sid _ 09800. New k factor : A side: 09600. B side: 09600. A side 10.00 lit--10.01 lit B side 10.00 lit --10.02 lit - Completed
CL4015 | 2023-12-09 | Udumalpet | C | Dispenser calibration and stamping work | Certification | Nepolean and Vigneshwaran | 2023-12-09 | - | Dispenser calibrated and stamping done - Dispenser Bottom side liquid line ROV Bottom LPG leakage arrested - Completed
CL4016 | 2023-12-10 | Aravakurichi | T | Unloading liquid hose adapter LPG leakage | Breakdown | Thirumalaisamy | 2023-12-10 | - | Unloading liquid hose adapter removed cleaned and refitted - Leakage arrested - Unloading done - Attended
CL4017 | 2023-12-11 | Viruthachalam | C | Calibration and stamping work | Certification | Nepolean and Pandi Durai | 2023-12-11 | - | Calibration and stamping done - Calibration Report A side k-factor -10100 B side k-factor -10200 K-factor both side no change A-testing : 159.52 B-testing : 150.86 Total testing: 310.38 - Completed
CL4018 | 2023-12-12 | Bhavani | G | Outlet visit | Breakdown | Avinash | 2023-12-12 | - | Rule 19 material requirement data collected - Attended
CL4019 | 2023-12-12 | Perambalur | R | Offline UPS back up issue | Breakdown | Pandi Durai | 2023-12-12 | - | 12V 7ah battery 1 No replaced - Back up is good - Rectified
CL4020 | 2023-12-12 | Ariyamangalam | D | B nozzle lock defect | Breakdown | Nepolean | 2023-12-12 | - | Nozzle lock replaced - Working fine - Resolved
CL4021 | 2023-12-12 | T.V.Kovil | D | Dispenser display glass damaged | Breakdown | Vigneshwaran | 2023-12-12 | - | Display glass replaced for both sides - Working fine - Resolved
CL4022 | 2023-12-12 | Villapuram | D | Vibration and noise from nozzle while tank filling | Breakdown | Kathiresan | 2023-12-12 | - | Dispenser pressure valve adjusted - Kept under observation - Rectified
CL4023 | 2023-12-13 | Musiri | C | Rule 18 work | Certification | Nivas, Nepolean and Pandi Durai | 2023-12-13 | - | Rule 18 work done - All equipment working fine - Total area leakage tested - A side nozzle replaced - Testing A side : 0.88 L - Completed
CL4024 | 2023-12-13 | Mettupalayam | T | Rochester dial and dispensing hose defect | Breakdown | Gowtham | 2023-12-13 | - | Rochester gauge dial replaced - Dispensing hose replaced at B side - No leakage found - Existing hose recrimped and kept as spare - Working good - Completed
CL4025 | 2023-12-13 | Eral | R | Online UPS error 63 occurred | Breakdown | Kathiresan | 2023-12-13 | - | Offline UPS connected - Rectified temporarily | Online UPS to be serviced
CL4026 | 2023-12-13 | Avadi | C | PMR work | Preventive | Suneel Sagar | 2023-12-13 | - | PMR done - Attended | 2" ROV - 1 No to be replaced
CL4027 | 2023-12-13 | Thuraiyur | T | Dispensing liquid line ball valve with ROV replacement | Breakdown | Pandi Durai | 2023-12-13 | - | Dispensing liquid line ball valve with ROV replaced - Unloading vapour line ball valve serviced - Rectified
CL4028 | 2023-12-13 | Karur | R | Turbo drive PLC defect ( Error Run LD) | Breakdown | Thirumalaisamy | 2023-12-13 | - | Error cleared in back end - Resolved
CL4029 | 2023-12-14 | Paramathivelur | C | Rule 18 work | Certification | Thirumalaisamy | 2023-12-14 | - | Rule 18 work done - ALDS earth regenerated - Total leakage tested - B nozzle hammer teeth changed - Unloading line pnuematic hose replaced with new - Completed
CL4030 | 2023-12-14 | Salem 2 | G | Site visit | New Project | Prakash | 2023-12-14 | - | Site visit done - Completed
CL4031 | 2023-12-14 | Hosur | G | New office construction | Renovation | Prakash | 2023-12-14 | - | Construction work started - Attended
CL4032 | 2023-12-14 | T.V.Kovil | G | N2 machine sensor problem | Breakdown | Nepolean | 2023-12-14 | - | Sensor replaced by Icon Embedded service person - Working good - Attended
CL4033 | 2023-12-14 | Kodumudi | C | Rule 18 work | Certification | Thirumalaisamy | 2023-12-14 | - | Rule 18 work done - ALDS earth regenerated - Total leakage tested - B nozzle hammer teeth changed - Completed
CL4034 | 2023-12-15 | T.V.Kovil | D | A nozzle teeth defect | Breakdown | Suresh Kumar | 2023-12-15 | - | Nozzle teeth replaced - Working fine - Attended
CL4035 | 2023-12-15 | Ammapet | G | EB ELCB problem | Breakdown | Avinash | 2023-12-15 | - | 63 A 4 pole MCB replaced with new - Outlet running both in EB and DG mode - Resolved
CL4036 | 2023-12-15 | Bathlagundu | R | Online UPS battery back up problem and ALDS control panel VSC conductor (MO-0 240/50HZ) due to EB high voltage | Breakdown | Kamaraj | 2023-12-15 | - | 12V 7 Ah batteries 3 Nos replaced - ALDS control panel VSC conductor (MO-0 240/50HZ) replaced - Working good - Rectified
CL4037 | 2023-12-15 | Karur | C | Rule 18 work | Certification | Thirumalaisamy | 2023-12-15 | - | Rule 18 work done - ALDS earth regenerated - Earth value checked - Total leakage tested - Completed | Turbo drive PLC sent to HO
CL4038 | 2023-12-15 | Puliyur | C | Rule 18 work | Certification | Thirumalaisamy | 2023-12-15 | - | Rule 18 work done - ALDS earth regenerated - Earth value checked - Total leakage tested -Automation equipment maintenance done - Completed
CL4039 | 2023-12-15 | Virudhunagar | G | Fire extinguisher service and renewal | Preventive | Kathiresan | 2023-12-15 | - | Fire extinguisher renewal and service done - Fire safety training provided to pump staffs - Completed
CL4040 | 2023-12-15 | Tenkasi | G | Fire extinguisher service and renewal | Preventive | Kathiresan | 2023-12-15 | - | Fire extinguisher renewal and service done - Fire safety training provided to pump staffs - Completed
CL4041 | 2023-12-15 | Tirunelveli | G | Fire extinguisher service and renewal | Preventive | Kathiresan | 2023-12-15 | - | Fire extinguisher renewal and service done - Fire safety training provided to pump staffs - Completed
CL4042 | 2023-12-15 | Eral | G | Fire extinguisher service and renewal | Preventive | Kathiresan | 2023-12-15 | - | Fire extinguisher renewal and service done - Fire safety training provided to pump staffs - Completed
CL4043 | 2023-12-15 | Tirunelveli | C | Calibration and stamping work | Certification | Kathiresan | 2023-12-15 | - | Calibration and stamping done - Calibration Report : "A" Side 10 ltrs = 9.98 "B" Side 10 ltrs = 10.00 "C" Side 10 ltrs = 9.93 "D" Side 10 ltrs = 9.95 "K" Factor Report : " A " Side = 10000 " B " Side = 10000 " C " Side = 10341 " D " Side = 10330 K Factor No Changes. Testing Report ; "A" Side = 142.59 "B" Side = 229.86 "C" Side = 155.07 "D" Side = 143.71 Total = 671.23 - Completed
CL4044 | 2023-12-16 | Kangeyam | R | Unloading solenoid valve defect | Breakdown | Gowtham | 2023-12-17 | - | Unloading solenoid valve replaced - Dispensing and unloading air hose replaced partially - Completed | Pump suction (liquid line) 1½" ball valve to be changed
CL4045 | 2023-12-16 | Tiruchengode | D | A side keypad not working | Breakdown | Avinash | 2023-12-16 | - | A side keypad changed - Working fine - Oil changed for both compressors - Resolved
CL4046 | 2023-12-17 | Tenkasi | A | Dispenser working in offline due to heavy rain | Breakdown | Kathiresan | 2023-12-18 | - | Dispenser back online - Attended
CL4047 | 2023-12-18 | Thanjavur | T | Dispensing motor love joy coupling spider damaged | Breakdown | Pandi Durai | 2023-12-18 | - | Lovejoy coupling spider replaced - Oil changed for both compressors - Unloading liquid line ROV air leakge arrested by tightening the stem - Air machine clip connector replaced - Working fine - Rectified
CL4048 | 2023-12-18 | Tirunelveli | G | Sales stopped due to heavy rain | Preventive | Kathiresan | 2023-12-18 | 44 Hours | Sales started - No damage found - All equipements working good - Working in genset mode - Testing : 8 Ltrs - Attended
CL4049 | 2023-12-18 | Kattupakkam | T | SRV thread damaged | Breakdown | Suneel Sagar | 2023-12-18 | - | SRV replaced - Resolved
CL4050 | 2023-12-19 | Palakkad | C | Mass flow meter calibration at FCRI | Certification | Gowtham | 2023-12-19 | - | Mass flow meter calibration done at FCRI - Completed
CL4051 | 2023-12-19 | Ariyalur | R | Master solenoid coil air leakage | Breakdown | Pandi Durai | 2023-12-19 | - | Interchanged the unloading coil - Oil changed for both compressors - Dispensing vapour line ROV air leakage arrested by tightening the stem - PMR done - Resolved
CL4052 | 2023-12-19 | Karur | R | Turbo drive PLC defect | Breakdown | Thirumalaisamy | 2023-12-19 | - | PLC error cleared - Pump running in turbo drive - Under observation - Rectified
CL4053 | 2023-12-20 | Mettupalayam | C | Calibration work | Breakdown | Gowtham | 2023-12-20 | - | Calibration work done - K factor A&B side -10200 No changes in K factor A side - 9.86/10 ltr B side - 9.90/10 ltr Testing ltr- 422.14 ltr. A side - 248.01 ltr. B side - 174.13 ltr. Safety and unloading training provided to pump staffs - Completed
CL4054 | 2023-12-20 | Hosur | G | Outlet visit | Renovation | Prabu | 2023-12-20 | - | Civil marking done - Attended
CL4055 | 2023-12-21 | Bhavani | C | Rule 19 and additional dispenser installation | Certification | Chandrasekar, Prakash and Suresh Kumar | 2023-12-23 | 2 Days | Rule 19 done - Additional dispenser installed - Sales started - Rule 18 done - Dispenser calibration done - Earth value tested and regenerated - Dispenser connected iwht automation IP board - ATG and HLA cable replaced with new -K Factor A-10000 B-10000 A-10 Lts =10.00 Lts B-10 Lts = 10.06 Lts Printer fixed - Completed | Sales stopped at 6 pm - Tank percentage 17% - Rule 19 work started - Bhavani Pump totalizer reading: A side-2226125.18 B side-2661019.81
CL4056 | 2023-12-21 | Dharapuram | T | ATG console not working | Breakdown | Gowtham | In process | - | In process
CL4057 | 2023-12-21 | Tharamangalam | R | 1 KVA UPS board heating issue | Breakdown | Prabu | 2023-12-21 | - | Spare UPS replaced - Working fine - Resolved | Faulty UPS sent to Mothish for servicing
CL4058 | 2023-12-22 | Mettupalayam | C | Stamping work | Certification | Gowtham | 2023-12-22 | - | Stamping done - Online UPS battery 27 ah replaced - Attended
CL4059 | 2023-12-22 | Aravakurichi | T | Unloading vapour ROV leakage | Breakdown | Thirumalaisamy | 2023-12-24 | - | ROV replaced - Working fine - Resolved
CL4060 | 2023-12-22 | Chengalpattu | C | PMR work | Certification | Suneel Sagar | 2023-12-22 | - | PMR done - DG shifted as per NH norms - Completed
CL4061 | 2023-12-22 | Villapuram | G | Site visit | Preventive | Kathiresan | 2023-12-22 | - | Oil changed for both compressors - NRV tension adjusted for ALDS compressor - Attended
CL4062 | 2023-12-23 | Tharamangalam | D | Dispenser motherboard hanging and error 21 occurred | Breakdown | Prabu | 2023-12-23 | - | Power cable reconnected - Working in DG mode due to power fluctuation - Working fine -Resolved
CL4063 | 2023-12-23 | Eral | D | Dispenser reading reverse due to power supply issue | Breakdown | Kathiresan | 2023-12-23 | - | Permission given from backend - Dispenser back online - Sales started - Rectified | Reverse reading : "A" Side = 47.81 "B" Side = 72.95 Online UPS sent to Mothish
CL4064 | 2023-12-23 | Namakkal 3 | D | Dispenser B side keypad defect | Breakdown | Nivas | 2023-12-23 | - | New keypad replaced at B side - Resolved
CL4065 | 2023-12-24 | Tharamangalam | D | Error 21 occurred in Dispenser while running in EB | Breakdown | Thirumalaisamy and Prabu | 2023-12-25 | - | Dispenser mother board replaced - Totalizer reading A side 1521.69 B side 1262.39 K factors A side 10250 B side 10250 - Working fine - Completed
CL4066 | 2023-12-26 | Thanjavur | T | Unloading bypass valve cleaning and Rochester gauge dial stuck up | Breakdown | Pandi Durai | 2023-12-26 | - | Unloading bypass valve cleaned - Rochester dial stuck up released - Resolved
CL4067 | 2023-12-26 | Cantonment | D | B nozzle LPG leakage | Breakdown | Nepolean | 2023-12-26 | - | Spare serviced nozzle replaced - Working fine - Testing B side : 0.75 Ltrs - Attended
CL4068 | 2023-12-26 | Bhavani | C | New dispenser stamping | Certification | Avinash | 2023-12-26 | - | Dispenser stamping done - Automation installed - Completed | Opening Reading C-1074.55 D-1162.49
CL4069 | 2024-12-26 | Vadivelan Nagar | D | DP valve diaphragm defect in C nozzle | Breakdown | Suneel Sagar | 2023-12-26 | - | DP valve diaphragm replaced - All 4 nozzles are in operation - Attended
CL4070 | 2024-12-26 | Vedachandur | T | Dispensing pump mechanical seal kit defect | Breakdown | Kamaraj | 2023-12-26 | 6 Hours | Spare pump replaced - Working good - Sales started - Rectified | Pump sent to HO for service
CL4071 | 2024-12-27 | Vellakovil | A | Automation work | New Project | Thirumalaisamy | 2023-12-27 | - | Automation installation done partially - Attended
CL4072 | 2023-12-28 | Vellakovil | A | Automation work | New Project | Thirumalaisamy | 2023-12-29 | - | Automation installation done - Dispenser working online - Kept under observation - Automation training provided to pump staffs - Attended
CL4073 | 2023-12-28 | Namakkal 2 | D | AB dispenser On/Off switch broke down | Breakdown | Nivas | 2023-12-28 | - | Yenen On/Off switches replaced with new - Working fine - Rectified
CL4074 | 2023-12-28 | T.V.Kovil | D | C nozzle hammer teeth defect | Breakdown | Vigneshwaran | 2023-12-28 | - | Hammer teeth 4 Nos replaced - Attended
CL4075 | 2023-12-29 | Ramnad | G | Main MCB short circuited, fuse damage due to high power input and Online UPS error 55 occurred | Breakdown | Kathiresan | 2023-12-29 | - | New 40 Amps MCB replaced - 63 Amps fuse replaced - A side keypad changed - Resolved | Online UPS sent to Mothish
CL4076 | 2023-12-29 | Kangeyam | R | Auxiliary contactor burnt due to high voltage | Breakdown | Gowtham | 2023-12-29 | 40 Mins | Stabilizer affected by fluctuations - Servo mode not working - Stabilizer directed - Panel working in direct genset power - Contactor and OLR relay replaced - Rectified temporarily | Stabilizer to be serviced
CL4077 | 2023-12-29 | Rasipuram | A | Yenen software closed abruptly after every transaction | Breakdown | Nivas | 2023-12-29 | - | Automation cable rewiring done - Earthing wire refitted - Dispenser B side keypad replaced - Rule 19 data collected - Completed
CL4078 | 2023-12-29 | Bhavani | G | Site visit | Preventive | Avinash | 2023-12-29 | - | All equipments leakage checked - EB phase input problem to be rectified by EB person - Training provided to pump staffs - Attended
CL4079 | 2023-12-29 | Ariyamangalam | D | B and C nozzle teeth defect | Breakdown | Pandi Durai | 2023-12-29 | - | Nozzle hammer teeth replaced - D side spare nozzle replaced - Testing D side : 0.75 Ltrs - Working good - Rectified
CL4080 | 2023-12-29 | Kangeyam | R | Servo stabilizer contactor, fuse and relay defect | Breakdown | Gowtham | 2023-12-29 | - | Servo stabilizer contactor, fuse and relay replaced - Stabilizer working in both EB and Genset mode - Dispensing suction ball valve and compressor drain water valve replaced - DB box input connector - Found satisfatory - Resolved
CL4081 | 2023-12-30 | Uthamapalayam | G | Fire extinguisher servicing | Preventive | Kamaraj | 2023-12-30 | - | Fire extinguisher service done - Safety training provided to pump staffs - All equipments working good - Attended
CL4082 | 2023-12-30 | Kodumudi | D | Nozzle hose replacement | Breakdown | Thirumalaisamy | 2023-12-30 | - | A and B side nozzle hose replaced - Rubber mat changed in EB room - Automation maintenance done - Rectified
CL4083 | 2023-12-30 | Bodi | G | Fire extinguisher servicing | Preventive | Kamaraj | 2023-12-30 | - | Fire extinguisher service done - Safety training provided to pump staffs - All equipments working good - Attended
CL4084 | 2023-12-30 | Theni | G | Fire extinguisher servicing | Preventive | Kamaraj | 2023-12-30 | - | Fire extinguisher service done - Safety training provided to pump staffs - Batchen dispenser nozzle front O ring replaced in both sides - A nozzle teeth replaced - All equipments working good - Attended
CL4085 | 2023-12-31 | Musiri | A | Automation CPU fan issue | Breakdown | Pandi Durai | 2023-12-31 | - | Spare CPU replaced - Automation working good - Rectified