## Sheet1
Service Logs - Jan' 2024 to Dec' 2024
ticket_no | date | name_of_the_outlet | code | nature_of_the_complaint | breakdown__ preventive | service_engineer | rectified_on | interruption_of_sales_if_any__time_duration | details_of_work_done
CL4086 | 2024-01-01 | Bhavani | R | Control panel not booting due to one phase surge arrester plug damage | Breakdown | Avinash | 2024-01-01 | 2.15 Hours | Surge arrester looped - Panel working - Sales started - Attended
CL4087 | 2024-01-04 | Virudhunagar | R | ALDS compressor not working and A nozzle defect | Breakdown | Kathiresan | 2024-01-04 | - | Compressor starter relay replaced - A and B nozzle teeth replaced - N2 machine On/Off switch changed - Rectified
CL4088 | 2024-01-04 | T.V.Kovil | D | A nozzle teeth defect | Breakdown | Vigneshwaran | 2024-01-04 | - | A nozzle teeth replaced - Oil changed for both compressors - Resolved
CL4089 | 2024-01-04 | Cantonment | R | Offline UPS battery defect | Breakdown | Chandrasekar | 2024-01-04 | - | 12 V 7 ah battery replaced in offline UPS - Working normally - Completed
CL4090 | 2024-01-05 | Villapuram | D | To replace D nozzle teeth due to the limit crossed more than 150000 L | Preventive | Kathiresan | 2024-01-05 | - | D nozzle teeth replaced - Working fine - Rectified
CL4091 | 2024-01-05 | Ellis Nagar | D | D side keypad not working properly | Breakdown | Kathiresan | 2024-01-05 | - | Keypad replaced in D side - Working properly - Attended
CL4092 | 2024-01-05 | Manapparai | G | Fire extinguisher service work | Preventive | Nepolean | 2024-01-05 | - | Fire extinguisher renewal and service work done - Completed
CL4093 | 2024-01-05 | Ariyamangalam | D | D nozzle leakage | Breakdown | Pandi Durai | 2024-01-05 | - | Spare nozzle changed - Working properly - Testing D side : 0.78 L - Resolved
CL4094 | 2024-01-06 | Omalur | A | Dispenser reading reverse due to EB supply fluctuation | Breakdown | Prabu | 2024-01-06 | - | Reverse reading noted - Authorized to dispense at the back end - Resolved
CL4095 | 2024-01-06 | Viruthachalam | R | ALDS compressor running continuously due to dispensing line air hose damaged | Breakdown | Pandi Durai | 2024-01-06 | - | Dispensing pneumatic line replaced with new - Compressor oil changed - Dispensing vapour line ROV air leakage arrested by tightening the stem - Working properly - Recitifed
CL4096 | 2024-01-06 | Bhavani | R | Surge arrester fuse replacement | Breakdown | Avinash | 2024-01-06 | - | Surge arrester loop removed - New fuse replaced - Working satisfoctory - Attended
CL4097 | 2024-01-08 | Kumbakonam | D | Dispenser bottom vapour line ROV air leakage | Breakdown | Pandi Durai | 2024-01-08 | - | Dispensing ROV replaced with unloading ROV - Oil changed for both compressors - PMR done - Attended
CL4098 | 2024-01-08 | Tharamangalam | R | Servo stabilizer R phase carbon bush, winding coil and motor gear wheel set burnt out | Breakdown | Prabu | 2024-01-08 | 30 Mins | Servo stabilizer to be serviced - Connected with direct MCB - Attended
CL4099 | 2024-01-08 | Vadivelan Nagar | T | Dispensing pump spider defect | Breakdown | Suneel Sagar | 2024-01-08 | - | Spider replaced with new - Dispensing pump working properly - Rectified
CL4100 | 2024-01-09 | Tenkasi | C | Calibration and stamping work | Certification | Kathiresan | 2024-01-10 | - | Stamping and calibration done - Calibration report: "A" Side 10 ltrs= 9.94 "B" Side 10 ltrs= 9.94 "K" Factor Report: "A" Side = 10050 "B" Side = 10050 No Changes in K Factor. Testing Reports: "A" Side = 155.84 ltrs "B" Side = 160.14 ltrs - Completed
CL4101 | 2024-01-10 | Manapparai | T | Cathodic protection testing | Preventive | Nepolean | 2024-01-10 | - | CP voltage checked and tested - Anode A1 and reference cell workings found not satistactory - Attended
CL4102 | 2024-01-11 | Vadivelan Nagar | T | Dispensing pump abnormal noise and vibration | Breakdown | Suneel Sagar | 2024-01-11 | - | Pump lovejoy coupling replaced - Pipe line realignment done - Vibration and noise arrested - Rectified
CL4103 | 2024-01-11 | Villapuram | C | Calibration and stamping work | Certification | Kathiresan | 2024-01-11 | - | Stamping and calibration done - B side DP valve diaphragm replaced - Working properly - Calibration Report : "A" Side 10 ltrs = 9.98 "B" Side 10 ltrs = 10.01 "C" Side 10 ltrs = 10.02 "D" Side 10 ltrs = 9.97 "K" Factor Report : " A " Side = 10070 " B " Side = 10000 " C " Side = 10300 " D " Side = 10030 Testing Report ; "A" Side = 297.58 "B" Side = 482.10 "C" Side = 237.06 "D" Side = 238.82 Total = 1255.56 - Completed
CL4104 | 2024-01-12 | Sulur | C | PMR work | Preventive | Gowtham | 2024-01-12 | - | PMR done - Unloading motor belt replaced - Completed
CL4105 | 2024-01-13 | Ramnad | R | Online UPS installation and unloading vapour hose testing | Breakdown | Kathiresan | 2024-01-13 | - | Unloading vapour hose checked visibly and no leakage found - Online UPS installed - Attended
CL4106 | 2024-01-13 | T.V.Kovil | R | Servo stabilizer servicing | Breakdown | Nepolean | 2024-01-13 | - | Servo stabilizer serviced - Kept under observation - Rectified
CL4107 | 2024-01-13 | Cantonment | A | Automation loyalty program app installation and testing | New Project | Chandrasekar | 2024-01-13 | - | New loyalty program app installed and tested - E side tesing : 7 L - Completed
CL4108 | 2024-01-13 | Cantonment | G | Oil dispenser dispensing quantity testing | Preventive | Chandrasekar | 2024-01-13 | - | Oil dispenser dispensing quantity tested - Testing : 8.50 L - Checked
CL4109 | 2024-01-13 | Cantonment | A | Automation going without mobile for testing loyalty program app | New Project | Madhavan | 2024-01-13 | - | Automation working with mobile after tested the app - Attended
CL4110 | 2024-01-13 | Kodungaiyur | G | Compound wall support rewelding | Breakdown | Suneel Sagar | 2024-01-13 | - | Compound wall support rewelding done - Attended
CL4111 | 2024-01-14 | Cantonment | A | Automation loyalty program app installation and testing | New Project | Chandrasekar | 2024-01-14 | - | Loyalty program app installed and tested - Night shift testing : E.side testing.24.39 L F.side testing.8 L - Completed
CL4112 | 2024-01-15 | Cantonment | A | Loyalty scheme app launch | New Project | Prakash and Madhavan | 2024-01-15 | - | Loyalty scheme has been activated in three of our COCO outlets at Tiruchirappalli - Tested successfully - Completed
CL4113 | 2024-01-15 | T.V.Kovil | A | Loyalty scheme app installation and testing | New Project | Vigneshwaran | 2024-01-15 | - | Loyalty scheme app installation and testing done - Testing at A side : 1.34 L - Attended
CL4114 | 2024-01-16 | Musiri | G | Fire extinguisher service work | Preventive | Nivas | 2024-01-16 | - | Fire extinguisher renewal and service work done - Completed
CL4115 | 2024-01-16 | Namakkal 2 | G | Fire extinguisher service work | Preventive | Nivas | 2024-01-16 | - | Fire extinguisher renewal and service work done - Completed
CL4116 | 2024-01-16 | Tharamangalam | R | Servo stabilizer servicing | Breakdown | Prabu | 2024-01-16 | - | Servo stabilizer serviced and installation done - Rectified
CL4117 | 2024-01-16 | Eral | R | Online UPS PCB defect | Breakdown | Kathiresan | 2024-01-16 | - | Online UPS main PCB changed and serviced - Working properly - Back up time : 25 Mins - Rectified
CL4118 | 2024-01-16 | Tiruchengode | A | Sales going offline due to CPU issue | Breakdown | Avinash | 2024-01-16 | - | CPU replaced with new - Resolved
CL4119 | 2024-01-17 | Kangeyam | D | Kalvacha dispenser provides signal to motor automatically | Breakdown | Gowtham | 2024-01-17 | - | Spare mother board installed - Dispenser kept under observation - Resolved
CL4120 | 2024-01-17 | Tiruchengode | D | Dispenser B side keypad defect | Breakdown | Nivas | 2024-01-17 | - | New keypad replaced at B side - Working satisfactory - Attended
CL4121 | 2024-01-17 | T.V.Kovil | D | Batchen dispenser A side On/Off switch defect and leakage found inside metering unit due to filter damage | Breakdown | Nepolean | 2024-01-17 | - | On/off switch replaced with new one - Metering unit filter replaced with new - Leakage arrested - Working properly - Completed
CL4122 | 2024-01-19 | Namakkal 1 | D | B nozzle leakage | Breakdown | Nivas | 2024-01-19 | - | Nozzle teeth 4 Nos replaced - Leakage arrested - Rectified
CL4123 | 2024-01-19 | Avadi | T | ATG probe error | Breakdown | Suneel Sagar | 2024-01-19 | - | ATG wiring reconnected - Display shows the tank percentage - Attended
CL4124 | 2024-01-20 | Thuraiyur | D | B nozzle leakage | Breakdown | Nivas | 2024-01-20 | - | New nozzle replaced at B side - Testing : 0.81 L - Resolved
CL4125 | 2024-01-20 | Dharapuram | R | Neutral surge fuse failure | Breakdown | Gowtham | 2024-01-20 | - | Fuse replaced in neutral surge protector- Working properly - Rectified
CL4126 | 2024-01-20 | Villapuram | R | Dispensing PLC programming adjusting due to high EB bill | Preventive | Kathiresan | 2024-01-20 | - | Dispensing PLC programming adjusted to Tank 1 and Tank 2 - Attended
CL4127 | 2024-01-20 | Namakkal 2 | D | Dispenser nozzle hose sleeve damaged | Breakdown | Nivas | 2024-01-20 | - | New nozzle 5m hose replaced - CO2 hose replaced - Testing : 0.65 L - Resolved
CL4128 | 2024-01-21 | Ellis Nagar | A | Dispenser C and D side reading reverse due to EB supply fluctuation | Breakdown | Kathiresan | 2024-01-21 | - | Reverse reading noted - Authorized to dispense at the back end - Resolved
CL4129 | 2024-01-23 | Rasipuram | A | Dispensing yenen program closed automatically | Breakdown | Nivas | 2024-01-23 | - | CAT6 cable from dispenser and RS485 to USB converter board rewiring done - Spare cable changed for RS485 converter board - Kept under observation - Rectified
CL4130 | 2024-01-23 | Hosur | G | Office room building installation work | Breakdown | Prakash and Vigneshwaran | 2024-01-25 | - | Office room building installed - Roof concrete work in process - Attended
CL4131 | 2024-01-23 | Vedachandur | A | Internet is not working | Breakdown | Kamaraj | 2024-01-23 | - | Internet problem sorted out - Nozzle teeth replaced in both ends - Attended
CL4132 | 2024-01-23 | Ellis Nagar | R | Offline UPS battery back up is low | Preventive | Kathiresan | 2024-01-23 | - | Offline UPS 12V 7AH battery replaced - Back up seems alright - Completed
CL4133 | 2024-01-24 | Bathlagundu | D | B side keypad is not working | Breakdown | Kamaraj | 2024-01-24 | - | New keypad replaced at B side - Automation maintenance done - PMR done - Attended
CL4134 | 2024-01-24 | Cantonment | G | Oil dispenser flow meter leakage | Breakdown | Chandrasekar | 2024-01-24 | - | Flow meter O ring replaced - No leakage found - Working properly - Testing : 2 L - Resolved
CL4135 | 2024-01-25 | Bhavani | T | Tank area dispensing line vapour ROV head air leakage | Breakdown | Avinash | 2024-01-25 | - | ROV interchanged with unloading ballvalve - Rectified temporarily
CL4136 | 2024-01-25 | Namakkal 2 | D | Dispenser bottom vapour line ROV air leakage | Breakdown | Nivas | 2024-01-25 | - | ROV interchanged with unloading ballvalve - Rectified temporarily
CL4137 | 2024-01-25 | Rasipuram | A | IP board worn out due to earthing issue | Breakdown | Nivas | 2024-01-26 | - | Automation connection has been given through New IP board - Under observation - Resolved
CL4138 | 2024-01-25 | Ammapet | D | A side keypad not working properly | Breakdown | Avinash | 2024-01-25 | - | Keypad replaced with new - Working properly - Completed
CL4139 | 2024-01-27 | Bathlagundu | A | Bill printer not working | Breakdown | Nivas | 2024-01-27 | - | New bill printer installation done - Working fine - Attended
CL4140 | 2024-01-27 | T.V.Kovil | A | Automation billing application for loyalty program testing | Preventive | Vigneshwaran | 2024-01-27 | - | App testing done - Testing : 3 L - Completed
CL4141 | 2024-01-28 | Tenkasi | A | Dispenser A and B side totalizer reverse due to EB supply fluctuation | Breakdown | Kathiresan | 2024-01-28 | - | Reverse reading noted - Authorized to dispense at the back end - Resolved
CL4142 | 2024-01-29 | T.V.Kovil | D | C nozzle leakage and point jumping | Breakdown | Suresh Kumar | 2024-01-29 | - | Hammer teeth and front O ring replaced in C nozzle - Working properly - Rectified
CL4143 | 2024-01-29 | Namakkal 2 | C | Calibration and stamping work | Certification | Nivas | 2024-01-29 | - | Calibration and stamping work done - "A" Side 10 ltrs= 9.98 "B" Side 10 ltrs= 9.96 New "K" Factor Reports: "A" Side = 10050 "B" Side = 10050 Old "K" Factor : "A" Side = 10100 "B" Side = 10100 Testing : "A" Side = 258.74 ltrs "B" Side = 303.98 ltrs - Completed
CL4144 | 2024-01-31 | Ariyalur | T | Tank area dispensing liquid line ROV inside air leakage | Breakdown | Pandi Durai | 2024-01-31 | - | Unloading line ROV interchanged - General check up done - Rectified Temporarily
CL4145 | 2024-01-31 | Dharmapuri | C | Calibration and stamping work | Certification | Prabu | 2024-01-31 | - | Calibration and stamping work done - "A" Side 10 ltrs= 9.94 "B" Side 10 ltrs= 9.96 K" Factor Reports: "A" Side = 10100 "B" Side = 10100 Testing Reports : "A" Side = 110.00 ltrs "B" Side = 100.00 ltrs - Dispenser display cable replaced - Working properly - Completed
CL4146 | 2024-01-31 | T.V.Kovil | R | MOL error at Turbo Drive | Breakdown | Nepolean | 2024-01-31 | - | Turbo drive reset done - Pump running properly - Resolved
CL4147 | 2024-02-01 | Nasiyanur | D | Keypads are not working at both A and B side of the dispenser | Breakdown | Avinash | 2024-02-01 | - | New keypads replaced in both sides - Rectified
CL4148 | 2024-02-01 | Erode | A | Printer position changing | Preventive | Avinash | 2024-02-01 | - | Printer shifted from office room to dispenser area - Working properly - Completed
CL4149 | 2024-02-02 | Bodi | A | Automation CPU heating issue | Breakdown | Kamaraj | 2024-02-02 | - | Automation maintenance done - Cleaned and fixed - Working fine - Attended
CL4150 | 2024-02-02 | Uthamapalayam | D | B side keypad is not working | Breakdown | Kamaraj | 2024-02-02 | - | New keypad replaced at B side - Dispensing motor spider replaced with new - Automation maintenance done - Rectified
CL4151 | 2024-02-02 | Palladam 1 | C | Calibration and stamping work | Certification | Gowtham | 2024-02-02 | - | Calibration and stamping done - A side ltr - 9.98/10.00 B side ltr - 9.96/10.00 C side ltr - 9.98/10.00 D side ltr - 9.99/10.00 K Factor A&B - 101000 C&D - 10050 Total testing ltr - 451.09 ltr - Completed
CL4152 | 2024-02-02 | Ellis Nagar | D | Nozzle and nozzle teeth replacement as a preventive measure | Preventive | Kathiresan | 2024-02-02 | - | B nozzle replaced as the nozzle is working over 873500 Litres - C nozzle teeth replaced as it is working over 150000 Litres - Completed
CL4153 | 2024-02-02 | Ammapet | G | EB voltage drop and Genset starting issue | Breakdown | Avinash | 2024-02-02 | 1.30 Hours | EB phase voltages became normal - Sales started - Attended
CL4154 | 2024-02-05 | Ellis Nagar | A | CD dispenser Printer sensor defect | Breakdown | Kathiresan | 2024-02-23 | - | CD printer sensor and self motor replaced - Working properly - Control panel indicator light 2 nos replaced - Resolved
CL4155 | 2024-02-05 | Kattupakkam | C | PMR work | Preventive | Suneel Sagar | 2024-02-05 | - | PMR work done - Completed
CL4156 | 2024-02-06 | Tirunelveli | G | Generator site visit | Preventive | Prakash and Kathiresan | 2024-02-06 | - | Outlet visit done - Everything seems okay - Attended
CL4157 | 2024-02-06 | Ariyamangalam | D | D side error 23 occurred | Breakdown | Nepolean | 2024-02-06 | - | Cold boot done - Error cleared - Resolved
CL4158 | 2024-02-06 | T.V.Kovil | D | Batchen dispenser A nozzle teeth worn out | Breakdown | Vigneshwaran | 2024-02-06 | - | Nozzle teeth 4 Nos replaced - Leakage arrested - Rectified
CL4159 | 2024-02-07 | Hosur | G | Generator battery defect | Breakdown | Prabu | 2024-02-08 | - | 12V 100 Ah Genset battery replaced - Working fine - Ammonia plant compressor oil changed - Air leakage checked - Attended
CL4160 | 2024-02-07 | Avinashi | C | PMR work | Preventive | Gowtham | 2024-02-07 | - | PMR done - Tank 2 dispensing solenoid valve replaced - Compressor oil changed - Completed
CL4161 | 2024-02-07 | Villapuram | D | Nozzle replacement as a preventive measure | Preventive | Kathiresan | 2024-02-07 | - | B nozzle replaced as the nozzle is working over 1268200 Litres - Working satisfactory - Completed
CL4162 | 2024-02-08 | Ariyamangalam | D | Error 23 occurred | Breakdown | Nepolean | 2024-02-08 | - | Cold boot done - Error cleared - Resolved
CL4163 | 2024-02-08 | Tiruchengode | C | PMR work | Preventive | Avinash | 2024-02-08 | - | PMR done and all area leakage tested - Completed
CL4164 | 2024-02-08 | Dharapuram | G | Camera is not working | Breakdown | Gowtham | 2024-02-09 | - | Service persons from Pragyaa Communications serviced and installed the camera - Working fine - Attended
CL4165 | 2024-02-08 | Kodungaiyur | R | Tank 1 3 way selector switch worn out in control panel | Breakdown | Suneel Sagar | 2024-02-08 | - | 3 way selector switch in control panel replaced - Rectified
CL4166 | 2024-02-08 | Sangagiri | R | Offline UPS battery defect | Breakdown | Avinash | 2024-02-08 | - | 12V 7 Ah battery replaced with new one - Working fine - PMR done - Leakage tested - Completed
CL4167 | 2024-02-08 | Avadi | T | Fill point liquid line ROV defect | Breakdown | Suneel Sagar | 2024-02-08 | - | 2" ROV replaced with new one - Resolved
CL4168 | 2024-02-09 | Mulanur | R | Stabilizer mode not working due to R phase variac damaged | Breakdown | Thirumalaisamy | 2024-02-10 | - | New variac replaced in stabilizer - Carbon bush changed for all variacs - Stabilizer working fine - Tank area dispensing line vapour ROV LPG leakage arrested - Automation equipement maintnenance done - Rectified
CL4169 | 2024-02-09 | Nasiyanur | T | Dispensing solenoid coil air leakage | Breakdown | Avinash | 2024-02-09 | - | New solenoid coil replaced - Working fine - PMR done - Tank area leakage checked - Completed
CL4170 | 2024-02-09 | Cantonment | D | Calibration work | Certification | Nepolean | 2024-02-09 | - | Calibration done - Testing A side: 150.15 B side: 221.11 C side: 150.17 D side: 150.84 E side : 151.07 F side: 172.52 Total: 995.86 L - Completed
CL4171 | 2024-02-09 | Tenkasi | A | Automation rack reinstallation | Preventive | Kathiresan | 2024-02-09 | - | Automation rack and equipements reinstallation and maintenance done - PMR done - Working properly - Attended
CL4172 | 2024-02-12 | Udumalpet | C | PMR work | Preventive | Gowtham | 2024-02-12 | - | PMR work done - Compressor oil changed - Batchen dispenser hose replaced at both nozzles - Completed
CL4173 | 2024-02-12 | Vellakovil | T | Dispensing motor vibration and noise | Breakdown | Thirumalaisamy | 2024-02-12 | - | Dispensing motor spider replaced - Statuatory, SOP and warning boards installed - Attended
CL4174 | 2024-02-12 | Omalur | C | PESO inspection | Certification | Prakash and Venkatesh | 2024-02-12 | - | PESO inspection done - Completed
CL4175 | 2024-02-12 | Kattupakkam | T | Dispensing motor vibration and noise | Breakdown | Suneel Sagar | 2024-02-12 | - | Dispensing motor spider replaced - Attended
CL4176 | 2024-02-13 | Vedachandur | T | Dispensing motor not working | Breakdown | Pandi Durai and Nepolean | 2024-02-13 | - | Dispensing motor oil seal replaced and kept under observation - Attended
CL4177 | 2024-02-14 | Dharmapuri | D | B side display hang randomly | Breakdown | Prabu | 2024-02-14 | - | Dispenser display and display cables reconnected - Working properly - Kept under observation - B Nozzle rope replaced - Resolved
CL4178 | 2024-02-14 | Chinnasalem | A | A nozzle reverse | Breakdown | Madhavan | 2024-02-14 | - | Reverse reading noted - Authorized to dispense at the back end - Resolved
CL4179 | 2024-02-15 | Vedachandur | D | A nozzle 5m dispensing hose LPG Leakage | Breakdown | Kamaraj | 2024-02-15 | - | 5m nozzle hose replaced at A side - Nozzle front O ring replaced at both sides - Rectified
CL4180 | 2024-02-15 | Ariyamangalam | A | Automation system maintenance | Preventive | Madhavan | 2024-02-15 | - | System cleaned and maintenance done - Completed
CL4181 | 2024-02-15 | Pudukkottai | D | Dispenser B side DP valve diaphragm punctured | Breakdown | Nepolean and Pandidurai | 2024-02-15 | - | DP valve diaphragm replaced with new - Under observation for 2 days - Day shift testing "B" side = 9.14 ltr. Night shift testing "A" side = 0.53 ltr "B" side = 5.16 ltr. Total testing = 14.83 ltr - Completed
CL4182 | 2024-02-15 | Cantonment | C | Stamping and calibration work | Certification | Nepolean | 2024-02-15 | - | Stamping and calibration work done - "B"side = 69.45 ltr "E"side = 58.66 ltr Total testing = 128.11 ltr - Completed
CL4183 | 2024-02-15 | Palayam | R | Dispenser to EB room pneumatic hose damaged | Breakdown | Thirumalaisamy | 2024-02-15 | - | Pneumatic hose replaced with new - PMR done - Automation equipement maintenance done - Rectified
CL4184 | 2024-02-16 | Attur | C | Stamping and calibration work | Certification | Nivas, Nepolean and Pandi Durai | 2024-02-16 | - | Calibration and Stamping done - Calibration reports: "A" Side 10 ltrs = 10.01 "B" Side 10 ltrs = 9.98 "C" Side 10 ltrs = 10.02 "D" Side 10 ltrs = 9.97 K" Factor Reports: "A" Side old K Factor = 100500 "A" Side new K Factor = 101000 "B" Side K Factor = 102200 "C" Side K Factor =09900 "D" Side K Factor =10000 Testing Reports: "A" Side = 694.29 ltr "B" Side = 132.97 ltr "C" Side = 150.84 ltr "D" Side = 140.42 ltr Total testing = 1118.52 ltr - B and C nozzle teeth replaced - C side keypad changed - Tank area unloading liquid line ballvalve LPG leakage arrested by tightening the nut - Completed
CL4185 | 2024-02-17 | Cantonment | C | Unloading Tank 1 Vapour line ball valve LPG leakage | Breakdown | Chandrasekar | 2024-02-17 | - | Ballvalve LPG leakage arrested by tightening the nut - C nozzle leakage arrested by replacing the hammer teeth - Resolved
CL4186 | 2024-02-17 | T.V.Kovil | A | D side POS machine device testing | Breakdown | Vigneshwaran | 2024-02-17 | - | Point of sales billing device tested - Attended
CL4187 | 2024-02-17 | Krishnagiri | R | Control panel DPS issue due to low air pressure | Breakdown | Prabu | 2024-02-17 | - | Turbo drive reset done - Air compressor pressure adjusted and starter restarted - Total leakage test done - PMR done - Completed
CL4188 | 2024-02-18 | Kumbakonam | G | B phase surge arrester failure due to EB surge | Breakdown | Pandi Durai | 2024-02-18 | - | Surge arrester replaced for B phase - RYB phase indicators replaced in both control panel and DB panel - Unloading vapour line ROV air leakage arrested by tightening the stem - Working properly - PMR done - Rectified
CL4189 | 2024-02-18 | Bhavani | G | Unloading training | Breakdown | Avinash | 2024-02-18 | - | Unloading done and unloading training provided to pump staffs - Attended
CL4190 | 2024-02-19 | Villapuram | D | C nozzle center mount and NRV O ring defect | Breakdown | Kathiresan | 2024-02-19 | - | New nozzle replaced at B side - Testing : 0.84 L - Resolved
CL4191 | 2024-02-19 | T.V.Kovil | A | C side POS machine device testing | Breakdown | Vigneshwaran | 2024-02-19 | - | Point of sales billing device tested - Attended
CL4192 | 2024-02-19 | T.V.Kovil | A | B side POS machine device testing | Breakdown | Vigneshwaran | 2024-02-19 | - | Point of sales billing device tested - Attended
CL4193 | 2024-02-20 | Ellis Nagar | T | Unloading Vapour Line Steam LPG leakage and Tank 2 Dispensing Solenoid valve defect | Breakdown | Kathiresan | 2024-02-20 | - | Unloading Vapour Line Steam LPG leakage arrested by tighening the nut and Tank 2 Dispensing Solenoid valve serviced - PMR done - Rectified
CL4194 | 2024-02-20 | T.V.Kovil | A | B and C sides POS machine device testing | Breakdown | Vigneshwaran | 2024-02-19 | - | Point of sales billing device tested - Attended
CL4195 | 2024-02-20 | Namakkal 1 | D | A nozzle leakage | Breakdown | Nivas | 2024-02-20 | - | Nozzle serviced - Working properly - Testing : 0.80 L - Resolved
CL4196 | 2024-02-21 | T.V.Kovil | D | Batchen dispenser A nozzle leakage | Breakdown | Vigneshwaran | 2024-02-21 | - | Spare nozzle replaced - Testing : 1.24 L - Rectified
CL4197 | 2024-02-21 | Karur | D | Batchen dispenser B nozzle high flow is not working | Breakdown | Thirumalaisamy | 2024-02-21 | - | Batchen dispenser power card failure - A nozzle working properly - Attended
CL4198 | 2024-02-22 | Manapparai | C | Calibration and stamping work | Certification | Nepolean and Pandidurai | 2024-02-22 | - | Calibration and stamping work done Calibration reports: "A" Side 10 ltrs = 9.99 ltr "B" Side 10 ltrs = 10.01 ltr K" Factor Reports: Both side K Factor No changed "A" Side K Factor = 10280 "B" Side K Factor = 10190 Testing Reports: "A" Side = 156.21ltr "B" Side = 187.07 ltr Total testing = 343.28 ltr CP reference failure and new 1 No changed.Before reading : C1R1 =-594 DCV C2R1 =-594 DCV A1R1 =-650 DCV A2R1 =-1.245 DCV A3R1 =-1.285 DCV A4R1 =-1.002 DCV After reading : C1R1 =-1.184 DCV C2R1 =-1.184 DCV Control panel R,Y,B, control on and tank-1 indicator light 5 No changed - Offline ups back up issue 12V 7AH battery 1 No replaced - Completed
CL4199 | 2024-02-23 | Cantonment | D | B side on/off switch fell off | Breakdown | Kathiresan | 2024-02-23 | - | On/Off switch refixed and working fine - Testing : 0.73 L - Rectified
CL4200 | 2024-02-24 | T.V.Kovil | D | D nozzle not working properly | Breakdown | Nepolean | 2024-02-24 | - | New nozzle replaced - Testing D side : 1.03 L - Resolved
CL4201 | 2024-02-25 | Perambalur | A | CPU heating issue | Breakdown | Pandi Durai | 2024-02-26 | - | CPU maintenance and cleaning done - Kept under observation - Attended
CL4202 | 2024-02-27 | Vedachandur | T | Dispensing pump servicing | Breakdown | Nepolean and Pandidurai | 2024-02-28 | - | Dispensing pump serviced and fitted - No leakage found - No vibration - Working properly - Kept under observation for two days - Completed
CL4203 | 2024-02-28 | Bhavani | D | B and D nozzle leakage | Breakdown | Avinash | 2024-02-28 | - | B and D nozzle cleaned and serviced - A nozzle teeth replaced - PMR done - Unloading training provided to pump staffs - Working fine - Resolved
CL4204 | 2024-02-28 | Ammapet | G | Preventive maintenance | Preventive | Avinash | 2024-02-28 | - | Compressor oil changed - PMR done - Automation maintenance done - Completed
CL4205 | 2024-02-28 | Cantonment | A | Automation tank cut off program testing | Development | Chandrasekar | 2024-02-28 | - | Automation tank cut off program testing done - E.Testing -16.49 L F.Testing - 22.10 L Total - 38.59 L - Completed
CL4206 | 2024-02-29 | Ellis Nagar | G | N2 machine nozzle defect | Breakdown | Kathiresan | 2024-02-29 | - | Nitrogen machine nozzle replaced - Oil dispenser measurements and calibration checked - Working properly - Oil testing : 4.50 L - Rectified
CL4207 | 2024-02-29 | Cantonment | A | Automation tank cut off program testing | Development | Chandrasekar | 2024-02-29 | - | Automation tank cut off program testing done - F.Testing - 6.37 L - Completed
CL4208 | 2024-03-02 | Ammapet | A | Dispenser A and B side totalizer reverse due to EB supply fluctuation | Breakdown | Avinash | 2024-03-02 | - | Reverse reading noted - Authorized to dispense at the back end - Resolved
CL4209 | 2024-03-02 | Ammapet | A | Earth regeneration | Breakdown | Avinash | 2024-03-02 | - | Earth generated - Kept under observation - Earth value - 0.9 V - Attended
CL4210 | 2024-03-02 | Cantonment | A | Automation tank cut off program testing | Development | Chandrasekar | 2024-03-02 | - | Automation tank cut off program testing done - F.Testing - 7.99 L - Completed
CL4211 | 2024-03-02 | T.V.Kovil | D | B nozzle leakage | Breakdown | Vigneshwaran | 2024-03-02 | - | B nozzle hammer teeth replaced with new - Leakage arrested - Rectified
CL4212 | 2024-03-03 | Tenkasi | D | Error 34 occurred in dispenser | Breakdown | Kathiresan | 2024-03-03 | 11 Hours | Dispenser temperature sensor probe reassembled - Wiring resoldering done - Dispenser working properly - Resolved
CL4213 | 2024-03-03 | Rasipuram | C | Rule 19 work | Certification | Nivas | 2024-03-05 | 39 Hours | Rule 19 work done - Rule 18 done - Sales started - Testing: A Side -5 lit. B Side -5 lit - Earth regenerated - All area leakage tested - All equipment working fine - Completed
CL4214 | 2024-03-04 | Mettupalayam | R | Voltage scanner failure | Breakdown | Gowtham | 2024-03-04 | - | RYB 5A fuses replaced - Voltage scanner disconnected - Rectified
CL4215 | 2024-03-04 | Bhavani | P | Unloading training | Preventive | Avinash | 2024-03-04 | - | Unloading training provided to pump staffs - A nozzle dispensing hose crimped as it is about to wear - Completed
CL4216 | 2024-03-04 | T.V.Kovil | C | Rule 19 work | Certification | Nepolean | 2024-03-05 | 26 Hours | Rule 19 work done - Sales started - Testing: A side: 12.58 lit B side : 5.00lit C side : 5.00 lit D side : 5.00 lit Total : 27.58 lit. All equipment working fine - Completed
CL4217 | 2024-03-05 | Perundurai | G | PMR work | Preventive | Avinash | 2024-03-05 | - | PMR work done - Tank area leak tested - A and B nozzles cleaned and serviced - New fire ball replaced due to expiration of the old one - Attended
CL4218 | 2024-03-06 | Udumalpet | D | LPG is dispensing when tank filling randomly | Breakdown | Gowtham | 2024-03-06 | - | LPG hoses cleaned and kept under observation - Attended
CL4219 | 2024-03-06 | Ellis Nagar | D | Nozzle replacement as a preventive measure | Preventive | Kathiresan | 2024-03-06 | - | D nozzle replaced as the nozzle is working over 150000 Litres - Working satisfactory - Completed
CL4220 | 2024-03-07 | Rasipuram | G | PMR work | Preventive | Nivas | 2024-03-07 | - | PMR work done - Total leakage checked - All equipment working fine - Resolved
CL4221 | 2024-03-08 | Thiruvaiyaru | C | DL stamping work | Certification | Nepolean and Vigneshwaran | 2024-03-08 | - | DL stamping done - A side : 110.31 lit B side : 12474. Total : 235.06 L - No changes in K factor -Attended
CL4222 | 2024-03-08 | Cantonment | A | Outlet going offline for POS app implementation | Development | Madhavan | 2024-03-08 | - | POS app implementated and tested - A side testing : 4.58 L - Completed
CL4223 | 2024-03-10 | Ariyamangalam | D | B side metering unit leakage | Breakdown | Nepolean | 2024-03-10 | - | Metering unit bearing and seal kit replaced - Leakage arrested - B side testing : 27.21 L - Rectified
CL4224 | 2024-03-11 | Kumbakonam | C | Stamping and calibration work | Certification | Pandi Durai and Vigneshwaran | 2024-03-11 | - | Calibration and Stamping Work done : Calibration reports: "A" Side 10 ltrs = 9.93 "B" Side 10 ltrs = 9.97 K" Factor Reports: "A" Side old K Factor = 10100 "A" Side new K Factor = 09850 "B" Side K Factor = 10100 Testing Reports: "A" Side = 609.55 ltr "B" Side = 250.18 ltr Total testing = 859.73 ltr - B nozzle teeth replaced - Completed
CL4225 | 2024-03-11 | Eral | R | Online UPS not working | Breakdown | Kathiresan | 2024-06-22 |  | Online UPS push button changed and working in good condition.
CL4226 | 2024-03-11 | Chengalpattu | G | PMR work | Certification | Suneel Sagar | 2024-03-11 | - | PMR done - Completed
CL4227 | 2024-03-11 | Saravanampatty | R | FRC unit defect | Breakdown | Avinash | 2024-03-12 | - | FRC unit replaced by new - Dispensing line pnuematic hose and conduit pipe replaced due to damage - Resolved
CL4228 | 2024-03-12 | Perambalur | R | 2 HP compressor motor winding defect and Servo stabilizer not working in servo mode due to 3 pole 63 amps MCB worn out | Breakdown | Pandi Durai | 2024-03-12 | - | 2 HP compressor motor rewinding done - Servo stabilizer MCB changed and it is working in servo mode - Oil changed for both compressors - Rectified
CL4229 | 2024-03-12 | Ariyamangalam | D | CD dispenser power card testing | Preventive | Nepolean | 2024-03-12 | - | Power card testing done - Testing : C side : 6 L - D side : 9.47 L - Total : 15.47 L - Attended
CL4230 | 2024-03-13 | Thanjavur | R | Offline UPS battery back up is low | Preventive | Pandi Durai | 2024-03-13 | - | 12V 7AH battery replaced with new - RYB indicator light replaced for control panel, DB panel and EB meter box - N2 compressor to Air machine air hose replaced to arrest the air leakage - Earth cable fixed for air machine - Completed
CL4231 | 2024-03-13 | Palayam | D | B nozzle LPG leakage | Breakdown | Thirumalaisamy | 2024-03-13 | - | Nozzle centre mount O ring replaced with new - Nozzle retraction rope changed for both sides - Working properly - Resolved
CL4232 | 2024-03-13 | T.V.Kovil | A | POS app implementation | Development | Madhavan | 2024-03-14 | - | Automation POS app installed and tested in both POS machine and Mobile - Dispenser back online - B side testing: 3 ltrs C side testing : 2 ltrs. D side testing: 1ltrs. Total Testing liter: 6 ltrs - Completed
CL4233 | 2024-03-14 | Perambalur | R | 2 HP compressor motor winding defect | Breakdown | Pandi Durai and Chandrasekar | 2024-03-16 | - | Motor coil rewinded - 63A conductor replaced and OLR relay 1 No replaced - Input R=422V, Y=422V, B=418V. Maximum amps = 3.1 - Working properly - Kept under observation - Resolved
CL4234 | 2024-03-14 | Bodi | A | Automation CPU heating issue | Breakdown | Kamaraj | 2024-03-14 | - | CPU fan defect - Outlet going offline - Totalizer readings A side - 144615.10 B side - 142491.33 - Attended
CL4235 | 2024-03-14 | Ariyamangalam | A | POS app implementation | Development | Nepolean | 2024-03-14 | - | Automation POS app installed and tested in both POS machine and Mobile - Dispenser back online - A side Testing : 1 L - Completed
CL4236 | 2024-03-14 | Karur | D | Batchen dispenser power card B nozzle high flow track defect | Breakdown | Thirumalaisamy | 2024-03-14 | - | Batchen dispenser power card B nozzle high flow track repaired - High flow is working fine - Resolved
CL4237 | 2024-03-15 | Bathlagundu | G | Fire extinguisher service work | Preventive | Kamaraj | 2024-03-15 | - | Fire extinguisher renewal and service work done - Training provided to pump staffs - Completed
CL4238 | 2024-03-15 | Cantonment | A | Loyalty program redeem | Development | Prakash | 2024-03-15 | - | Redeem Litre - 343.23 Amount Rs 21144.11 Total No. of Redeem vehicle 121. Auto - 119 Car - 2
CL4239 | 2024-03-16 | T.V.Kovil | A | Loyalty program redeem | Development | Prakash | 2024-03-16 | - | Redeem Litre - 265.64 Amount Rs 16336.86 Auto = 82 Auto litre =256.71 Auto Amount =15787.66 Car = 02 Car litre = 8.93 Car amount = 549.20
CL4240 | 2024-03-16 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-16 | - | Redeem Litre - 128.34 Amount Rs 7893/- Total No. of Redeem vehicle 44. Auto - 42 Car - 2
CL4241 | 2024-03-16 | Nasiyanur | G | Unloading and unloading training and IP camera installation | Preventive | Avinash | 2024-03-16 | - | Unloading done and unloading training provided to pump staffs - IP camera installed - Unloading, dispensing camera and NVR details shared with HO automation for security purpose - Attended
CL4242 | 2024-03-16 | Ammapet | G | IP camera installation | Preventive | Avinash | 2024-03-16 | - | IP camera installed - Unloading, dispensing camera and NVR details shared with HO automation for security purpose - Attended
CL4243 | 2024-03-16 | Bodi | A | CPU service | Preventive | Kamaraj | 2024-03-16 | - | Automation CPU serviced - Dispenser working online - Testing : 3.20 L - Completed
CL4244 | 2024-03-16 | Tirunelveli | A | Dispenser reading reverse due to EB supply fluctuation | Breakdown | Kathiresan | 2024-03-16 | - | Reverse reading noted - Authorized to dispense at the back end - Resolved
CL4245 | 2024-03-16 | Vadivelan Nagar | G | PMR work | Preventive | Suneel Sagar | 2024-03-16 | - | PMR work done - Attended
CL4246 | 2024-03-16 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-16 | - | Redeem lit : 50.56 lit Redeem amount : 3109.49 /- Total vehicle : 18 no Auto : 18 no Car : Nil - Completed
CL4247 | 2024-03-16 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-16 | - | Redeem litre = 69.99 Total Amount = 4312 Auto = 19 Auto litre =58.45 Auto Amount =3601 Car = 03 Car litre = 11.54 Car amount = 711 - Completed
CL4248 | 2024-03-17 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-17 | - | Redeem Litre.149.02 Amount Rs 9177.43 Total No's of Redeem vehicle -54 - Completed
CL4249 | 2024-03-17 | Sulur | D | A nozzle inner O ring damaged | Breakdown | Gowtham | 2024-03-17 | - | New nozzle replaced for a time - Tesintg : 0.89 L - Rectified
CL4250 | 2024-03-18 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-18 | - | Total Redeem vehicle no: 30 nos. 30 nos vehicle amount : 5950.00/- 30 nos vehicle lit: 96.77 Auto 28 no lit. 85.38 lit Auto 28 no : 5250.00/- Car - 2 no: 11.39 lit Car - 2 no : 700.00/- Completed
CL4251 | 2024-03-18 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-18 | - | Total liters-303.41 Total Amount -18684.00 Auto -87 Car -5 Total= 92 - Completed
CL4252 | 2024-03-18 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-18 | - | Redeem Litre.458.79 Amount Rs-28257.51 Total No's of Redeem vehicle -151 Auto-149 Car-2 - Completed
CL4253 | 2024-03-18 | Tharamangalam | D | A nozzle leakage | Breakdown | Prabu | 2024-03-18 | - | Nozzle serviced and teeth replaced - Leakage arrested - USB Convertor board checked and reconnected - Working fine - Resolved
CL4254 | 2024-03-18 | Vellakovil | A | CPU cooling fan caught with fire due to fan coil issue | Breakdown | Thirumalaisamy | 2024-03-18 | 10 Minutes | Office room emergency switch hit - UPS supply stopped - CO2 fire extinguisher used to control fire - Offline sales for 2.30 Hours - Working properly - Rectified
CL4255 | 2024-03-18 | Erode | C | PMR work | Preventive | Avinash | 2024-03-18 | - | PMR done - Attended
CL4256 | 2024-03-19 | Kumbakonam | G | Fire extinguisher service work | Preventive | Pandi Durai | 2024-03-19 | - | Fire extinguisher service and renewal work done - Attended
CL4257 | 2024-03-19 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-19 | - | Total Redeem vehicle : 42 nos Car : 1 no Auto : 41 nos. Total Redeem Bill (40): 112.69 lit Cash Bill (2) : 4.23 lit Total lit.: 116.92 Total amount : 7190.00Completed
CL4258 | 2024-03-19 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-19 | - | Redeem points Total liters-177.72 Total Amount -10948 Auto -54 Car -2 Total= 56 - Completed
CL4259 | 2024-03-19 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-19 | - | Redeem Litre.529.97 Amount Rs-32648.46 Total No's of Redeem vehicle -175 Auto-173 Car-2 Completed
CL4260 | 2024-03-19 | Thanjavur | D | A side point jumping and Fire extinguisher painting work | Breakdown | Pandi Durai | 2024-03-19 | - | DP valve spring adjusted to resolve the point jumping issue - Fire extinguisher painting work done - Tank area dispensing liquid and vapour line ROV air leakage arrested by tightening the stem - Day shift: "A" side testing = 24.55 Lit "B" side testing = 0.98 Lit Night shift: "A" side testing = 10.00 Lit Total testing = 35.53 Lit - PMR done - Rectified
CL4261 | 2024-03-20 | HO | G | Service engineer training and assessment program | Development | Prakash and Venkatesh | 2024-03-20 | - | Service engineer training and assessment program conducted - Completed
CL4262 | 2024-03-20 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-20 | - | Total Redeem vehicle no: 31 nos Car : 2 no Auto : 29 no Total : 31 nos Total Redeem vehicle Amount : 5620.00 Lit : 91.38 - Completed
CL4263 | 2024-03-20 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-20 | - | Redeem Litre.229.98 Amount Rs-14170.06 Total No's of Redeem vehicle -80 Auto-78 Car-2 Completed
CL4264 | 2024-03-21 | Mulanur | G | Fire extinguisher service and stamping work | Preventive | Thirumalaisamy | 2024-03-21 | - | Fire extinguisher service done - Stamping and calibration work done - "A" Side 10 ltrs= 10.03 "B" Side 10 ltrs= 10.05 "K" Factor Reports: "A" Side = 10000 "B" Side = 1000 "K" Factor no change Testing Reports; "A" Side = 179.59 ltrs. "B" Side = 120.12 ltrs. Total testing:299.71 ltrs- Attended
CL4265 | 2024-03-21 | Attur | A | Firewall issue and Batchen dispenser power card replacement | Breakdown | Nivas | 2024-03-21 | - | Spare firewall replaced - Batchen dispenser power removed and rerouted old power card replaced - Testing A side -14.61lit. B side -5 lit - Resolved
CL4266 | 2024-03-21 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-21 | - | Redeem points Total liters-292.65 Total Amount -18026.20 Auto - 98 Car -3 Total= 101 - Completed
CL4267 | 2024-03-21 | Ariyamangalam | D | Nozzle service and testing at C side | Preventive | Nepolean | 2024-03-21 | - | C nozzle service and testing done - Testing : 1.69 L - Attended
CL4268 | 2024-03-21 | Cantonment | D | F nozzle leakage | Breakdown | Chandrasekar | 2024-03-21 | - | Nozzle hammer teeth 4 Nos replaced - Working fine - Rectified
CL4269 | 2024-03-21 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-21 | - | Total Redeem vehicle : 30 Car : 3 nos Auto : 27 nos Total Redeem Amount Rs: 5570/- Total Redeem lit: 90.59 - Completed
CL4270 | 2024-03-21 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-21 | - | Total liters-241.20 Total Amount -14858 Auto -78 Car -3 Total= 81 - Completed
CL4271 | 2024-03-21 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-21 | - | Redeem Litre.294.22 Amount Rs-18126.00 Total No's of Redeem vehicle -101 Auto-100 Car-1 - Completed
CL4272 | 2024-03-22 | Ariyalur | T | Dispensing and unloading liquid line ROV defect | Breakdown | Pandi Durai | 2024-03-22 | - | Dispensing liquid line ROV serviced and fitted - Unloading liquid line ROV air leakage arrested by tightening the stem - Unloading ROV solenoid coil cleaned and refitted to remove the rust - Both A and B keypads cables reconnected to avoid the loose connections - PMR done - Outlet working fine - Completed
CL4273 | 2024-03-22 | Bhavani | R | Panel booting problem due to surge protector failure caused by EB voltage fluctuations | Breakdown | Avinash | 2024-03-22 | 30 Mins | New surge protector replaced - Panel booting working properly - Resolved
CL4274 | 2024-03-22 | Neelambur | A | Automation internal server issue due to Firewall power adapter failure | Breakdown | Gowtham | 2024-03-22 | - | New firewall power adapter provided and working fine - Compressor pressure switch adjusted and reassembled for cutoff at high level - Rectified
CL4275 | 2024-03-22 | Uthamasolapuram | G | Outlet running in DG mode due to EB main MBC coil burnt | Breakdown | Prabu | 2024-03-22 | - | 63A 4 Pole MCB replaced with new - Outlet running in EB mode after an hour - Attended
CL4276 | 2024-03-22 | Melur | R | Online UPS 12V battery back up problem | Breakdown | Kathiresan | 2024-03-22 | - | Online UPS 12V battery 7AH battery replaced with new - Back up is now up to 10 Mins - Working properly - Rectified
CL4277 | 2024-03-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-22 | - | Redeem Litre.150.97 Amount Rs-9301 Total No's of Redeem vehicle -58 Auto-58 Car-0 - Completed
CL4278 | 2024-03-22 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-22 | - | Total Redeem vehicle : 15 Total Redeem Amount : 2882.70 Total Redeem Lit: 46.87- Completed
CL4279 | 2024-03-22 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-22 | - | Total liters-153.25 Total Amount -9439 Auto -44 Car -7 Total= 51 - Completed
CL4280 | 2024-03-23 | Karur | C | Dispenser calibration and stamping work | Certification | Thirumalaisamy | 2024-03-23 | - | Calibration and stamping done - Calibration Report : "A" Side 10 ltrs = 10.02 "B" Side 10 ltrs = 10.05 "C" Side 10 ltrs = 9.99 "D" Side 10 ltrs = 9.98 "K" Factor Report : " A " Side old K factor = 101500 " A " Side new K factor=101500 " B " Side old K factor = 101800 " B " Side new K factor =101800 " C " Side old K factor = 10180 " C " Side new K factor=10100 " D " Side old K factor = 10180 " D " Side new K factor =10050 Testing Report ; "A" Side = 136.73 "B" Side = 207.48 "C" Side = 292.40 "D" Side = 366.13 Total = 1002.74 - Completed
CL4281 | 2024-03-23 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-23 | - | Redeem Litre-133.92 Amount Rs-8255.48 Total No's of Redeem vehicle -48 Auto-46 Car-2 - Completed
CL4282 | 2024-03-23 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-23 | - | Total Redeem vehicle : 9 Car : no Auto : 9 no Total Redeem Amount: 1940.00/- Total Redeem Lit: 31.54- Completed
CL4283 | 2024-03-23 | T.V.Kovil | G | Yenen dispenser keypads testing | Preventive | Nepolean | 2024-03-23 | - | 26 Nos of yenen dispenser keypads tested - Completed
CL4284 | 2024-03-23 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-23 | - | Total liters-135.71 Total Amount -8361.27 Auto -46 Car -1 Total= 47- Completed
CL4285 | 2024-03-24 | Thuraiyur | G | Fire extinguisher service work | Preventive | Nivas | 2024-03-24 | - | Fire extinguisher service work done - 9 kg DCP extinguisher replaced with ABC type - Attended
CL4286 | 2024-03-25 | Cantonment | D | D nozzle leakage | Breakdown | Chandrasekar | 2024-03-25 | - | D nozzle hammer teeth 4 Nos replaced - working fine - Resolved
CL4287 | 2024-03-25 | Villapuram | T | Dispensing motor noise due to love joy coupling spider defect | Breakdown | Kathiresan | 2024-03-25 | - | Love joy coupling spider replaced to arrest the noise - Motor and pump alignment checked - Rectified
CL4288 | 2024-03-25 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-25 | - | Total liters-151.43 Total Amount -9327 Auto -44 Car -7 Total= 51- Completed
CL4289 | 2024-03-25 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-25 | - | Total liters-53.64 Total Amount -3300.00 Total vehicle -20 Auto -19 Car -1 - Completed
CL4290 | 2024-03-25 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-25 | - | Redeem Litre-105.82 Amount Rs-6521.00 Total No's of Redeem vehicle -42 Auto-40 Car-2 - Completed
CL4291 | 2024-03-25 | Kodumudi | R | Air leakage due to air fittings damaged | Breakdown | Thirumalaisamy | 2024-03-25 | - | 1/2" to 6mm air fitting replaced - SOP and safety unloading procedure faded board replaced - Automation equipment maintenance done - Resolved
CL4292 | 2024-03-26 | Ellis Nagar | R | Servo stabilizer B phase carbon winding bush defect | Breakdown | Kathiresan | 2024-03-26 | - | Servo stabilizer B phase carbon winding bush replaced - Working properly - Rectified
CL4293 | 2024-03-26 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-26 | - | Total liters-100.9 Total Amount -6216 Auto -33 Car -1 Total= 34- Completed
CL4294 | 2024-03-26 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-26 | - | Total Redeem vehicle : 13 nos. Car : 02 no Auto: 11 no Total Redeem Lit: 42.44 Total Redeem Amount : 2610.00/- Completed
CL4295 | 2024-03-26 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-26 | - | Amount Rs-5901.00 Total No's of Redeem vehicle -40 Auto-40 Car-0 - Completed
CL4296 | 2024-03-27 | Saravanampatty | T | Dispensing line vapour ROV replacement | Breakdown | Gowtham | 2024-03-28 | - | Dispensing line vapour ROV - 1 1/2" replaced - Resolved
CL4297 | 2024-03-27 | Bodi | A | Automation system CPU cooling fan issue | Breakdown | Kamaraj | 2024-03-27 | - | Spare CPU replaced - PMR done - Attended
CL4298 | 2024-03-27 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-27 | - | Total liters-76.43 Total Amount -4708 Auto -23 Car -3 Total= 26 - Completed
CL4299 | 2024-03-27 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-27 | - | Total liters : 33.25 Total Amount : 2044.30 Auto -7 Car -1 Total= 8 - Completed
CL4300 | 2024-03-27 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-27 | - | Redeem Litre-95.87 Amount Rs-5907.00 Total No's of Redeem vehicle -36 Auto-35 Car-1 - Completed
CL4301 | 2024-03-27 | Krishnagiri | G | Fencing area grill gate installation | Preventive | Prabu | 2024-03-27 | - | Fencing area grill gate installed - Attended
CL4302 | 2024-03-27 | T.V.Kovil | G | PMR work | Preventive | Vigneshwaran | 2024-03-27 | - | PMR work done - Completed
CL4303 | 2024-03-28 | Sulur | D | Dispenser A nozzle dispensing hose leakage | Breakdown | Gowtham | 2024-03-28 | - | Dispenser A nozzle dispensing hose replaced with new - Resolved
CL4304 | 2024-03-28 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-28 | - | Total Redeem Lit: 56.84 Total Amount : 3495.70 Total vehicle : 21 no Car :3 no Auto: 18 no - Completed
CL4305 | 2024-03-28 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-28 | - | Redeem Litre-105.90 Amount Rs-6526.77 Total No's of Redeem vehicle -40 Auto-39 Car-1 - Completed
CL4306 | 2024-03-28 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-28 | - | Total liters-65.14 Total Amount -4013.00 Auto -20 Car -2 Total= 22 - Completed
CL4307 | 2024-03-28 | Namakkal 2 | D | B side DP valve diaphragm punctured | Breakdown | Nivas | 2024-03-28 | - | New diaphragm replaced - Working properly - Rectified
CL4308 | 2024-03-29 | Kattupakkam | D | PMR work | Preventive | Suneel Sagar | 2024-03-29 | - | PMR work done - Completed
CL4309 | 2024-03-29 | Avadi | D | PMR work | Preventive | Suneel Sagar | 2024-03-29 | - | PMR work done - Completed
CL4310 | 2024-03-29 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-29 | - | Total liters-42.13 Total Amount -2595.00 Auto -12 Car -1 Total= 13 - Completed
CL4311 | 2024-03-29 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-29 | - | Redeem Litre-80.46 Amount Rs-4957.00 Total No's of Redeem vehicle -31 Auto-30 Car-1 - Completed
CL4312 | 2024-03-29 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-29 | - | Total liters -23.58 Total Amount -1450.00 Auto -5 Car -2 Total =7 - Completed
CL4313 | 2024-03-30 | Devakottai | G | Fire extinguisher service | Preventive | Nepolean | 2024-03-30 | - | Fire extinguisher service and renewal work done - PMR done - Fire safety training provided - Attended
CL4314 | 2024-03-30 | Tiruchengode | R | N2 machine air compressor oil leakage due to air return | Breakdown | Avinash | 2024-03-30 | - | NRV removed, adjusted and refitted - Oil leakage arrested - Kept under observation - Rectified
CL4315 | 2024-03-30 | Namakkal 3 | G | PMR work | Preventive | Nivas | 2024-03-30 | - | PMR work done - Completed
CL4316 | 2024-03-30 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-03-30 | - | Redeem Litre-85.92 Amount Rs-5292.43 Total No's of Redeem vehicle -30 Auto-29 Car-1 - Completed
CL4317 | 2024-03-30 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-03-30 | - | Total liters-8.94 Total Amount -550.00 Total vehicle -3 Auto -2 Car -1- Completed
CL4318 | 2024-03-30 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-03-30 | - | Total liters-34.09 Total Amount -2101.00 Auto -12 Car -1 Total= 13 - Completed
CL4319 | 2024-03-30 | Pudukkottai | R | Online UPS battery voltage drop | Breakdown | Pandi Durai | 2024-03-30 | - | Online UPS battery 3 nos replaced - Offline UPS battery 1 No replaced - UPS air and dry cleaned - Automation maintenance done - Working properly - Resolved
CL4320 | 2024-03-31 | Ayothiyapattinam | G | N2 machine keypad defect | Breakdown | Prabu | 2024-03-31 | - | New keypad replaced - Solenoid valve cleaned - Automation maintenance and EB maintenance done - Working fine - Rectified
CL4321 | 2024-04-01 | Ammapet | A | Billing mobile defect | Breakdown | Avinash | 2024-04-01 | - | Spare mobile replaced - Billing started with mobiles - Resolved
CL4322 | 2024-04-01 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-01 | - | Redeem Litre-41.72 Amount Rs-2530.00 Total No's of Redeem vehicle -17 Auto-16 Car-1 - Completed
CL4323 | 2024-04-01 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-01 | - | Total liters-18.02 Total Amount -1090.70 Total vehicle -6 Auto -5 Car -1 Completed
CL4324 | 2024-04-01 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-01 | - | Total liters-16.44 Total Amount -999 Auto -5 Car -0 Total= 5 - Completed
CL4325 | 2024-04-02 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-02 | - | Redeem Litre-48.87 Amount Rs-2963.00 Total No's of Redeem vehicle -18 Auto-16 Car-2 - Completed
CL4326 | 2024-04-02 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-02 | - | Total liters-12.59 Total Amount -763 Auto -2 Car -2 Total= 4 - Completed
CL4327 | 2024-04-02 | Sangagiri | G | 9 kg extinguisher pressure dropped | Preventive | Avinash | 2024-04-02 | - | ABC 9 kg extinguisher replaced with new - Fire safety training provided to pump staffs - Attended
CL4328 | 2024-04-02 | Ammapet | G | 2 kg CO2 in 75 Kg ABC fire extinguisher pressure dropped | Preventive | Avinash | 2024-04-02 | - | Spare 2 kg CO2 replaced - Fire safety training provided to pump staffs - Resolved
CL4329 | 2024-04-02 | Bhavani | G | 9 kg DCP extinguisher replacement | Preventive | Avinash | 2024-04-02 | - | 9 kg DCP extinguisher replaced by ABC type extinguisher - Fire safety training provided to pump staffs - Attended
CL4330 | 2024-04-02 | Perundurai | G | 2 kg CO2 extinguisher hose damaged | Preventive | Avinash | 2024-04-02 | - | 2 kg CO2 extinguisher new hose replaced - 9 kg DCP extinguisher replaced by ABC type extinguisher - Fire safety training provided to pump staffs - Attended
CL4331 | 2024-04-02 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-02 | - | Total redeem lit: 20.82 Total redeem Amount : 1260/-. Total vehicle : 06 Auto: 06 Car : no - Completed
CL4332 | 2024-04-03 | Omalur | A | Dispenser going offline due to shift closing error | Breakdown | Prabu | 2024-04-03 | - | Night shift closed properly - Dispenser back online - Spare online UPS installed due to the error 62 occurred - Completed
CL4333 | 2024-04-03 | Bodi | R | Online UPS battery back up issue | Breakdown | Kamaraj | 2024-04-03 | - | 12V 7ah battery replaced with new - Working properly - Resolved
CL4334 | 2024-04-03 | Cantonment | D | E nozzle leakage | Breakdown | Chandrasekar | 2024-04-03 | - | Hammer teeth replaced - Leakage arrested - Rectified
CL4335 | 2024-04-03 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-03 | - | Redeem Litre-32.30 Amount Rs-1958.00 Total No's of Redeem vehicle -9 Auto-6 Car-3 - Completed
CL4336 | 2024-04-03 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-03 | - | Redeem points Total liters-22.32 Total Amount -1354 Auto -7 Car -0 Total= 7 - Completed
CL4337 | 2024-04-03 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-03 | - | F2 station redeem lit: 4.13. Total redeem Amount : 250/- Total vehicle : 2 no Car : no Auto : 2 no - Completed
CL4338 | 2024-04-03 | Vellakovil | R | Online UPS battery back up issue | Breakdown | Thirumalaisamy | 2024-04-03 | - | 12V 26ah battery replaced with new - Working properly - Resolved
CL4339 | 2024-04-03 | Mulanur | A | Automation mobile app working not properly | Breakdown | Thirumalaisamy | 2024-04-03 | - | New mobile software installed and logged in - Working fine - Attended
CL4340 | 2024-04-04 | Cantonment | D | New nozzle replacement at E and F nozzle | Preventive | Chandrasekar | 2024-04-04 | - | New nozzle replaced - E.side reading.848934.48 F.side reading.783282.58 E.testing.0.92 litre F.testing.0.88 litre - Completed
CL4341 | 2024-04-04 | Ellis Nagar | D | C nozzle leakage | Breakdown | Kathiresan | 2024-04-04 | - | Hammer teeth replaced - Leakage arrested - ontrol Panel Isolator Transformer ''220' v Holder Jack replaced with new - Rectified
CL4342 | 2024-04-04 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-04 | - | Total Redeem lit: 15.58 Total amount : 943.90. Total vehicle : 7 no Car : 1 no Auto: 6 no - Completed
CL4343 | 2024-04-04 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-04 | - | Redeem Litre-32.37 Amount Rs-1964.26 Total No's of Redeem vehicle -14 Auto-14 Car-0 - Completed
CL4344 | 2024-04-04 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-04 | - | Total liters-28.19 Total Amount -1709.72 Auto -6 Car -2 Total= 8- Completed
CL4345 | 2024-04-05 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-05 | - | Total lit: 27.28 Total Redeem amount : 1650/- Total vehicle : 15 no Car :no Auto: 15 - Completed
CL4346 | 2024-04-05 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-05 | - | Total liters-55.08 Total Amount -3342 Auto -15 Car -5 Total= 20 - Completed
CL4347 | 2024-04-05 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-05 | - | Redeem Litre-63.40 Amount Rs-3847.72 Total No's of Redeem vehicle -30 Auto-28 Car-2 - Completed
CL4348 | 2024-04-06 | Rasipuram | G | ALDS is not working in EB mode due to changeover defect | Breakdown | Nivas | 2024-04-06 | 30 Mins | New change over replaced - Outlet running in EB mode - Resolved
CL4349 | 2024-04-06 | Pudukkottai | G | Rule 19 material requirement | Preventive | Pandi Durai | 2024-04-06 | - | Rule 19 material requirement data collected - Attended
CL4350 | 2024-04-06 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-06 | - | Total redeem vehicle : 3 no Car :1 no Auto : 2 no Total redeem lit: 7.44 Total amount : 450/- Completed
CL4351 | 2024-04-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-06 | - | Redeem Litre-54.49 Amount Rs-3306.00 Total No's of Redeem vehicle -22 Auto-20 Car-2 - Completed
CL4352 | 2024-04-06 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-06 | - | Total liters-50.79 Total Amount -3084.00 Auto -22 Car -2 Total= 24 - Completed
CL4353 | 2024-04-08 | Pudukkottai | T | Dispensing motor bed marking | Development | Nepolean, Prakash and Sekar | 2024-04-08 | - | Motor bed marking done - Attended
CL4354 | 2024-04-08 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-08 | - | Total liters-25.68 Total Amount -1557.00 Auto -7 Car -3 Total= 10 - Completed
CL4355 | 2024-04-08 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-08 | - | Total redeem lit: 8.27. Total amount : 500/- Total vehicle : 3 no Car : 1 no Auto : 2 no - Completed
CL4356 | 2024-04-08 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-08 | - | Redeem Litre-31.93 Amount Rs-1938.00 Total No's of Redeem vehicle -14 Auto-14 Car-0 - Completed
CL4357 | 2024-04-09 | Madurai - Sivagangai Road | G | Site visit | New Project | Prakash and Vigneshwaran | 2024-04-09 | - | Site visit done - Completed
CL4358 | 2024-04-09 | Pudukkottai | C | Rule 19 work started and sales stopped | Certification | Nepolean | 2024-04-11 | 36 Hours | Rule 19 work completed - Pipeline work completed - All equipment working fine - Sales started - Total area leakage checked - All equipments working in good condition - Completed
CL4359 | 2024-04-09 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-09 | - | Total liters-26.69 Total Amount -1619.00 Auto -9 Car -4 Total - 13 - Completed
CL4360 | 2024-04-09 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-09 | - | Redeem Litre-14.11 Amount Rs-856.00 Total No's of Redeem vehicle -6 Auto-5 Car-1- Completed
CL4361 | 2024-04-09 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-04-09 | - | Total liters-10.73 Total Amount -650.00 Auto -4 Car -0 Total - 4 - Completed
CL4362 | 2024-04-10 | Saravanampatty | C | PMR work | Preventive | Gowtham | 2024-04-10 | - | PMR done - Unloading vapour line ROV replaced with new - Compressor oil changed - A side dispensing hose crimping work done - Panel RYB indicators replaced - Testing : 0.82 Ltr - Attended
CL4363 | 2024-04-10 | Bathlagundu | C | Calibration and stamping work | Certification | Kamaraj | 2024-04-10 | - | Calibration and stamping work done -Calibration Report : "A" Side 10 ltrs = 9.96 "B" Side 10 ltrs = 9.97 "K" Factor Report : " A " Side old K factor = 10050 " A " Side new K factor=10050 " B " Side old K factor = 10050 " B " Side new K factor =10050 Testing Report ; "A" Side = 124.53 "B" Side = 120.11 Total testing = 244.64 - Completed
CL4364 | 2024-04-10 | T.V.Kovil | R | Air leakage due to dispensing solenoid valve defect | Breakdown | Vigneshwaran | 2024-04-10 | - | Dispensing solenoid valve replaced - Air leakage arrested - Resolved
CL4365 | 2024-04-10 | Bhavani | G | Unloading view camera outer junction box and view adjustable screw has been damaged | Breakdown | Avinash | 2024-04-10 | - | Camera fixed temporarily for unloading view - Rectified
CL4366 | 2024-04-10 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-10 | - | Total liters-26.04 Total Amount -1580.00 Auto -9 Car -2 Total - 11- Completed
CL4367 | 2024-04-10 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-04-10 | - | Total liters-11.58 Total Amount -700.90 Total vehicle -4 Auto -4 Car -0 Total= 4 - Completed
CL4368 | 2024-04-10 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-10 | - | Redeem Litre-30.73 Amount Rs-1864.00 Total No's of Redeem vehicle -14 Auto-14 Car - 0 - Completed
CL4369 | 2024-04-11 | Ammapet | R | Panel booting problem due to VSC contactor failure | Breakdown | Avinash | 2024-04-11 | - | Tank 2 contactor interchanged - Panel booting done - Working properly - Resolved
CL4370 | 2024-04-11 | Paramathivelur | D | B nozzle leakage due to center mount O ring damaged | Breakdown | Thirumalaisamy | 2024-04-11 | - | B nozzle leakage due to center mount O ring replaced - Leakage arrested - Rectified
CL4371 | 2024-04-11 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-11 | - | Total liters-9.94 Total Amount -603.00 Auto -4 Car -1 Total - 5 - Completed
CL4372 | 2024-04-11 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-11 | - | Redeem Litre-15.55 Amount Rs-943.00 Total No's of Redeem vehicle -5 Auto-4 Car-1 - Completed
CL4373 | 2024-04-12 | Namakkal 1 | R | Control panel booting error due to R phase surge protector failure | Breakdown | Nivas | 2024-04-12 | - | Surge protector looped - Rectified temporarily
CL4374 | 2024-04-12 | Pudukkottai | G | Unloading and PMR work | Preventive | Pandi Durai | 2024-04-12 | - | Unloading done - PMR done - Total area leakage checked - Attended
CL4375 | 2024-04-12 | Vadivelan Nagar | D | B side DP valve defect | Breakdown | Suneel Sagar | 2024-04-12 | - | Differential pressure valve replaced by new one - All 4 nozzles are in operation - Attended
CL4376 | 2024-04-12 | Ellis Nagar | G | General outlet visit | Preventive | Kathiresan | 2024-04-12 | - | Oil dispenser dispensing quantity tested - Testing : 6.4 L - Checked
CL4377 | 2024-04-12 | Villapuram | D | Dispenser C side on/off switch defect | Breakdown | Kathiresan | 2024-04-12 | - | NO element changed - On/off switch changed - Working properly - Completed
CL4378 | 2024-04-12 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-12 | - | Redeem Litre-16.69 Amount Rs-1013.00 Total No's of Redeem vehicle -8 Auto-7 Car-1 - Completed
CL4379 | 2024-04-12 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-12 | - | Total liters-8.75 Total Amount -531.00 Auto -3 Car -1 Total - 4 - Completed
CL4380 | 2024-04-13 | Perundurai | R | Online UPS battery failure | Breakdown | Avinash | 2024-04-13 | - | 12V 7ah batteries 3 Nos replaced - Online UPS working fine - Resolved
CL4381 | 2024-04-13 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-04-13 | - | Total liters-8.73 Total Amount -530.00 Auto -2 Car -1 Total - 3 - Completed
CL4382 | 2024-04-13 | T.V.Kovil | D | Batchen dispenser A nozzle dispensing hose damaged | Breakdown | Vigneshwaran | 2024-04-13 | - | New 5m dispensing hose replaced - Testing : 1.12 L - Rectified
CL4383 | 2024-04-13 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-04-13 | - | Total liters -2.98 Total Amount -180.00 Auto -2 Car -0 Total - 2 - Completed
CL4384 | 2024-04-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-13 | - | Redeem Litre-5.78 Amount Rs-351.00 Total No's of Redeem vehicle -3 Auto-3 Car-0 - Completed
CL4385 | 2024-04-13 | Hosur | G | Outlet running in DG mode due to EB phase 1 problem | Breakdown | Prabu | 2024-04-13 | - | EB line clear - Working in EB mode - Attended
CL4386 | 2024-04-15 | Devakottai | C | DL stamping work | Certification | Nepolean and Vigneshwaran | 2024-04-15 | - | DL stamping done - Calibration report : K factor : old A side : 10000 B side : 10000 K factor : new A side: 10000 B side: 10000 Both side k factor no changes. A side 10 lit : 10.05 lit B side 10 lit: 10.02 lit Testing : A side: 258.76 B side: 280.51 Total : 539.27 lit - Bore motor MCB replaced with new - Completed
CL4387 | 2024-04-15 | Paramathivelur | C | Rule 19 work and additional dispenser provision welding | Certification | Chandrasekar and Suresh Kumar | 2024-04-17 | 36 Hours | Rule 19 work done - Additional dispenser pipeline welding work done - Total area leakage checked - Dispensing and decanting motor shed work done - Completed
CL4388 | 2024-04-15 | Villapuram | G | Sales stopped due to Meenakshi Amman Kovil Utsavam | Preventive | Kathiresan | 2024-04-15 | 9.15 am to 10.45 am (1.30 hours) 5 pm to 7.10 pm (2 hours) | Sales started - Attended
CL4389 | 2024-04-15 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-15 | - | Redeem Litre-9.75 Amount Rs-592.00 Total No's of Redeem vehicle -5 Auto-5 Car-0 - Completed
CL4390 | 2024-04-15 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-04-15 | - | Total liters -9.41 Total Amount -570.00 Auto -3 Car -0 Total - 3 - Completed
CL4391 | 2024-04-16 | Pudukkottai | T | Tank area painting work | Preventive | Pandi Durai | 2024-04-16 | - | Tank area painting work done - Total area leakage done - All equipment working properly - Completed
CL4392 | 2024-04-16 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-16 | - | Redeem Litre-6.48 Amount Rs-393.00 Total No's of Redeem vehicle -2 Auto-2 Car - 0 - Completed
CL4393 | 2024-04-17 | Musiri | C | Stamping work | Certification | Nivas | 2024-04-17 | - | Calibration and stamping work done -Calibration reports ; "A" Side 10 ltrs=9.97 "B" Side 10 ltrs= 9.94 New "K" Factor Reports: "A" Side = 10100 "B" Side = 10100 Old "K" Factor : "A" Side = 10200 "B" Side = 10200 Testing Reports; "A" Side = 267.83 ltrs "B" Side = 419.29 ltrs - Completed
CL4394 | 2024-04-17 | Kangeyam | G | General outlet visit | Preventive | Gowtham | 2024-04-17 | - | Retrofitment work, material requirement for Rule 19 prepared - Completed
CL4395 | 2024-04-17 | Thuraiyur | C | Stamping work | Certification | Nivas | 2024-04-17 | - | Calibration and stamping work done -Calibration reports : "A" Side 10 ltrs=9.99 "B" Side 10 ltrs= 9.96 New "K" Factor Reports: "A" Side = 101600 "B" Side = 100000 Old "K" Factor : "A" Side =101600 "B" Side = 100000 Testing Reports; "A" Side = 131.34 ltrs "B" Side = 116.35 ltrs - Completed
CL4396 | 2024-04-17 | Ariyamangalam | D | Nozzle service and testing at D side | Preventive | Nepolean | 2024-04-17 | - | Nozzle teeth and lock set replaced - Working fine - Testing D side : 1.51 L - Attended
CL4397 | 2024-04-17 | T.V.Kovil | D | A side metering unit problem | Breakdown | Nepolean | 2024-04-17 | - | A side testing : 20.59 L - Resolved
CL4398 | 2024-04-17 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-17 | - | Redeem Litre-11.63 Amount Rs-706.00 Total No's of Redeem vehicle -5 Auto-4 Car - 1 - Completed
CL4399 | 2024-04-18 | Ellis Nagar | D | D side DP valve diaphragm punctured | Breakdown | Kathiresan | 2024-04-18 | - | Diaphragm replaced - Working properly - A nozzle replaced with new one as it is running more than 900000 Ltrs - Attended
CL4400 | 2024-04-18 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-18 | - | Redeem Litre-2.18 Amount Rs-132.00 Total No's of Redeem vehicle -1 Auto-1 Car-0 - Completed
CL4401 | 2024-04-18 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-04-18 | - | Total lit: 1.65 Total amount : 100/- Auto: 1 no Total vehicle : 1 no - Completed
CL4402 | 2024-04-18 | Namakkal 2 | D | B nozzle leakage | Breakdown | Nivas | 2024-04-18 | - | Nozzle teeth 4 Nos replaced - Leakage arrested - Rectified
CL4403 | 2024-04-19 | Paramathivelur | G | Unloading and unloading training | Preventive | Thirumalaisamy | 2024-04-19 | - | Unloading done - Unloading training provided - Attended
CL4404 | 2024-04-20 | Theni | D | Batchen dispenser A side display defect | Breakdown | Kamaraj | 2024-04-20 | - | A side display cable replaced - On/off switch replaced - Working properly - Resolved
CL4405 | 2024-04-20 | Dharmapuri | G | Unloading and unloading training | Preventive | Prabu | 2024-04-20 | - | Unloading done - Unloading training provided - Attended
CL4406 | 2024-04-20 | Avadi | G | Fire extinguisher service | Preventive | Suneel Sagar | 2024-04-20 | - | Fire extinguisher service done and fire safety training provided to pump staffs - Attended
CL4407 | 2024-04-20 | Kattupakkam | G | Fire extinguisher service | Preventive | Suneel Sagar | 2024-04-20 | - | Fire extinguisher service done and fire safety training provided to pump staffs - Attended
CL4408 | 2024-04-20 | Virudhunagar | C | Stamping and calibration work | Certification | Kathiresan | 2024-04-20 | - | Calibration and stamping work done - "A" Side 10 ltrs = 9.94 "B" Side 10 ltrs = 9.94 "K" factor reports ; 'A' Side = 10200 'B' Side = 10200 Testing reports : 'A' Side = 151.32 'B' Side = 134.14 Total = 285.46 - Completed
CL4409 | 2024-04-20 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-20 | - | Total lit : 1.98 Total Amount : 120/- Auto : 1 no Total vehicle : 1 no- Completed
CL4410 | 2024-04-20 | Ariyamangalam | D | Nozzle testing and servicing at B side | Development | Nepolean | 2024-04-20 | - | Nozzle tested and serviced - B side testing : 3.30 L - Attended
CL4411 | 2024-04-20 | Ellis Nagar | T | Dispensing pump and motor teflon coupling damaged | Breakdown | Kathiresan | 2024-04-20 | 1.55 Hours | New coupler replaced - Working fine - Rectified
CL4412 | 2024-04-21 | Hosur | G | Fire extinguisher service and renewal | Preventive | Navaneetha Krishnan | 2024-04-21 | - | Fire extinguisher renewal done - Fire safety training provided to pump staffs - Attended
CL4413 | 2024-04-21 | Krishnagiri | R | Drive panel MOL problem | Breakdown | Prabu | 2024-04-21 | - | Turbo drive looped and MNX18 contactor fitted - Rectified temporarily
CL4414 | 2024-04-21 | Palladam | A | Automation mobile lost | Breakdown | Gowtham | 2024-04-21 | - | Mobile replaced with batchen dispenser mobile - Resolved
CL4415 | 2024-04-22 | Kangeyam | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2024-04-22 | - | Fire extinguisher renewal and service done - 75 Kg extinguisher replaced by new one - Fire safety training provided to pump staffs - Attended
CL4416 | 2024-04-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-22 | - | Redeem Litre-13.29 Amount Rs-805.74 Total No's of Redeem vehicle -6 Auto-6 Car-0 - Completed
CL4417 | 2024-04-22 | Erode | D | A nozzle defect | Breakdown | Avinash | 2024-04-22 | - | A nozzle replaced with new one - Testing : 0.89 L - Rectified
CL4418 | 2024-04-23 | Bhavani | R | Stablizer B phase coil winding burnt | Breakdown | Avinash | 2024-04-23 | - | Stabilizer working in bypass mode - Rectified temporarily
CL4419 | 2024-04-23 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-04-23 | - | Total liter: 1.49 Total amount: 90/- Total vehicle : 1no Auto: 1no - Completed
CL4420 | 2024-04-23 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-23 | - | Redeem Litre-13.84 Amount Rs-840.00 Total No's of Redeem vehicle -6 Auto-6 Car-0- Completed
CL4421 | 2024-04-24 | Bhavani | R | Servo stabilizer servicing | Breakdown | Avinash | 2024-04-24 | - | B phase coil winding replaced - Coil motor capacitor replaced for all 3 phases - Stabilizer working properly - Resolved
CL4422 | 2024-04-24 | Ellis Nagar | D | A side keypad not working properly | Breakdown | Kathiresan | 2024-04-24 | - | Keypad replaced with new - Working properly - Completed
CL4423 | 2024-04-24 | Palladam | R | R phase variac surface damaged | Breakdown | Gowtham | 2024-04-24 | - | Variac serviced by vendor service person - Working good - Attended
CL4424 | 2024-04-25 | Krishnagiri | T | STP motor defect | Breakdown | Prakash, Prabu and Chandrasekar | 2024-04-26 | 12 Hours | Above ground motor is replaced - Working properly - Sales started - No leakage found - PMR done on 27.04.2024 - Completed
CL4425 | 2024-04-25 | Ariyamangalam | T | Decanting motor belt defect | Breakdown | Nepolean | 2024-04-25 | - | Decanting motor belt replaced with new and side cover bolt nut replaced - Rectified
CL4426 | 2024-04-25 | Vedachandur | C | PMR work | Preventive | Kamaraj | 2024-04-25 | - | Total area leakage tested - PMR done - Earthing Resistance - 1.9 ohms.CP voltage -0.850 DC - Attended
CL4427 | 2024-04-25 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-25 | - | Redeem Litre-3.47 Amount Rs-211.00 Total No's of Redeem vehicle -2 Auto-2 Car-0 - Completed
CL4428 | 2024-04-26 | Thiruvaiyaru | T | Unloading liquid line ROV defect | Breakdown | Pandi Durai | 2024-04-26 | - | Unloading liquid line ROV serviced and fitted - Oil changed for both ALDS and N2 compressors - All the equipments are working properly - PMR done - Attended
CL4429 | 2024-04-26 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-26 | - | Redeem Litre-7.92 Amount Rs-480.00 Total No's of Redeem vehicle -3 Auto-3 Car-0 - Completed
CL4430 | 2024-04-26 | Thanjavur | R | ALDS compressor running continuously due to dispensing liquid line ROV air leakage | Breakdown | Pandi Durai | 2024-04-26 | - | Unloading liquid line ROV replaced with dispensing ROV - Compressor running properly - V belt is replaced to arrest the noise from compressor - Total area leakage tested - PMR done - Completed
CL4431 | 2024-04-27 | Avinashi | C | PMR work | Preventive | Gowtham | 2024-04-27 | - | PMR done - Refreshment safety training program provided to pump staffs - Attended
CL4432 | 2024-04-27 | Ariyamangalam | G | Outlet running in Genset due to EB one phase problem | Breakdown | Nepolean and Pandi Durai | 2024-04-28 | - | EB phase problem resolved - Working in EB mode - Attended
CL4433 | 2024-04-28 | Villapuram | T | Dispensing pneumatic line damaged | Breakdown | Kathiresan | 2024-04-28 | - | Dispensing pneumatic hose replaced for 35 mtrs to arrest the air leakage - AB dispenser printer cable changed for 43 mtrs - ALDS compressor NRV inner spring replaced - Completed
CL4434 | 2024-04-28 | Ariyamangalam | R | Servo stabilizer servo mode is not working | Breakdown | Nepolean | 2024-04-29 | - | Phase variac serviced and fitted - Servo stabilizer working properly - kept under observation - Resolved
CL4435 | 2024-04-28 | Paramathivelur | D | B nozzle leakage | Breakdown | Thirumalaisamy | 2024-04-28 | - | New nozzle replaced - Defective nozzle repaired and kept for replacement - PMR done - Rectified
CL4436 | 2024-04-28 | Uthamasolapuram | T | Dispensing ROV pneumatic hose damaged | Breakdown | Prabu | 2024-04-28 | - | New pneumatic hose replaced to arrest the leakage - PMR done - Rectified
CL4437 | 2024-04-29 | Tharamangalam | D | A nozzle dispensing hose damaged | Breakdown | Prabu | 2024-04-29 | - | New dispensing hose replaced - PMR done - Resolved
CL4438 | 2024-04-29 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-04-29 | - | Redeem Litre-4.49 Amount Rs-272.00 Total No's of Redeem vehicle -2 Auto-1 Car-1 - Completed
CL4439 | 2024-04-29 | Bathlagundu | C | PMR work | Preventive | Kamaraj | 2024-04-29 | - | PMR done - Completed
CL4440 | 2024-04-29 | Namakkal 2 | T | Dispensing line pneumatic hose damaged | Breakdown | Nivas | 2024-04-29 | - | New pneumatic hose replaced to arrest the leakage for 60 Mtrs - PMR done - Rectified
CL4441 | 2024-04-29 | T.V.Kovil | T | Unloading line pneumatic hose damaged | Breakdown | Vigneshwaran | 2024-04-29 | - | New pneumatic hose replaced to arrest the leakage - Rectified
CL4442 | 2024-04-29 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-04-29 | - | Total liters -3.97 Total Amount -240.00 Auto -2 Car -0 Total - 2 - Completed
CL4443 | 2024-05-01 | T.V.Kovil | D | A side metering unit slow delivery | Breakdown | Vigneshwaran | 2024-05-01 | - | A metering unit solenoid coil cable corrected - A side testing : 0.64 lit - Resolved
CL4444 | 2024-05-02 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-02 | - | Redeem Litre-2.27 Amount Rs-136.00 Total No's of Redeem vehicle -1 Auto-1 Car-0 - Completed
CL4445 | 2024-05-02 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-02 | - | Total liters -4.01 Total Amount -240.00 Auto -1 Car -1 Total =2- Completed
CL4446 | 2024-05-03 | Kodumudi | G | Unloading training | Preventive | Thirumalaisamy | 2024-05-03 | - | Unloading training provided - DP valve screw adjusted to rectify the jumping complaint - PMR done - Automation equipment maintenance done - Testing 4.76 L - Completed
CL4447 | 2024-05-03 | Namakkal 1 | G | N2 machine filling problem due to duct accumulated in solenoid valve | Breakdown | Nivas | 2024-05-03 | - | Solenoid valve cleaned - N2 machine wokring fine - Outlet is running in DG mode due to EB post damaged - Attended
CL4448 | 2024-05-03 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-03 | - | Redeem Litre-2.29 Amount Rs-137.00 Total No's of Redeem vehicle -1 Auto-1 Car-0 - Completed
CL4449 | 2024-05-03 | Dindigul | C | PMR work | Preventive | Kamaraj | 2024-05-03 | - | PMR done - Completed
CL4450 | 2024-05-04 | Tiruchengode | C | PMR work | Preventive | Avinash | 2024-05-04 | - | PMR done - Total area leakage checked - Earth regenerated - Safety training provided to pump staffs - CP value dropped CP( -0.811 VDC) - Kept under observation - Completed
CL4451 | 2024-05-04 | Villapuram | D | A nozzle replacement due to running over 1215800 Ltrs | Preventive | Kathiresan | 2024-05-04 | - | New nozzle replaced - Testing A side : 5.88 Ltrs - Resolved
CL4452 | 2024-05-04 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-04 | - | Total liters -5.18 Total Amount -310.00 Auto -0 Car -2 Total =2 - Completed
CL4453 | 2024-05-04 | Kodungaiyur | D | A nozzle dispensing hose damaged | Breakdown | Suneel Sagar | 2024-05-04 | - | Defected hose replaced by recrimped dispensing hose - Found satisfactory - Rectified
CL4454 | 2024-05-04 | Uthamapalayam | D | Dispenser E05 and E10 errors occurred - Display not working and totalizer reversed due to power fluctuation | Breakdown | Kamaraj | 2024-05-04 | 5 Hours | Sales running only at A nozzle - Permission given from backend to resolve totalizer reversal - Problematic display sent to HO - Attended
CL4455 | 2024-05-04 | Sulur | C | PMR work | Preventive | Gowtham | 2024-05-04 | - | PMR done - Safety training provided to pump staffs - Oil changed for both ALDS and N2 compressor - Completed
CL4456 | 2024-05-04 | Neelambur | C | PMR work | Preventive | Gowtham | 2024-05-04 | - | PMR done - Safety training provided to pump staffs - Completed
CL4457 | 2024-05-05 | Ammapet | C | Unloading training and PMR - CCTV POE switch problem - Camera working in offline mode | Preventive | Avinash | 2024-05-05 | - | Unloading training provided and unloading done - PMR done - Leakage checked in total area - Earth regenerated - Safety training provided to pump staffs - CCTV POE switch replaced with new - Camera working online - Completed
CL4458 | 2024-05-05 | Namakkal 1 | D | A nozzle leakage | Breakdown | Nivas | 2024-05-05 | - | Nozzle cleaned and refitted - Leakage arrested -Testing : 0.82 L - Resolved
CL4459 | 2024-05-05 | Vedachandur | T | Unloading vapour ROV air leakage | Breakdown | Kamaraj | 2024-05-31 | - | Unloading vapour ROV air leakage arrested by servicing at H.O and fitted
CL4460 | 2024-05-06 | Uthamapalayam | D | Replacement of problematic display card | Breakdown | Kamaraj | 2024-05-06 | - | New display card and dsiplay cable has been replaced - Working properly - PMR done - Resolved
CL4461 | 2024-05-06 | Ayothiyapattinam | C | PMR work | Preventive | Prabu | 2024-05-06 | - | PMR done - Tank area leakage checked - CP - 1.14 VDC - Safety training provided to pump staffs - Completed
CL4462 | 2024-05-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-06 | - | Redeem Litre-8.99 Amount Rs-539.00 Total No's of Redeem vehicle -3 Auto-1 Car-2 - Completed
CL4463 | 2024-05-06 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-06 | - | Total liters-3.17 Total Amount -190.00 Auto -1 Car -0 Total - 1- Completed
CL4464 | 2024-05-07 | Avinashi | T | HLA and ATG probe cables damaged due to rat bite | Breakdown | Gowtham | 2024-05-07 | - | Cables of both components reconnected - ATG working properly - Rectified
CL4465 | 2024-05-07 | Nasiyanur | C | PMR work | Preventive | Avinash | 2024-05-07 | - | PMR done - Total area leakage checked - Earth regenerated - Safety training provided to pump staffs - Completed
CL4466 | 2024-05-07 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-07 | - | Redeem Litre-4.54 Amount Rs-272.00 Total No's of Redeem vehicle -2 Auto-1 Car-1- Completed
CL4467 | 2024-05-07 | Palayam | G | Fire extinguisher service and renewal | Preventive | Thirumalaisamy | 2024-05-07 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - 9kg DCP extinguisher replaced with ABC type - Attended
CL4468 | 2024-05-07 | Aravakurichi | G | Fire extinguisher service and renewal | Preventive | Thirumalaisamy | 2024-05-07 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - Attended
CL4469 | 2024-05-07 | Kodumudi | G | Fire extinguisher service and renewal | Preventive | Thirumalaisamy | 2024-05-07 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - Attended
CL4470 | 2024-05-07 | Avinashi | D | Batchen dispenser error 20 occurred | Breakdown | Gowtham | 2024-05-10 | 10 Hours (in 3 days in Batchen Dispenser) | Reset done - Y and B phase indicator newly replaced - Cable conduits are packed with PU foam - Batchen dispenser input power avail from UPS for observation - Found satisfactory on all of the ALDS operation - Resolved
CL4471 | 2024-05-08 | Tenkasi | R | Online UPS reinstallation and automation maintenance | Preventive | Kathiresan | 2024-05-08 | - | Online UPS reinstallation and automation maintenance done - PMR done - Attended
CL4472 | 2024-05-08 | T.V.Kovil | C | Calibration work | Certification | Nepolean | 2024-05-08 | - | Calibration work done - Testing : A side : 255.46 L B side : 152.66 L C side162.14 L D side: 157.65 L Total: 727.91 L - Completed
CL4473 | 2024-05-08 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-08 | - | Total liters-2.34 Total Amount -140.00 Total vehicle -1 Auto -1- Completed
CL4474 | 2024-05-08 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-08 | - | Redeem Litre-13.92 Amount Rs-834.00 Total No's of Redeem vehicle -5 Auto-4 Car-1- Completed
CL4475 | 2024-05-08 | Palladam 1 | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2024-05-08 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - Attended
CL4476 | 2024-05-08 | Palladam 2 | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2024-05-08 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - Attended
CL4477 | 2024-05-08 | Avinashi | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2024-05-08 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - Attended
CL4478 | 2024-05-08 | Neelambur | G | Fire extinguisher service and renewal | Preventive | Gowtham | 2024-05-08 | - | Fire extinguisher service done - Fire safety training provided to pump staffs - Attended
CL4479 | 2024-05-09 | Ramnad | R | Compressor running continuously due to FRL unit defect | Breakdown | Kathiresan | 2024-05-09 | - | New FRL unit replaced - RS485 to USB converter board replaced - CP value = - 1.36 - Earth value = 1.1 (v) - PMR done - Completed
CL4480 | 2024-05-09 | Viruthachalam | R | Online UPS back up problem | Breakdown | Pandi Durai | 2024-05-09 | - | 12V 7AH battery 3 Nos replaced with new - Dispenser vapour line ROV air leakage arrested by tihgtening the stem - Total area leakage checked - All equipments working properly - Unloading training provided - PMR done - Completed
CL4481 | 2024-05-09 | T.V.Kovil | C | DL stamping work | Certification | Nepolean | 2024-05-09 | - | DL Stamping done - K factor: A side : 100360 B side: 101000 C side: 10100 D side : 10000 Testing lit: D side: 159.28. A side 10. 00 lit = 10.02 B side 10.00 lit = 10.02 C side 10.00 lit = 9.97 D side 10.00 lit = 10.04 - Completed
CL4482 | 2024-05-09 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-09 | - | Redeem Litre-16. 01 Amount Rs-960.00 Total No's of Redeem vehicle -7 Auto-6 Car-1- Completed
CL4483 | 2024-05-10 | Sangagiri | G | General outlet visit | Preventive | Avinash | 2024-05-10 | - | PMR done - Total area leakage checked - Safety training provided to pump staffs - Automation maintenance done - Master solenoid coil replaced with unloading solenoid coil to arrest the leakage - Working properly - Attended
CL4484 | 2024-05-10 | Theni | D | Batchen dispenser B nozzle LPG leakage due to mount defect | Breakdown | Kamaraj | 2024-05-10 | - | B side new nozzle replaced - Total area leakage checked and PMR done - Totalizer reading B-side= 248023.00 - Testing - 1.2 L - Resolved
CL4485 | 2024-05-10 | Cantonment | D | Dispenser A side slow delivery | Breakdown | Chandrasekar | 2024-05-10 | - | High flow low flow cleaned and serviced - Flow is proper - Testing : 1.01 L - Rectified
CL4486 | 2024-05-10 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-10 | - | Redeem Litre-1.97 Amount Rs-118.00 Total No's of Redeem vehicle -1 Auto-1 Car-0 - Completed
CL4487 | 2024-05-10 | Avinashi | R | Online UPS battery problem | Breakdown | Gowtham | 2024-05-10 | 35 Mins | Online UPS battery topped up with distilled water and serviced - Working properly - Rectified
CL4488 | 2024-05-11 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-11 | - | Redeem Litre-12.90 Amount Rs-773.00 Total No's of Redeem vehicle -3 Auto-1 Car-2 - Completed
CL4489 | 2024-05-12 | Mettupalayam | C | PMR work | Preventive | Gowtham | 2024-05-12 | - | PMR done - Automation maintenance done - ATG is not working properly - Kept under observation - Safety training provided to pump staffs - Completed
CL4490 | 2024-05-12 | Musiri | G | Panel not working DG mode due to loose contact in changeover fuse | Breakdown | Nivas | 2024-05-12 | - | Changeover fuse wiring reconnected - Panel working in both EB and DG mode - Rectified
CL4491 | 2024-05-12 | Ariyamangalam | D | Batchen dispenser 'C' side metering unit leakage | Breakdown | Nepolean | 2024-05-12 | - | New mechanical seal kit changed - Leakage arrested - Working properly - Testing C side : 107.30 L - Resolved
CL4492 | 2024-05-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-13 | - | Redeem Litre-4.37 Amount Rs-262.00 Total No's of Redeem vehicle -2 Auto-2 Car-0 - Completed
CL4493 | 2024-05-13 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-13 | - | Redeem Litre-6.52 Amount Rs-390.00 Total No's of Redeem vehicle -2 Auto-1 Car-1 - Completed
CL4494 | 2024-05-13 | Ellis Nagar | R | Online UPS 12 (v) 42 AH Battery 3 nos defect | Breakdown | Kathiresan | 2024-05-13 | - | Now UPS working in bypass mode - Rectified temporarily
CL4495 | 2024-05-13 | Bhavani | D | A nozzle replacement due to running over 2500000 Ltrs | Preventive | Avinash | 2024-05-13 | - | A side nozzle & B nozzle teeth replaced - PMR completed - Leak checked in total area - Safety training provided to pump staffs - Testing A side : 0.84 lts - Recitified
CL4496 | 2024-05-14 | Attur | D | Dispenser C and D side nozzle hoses damaged | Breakdown | Nivas | 2024-05-14 | - | Both side nozzle hoses are replaced and display glass changed due to fade condition. PMR completed - Leak checked - Attended
CL4497 | 2024-05-14 | Manapparai | T | Unloading training and ROV Service | Breakdown | Nepolean | 2024-05-14 | - | Unloading training provided, Vapour line ROV serviced and in Dispenser nozzle teeth 8 nos replaced at both side - Working properly - PMR done - Servo stabilizer working in servo mode - Completed
CL4498 | 2024-05-14 | Dharmapuri | T | Dispensing liquid line ROV leakage | Breakdown | Prabu | 2024-05-14 | - | Dispensing liquid line ROV stem leakage arrested by tightening the nut. Dispensing motor spider changed. Dispenser A side display glass changed - PMR Completed - Attended
CL4499 | 2024-05-14 | Krishnagiri | D | Dispenser Error 04 noticed to improper input power | Breakdown | Prabu | 2024-05-14 | - | Error cleared - Kept under observation -Tank area pipe line leakage and copper jumper fixed - PMR done - Resolved temporarily
CL4500 | 2024-05-14 | Ariyamangalam | A | Dispenser running without mobile | Development | Pandi Durai | 2024-05-14 | - | Dispenser running with mobile. New reedem app updated - Completed
CL4501 | 2024-05-14 | Cantonment | A | Dispenser running without mobile | Development | Pandi Durai | 2024-05-14 | - | Dispenser running with mobile. New reedem app updated - Completed
CL4502 | 2024-05-14 | T.V.Kovil | A | Dispenser running without mobile | Development | Pandi Durai | 2024-05-14 | - | Dispenser running with mobile. New reedem app updated - Completed
CL4503 | 2024-05-14 | Madurai-Villapuram | D | Dispenser D side nozzle leakage | Breakdown | Kathiresan | 2024-05-14 | - | D side spare nozzle replaced - Resolved
CL4504 | 2024-05-15 | Chengalpattu | C | Stamping and Calibration work | Certification | Vigneshwaran | 2024-05-15 | - | Calibration and stamping work done -PMR Completed, Yenen dispenser B side Nozzle hose replaced - No changes in K factor "K" factor reports : 'A' Side = 10040 'B' Side = 10010 Testing reports : 'A' Side = 150.01 L 'B' Side = 155.68 L Total = 305.69 L - Completed
CL4505 | 2024-05-15 | Perundurai | D | Dispenser A nozzle leakage | Breakdown | Avinash | 2024-05-15 | - | Dispenser A nozzle replaced - DP valve spring tension adjusted - Fill point liquid line ROV stem leakage arrested by tightening the nut, PMR done - Total leakage checked - Testing A = 27.16 L - Attended
CL4506 | 2024-05-15 | Perundurai | A | Dispenser running without mobile due to billing mobile defect | Breakdown | Avinash | 2024-06-23 | - | Dispenser mobile billing defect resoved by changing of new mobile.Working in good condition.
CL4507 | 2024-05-15 | Palayam | G | Outlet general visit | Preventive | Thirumalaisamy | 2024-05-15 | - | Dispenser both side defective keyboard changed with new - PMR completed. Automation equipment maintenance completed - Attended
CL4508 | 2024-05-15 | Ariyamangalam | G | Outlet running in DG mode due E.B Power off due to Y Phase problem | Breakdown | Nepolean | 2024-05-15 | - | Outlet running back in EB mode after resolved Y phase problem - Rectified
CL4509 | 2024-05-15 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-15 | - | Redeem Litre-51.34 Amount Rs-3070.00 Total No's of Redeem vehicle -19 Auto-19 Car-0 - Completed
CL4510 | 2024-05-15 | Ellis Nagar | R | Dispenser running in offline mode due to Online UPS battery defect | Breakdown | Kathiresan | 2024-05-15 | - | Online UPS 12 v 42 AH new battery changed and the back up timing is increased to more than 15 min - Dispenser back to online mode - Rectified
CL4511 | 2024-05-15 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-15 | - | Redeem Litre-104.27 L Amount Rs-6249.00 Total No's of Redeem vehicle -41 Auto-41 Car-0 - Completed
CL4512 | 2024-05-15 | Kangeyam | C | Rule-19 work | Certification | Gowtham, Prakash & Chandrasekar | 2024-05-17 | 38 Hours | Rule 19 work completed. HLA, ATG, Fill point emergency switch cables are replaced. New DOL starter installed. All joint leak checked and found satisfactory - All pneumatic hose replaced - Sales started - Completed
CL4513 | 2024-05-15 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-15 | - | Redeem Litre-157.78 L Amount Rs- 9456.00 Total No's of Redeem vehicle -60 Auto-58 Car-2 - Completed
CL4514 | 2024-05-16 | Rasipuram | G | Unloading training | Preventive | Nivas | 2024-05-16 | - | Unloading completed and training provided to pump staffs
CL4515 | 2024-05-16 | Tirunelveli | T | Unloading motor not working due to tank 1 HLA card PCB problem | Breakdown | Kathiresan | 2024-04-17 | - | Tank 1 looping with Tank 2 is done and motor is working. Dispensing pneumatic hose 35 mtrs changed to arrest leakage - Rectified temporarily
CL4516 | 2024-05-16 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-16 | - | Redeem Litre-83.78 L Amount Rs-5010.00 Total No's of Redeem vehicle -31 Auto-30 Car-1 - Completed
CL4517 | 2024-05-16 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-16 | - | Redeem Litre- 197.76 L Amount Rs-11853.00 Total No's of Redeem vehicle -77 Auto-74 Car-3 - Completed
CL4518 | 2024-05-16 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-16 | - | Redeem Litre- 282.03 L Amount Rs-16898.41 Total No's of Redeem vehicle -106 Auto-106 Car-0 - Completed
CL4519 | 2024-05-16 | Avadi | C | Stamping and Calibration work | Certification | Vigneshwaran | 2024-05-17 | - | Calibration and stamping work done, K factor no changes. "K" factor 'A' Side = 10000 'B' Side = 10000 C side : 10000 D side : 10000 Testing reports : 'A' Side = 145.08 L 'B' Side = 150.07 L C side : 130.11 L D side : 130.02 L Total = 555.28 L - Unloading vapour line ROV one number replaced - Completed
CL4520 | 2024-05-16 | Kattupakkam | C | Stamping and Calibration work | Certification | Vigneshwaran | 2024-05-16 | - | Calibration done, K factor no changes. Stamping report : K factor A side: 9842 B side :9842 C side :9820 D side :9820 Testing lit: A side:124.31ltrs B side :161.94 ltrs C side :127.79ltrs D side :130.55 ltrs Total Testing liter: 544.59 - Stamping done 20.05.2024 - Completed
CL4521 | 2024-05-17 | Omalur | G | Unloading Training | Preventive | Prabu | 2024-05-17 | - | Unloading done - Unloading training provided - Attended
CL4522 | 2024-05-17 | Tharamangalam | D | Temperature gauge not working and Dispenser B side nozzle teeth worn out | Breakdown | Prabu | 2024-05-17 | - | New temperature gauge replaced - B nozzle teeth replaced - Resolved
CL4523 | 2024-05-17 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-17 | - | Redeem Litre- 53.02 L Amount Rs-3170 Total No's of Redeem vehicle -20 Auto-20 Car-0 - Completed
CL4524 | 2024-05-17 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-17 | - | Redeem Litre- 232.76 L Amount Rs-13944. Total No's of Redeem vehicle -81 Auto-80 Car-1 - Completed
CL4525 | 2024-05-17 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-17 | - | Redeem Litre- 219.10 L Amount Rs-13129 Total No's of Redeem vehicle -80 Auto-76 Car-4 - Completed
CL4526 | 2024-05-17 | Kodungaiyur | C | Calibration work | Certification | Vigneshwaran | 2024-05-17 | - | Calibration work completed, K factor no changes. Calibration report : K factor A side:1000 B side :1000 Testing lit: A side:155.22 ltrs B side :152.92 ltrs Total Testing liter:308.14 - Completed
CL4527 | 2024-05-18 | Avinashi | D | Batchen dispenser B side not working due to automation nullify error | Breakdown | Avinash | 2024-05-18 | 12 Hours (B side) | Solenoid valve cleaned - Automation nullify error cleared at the back end - Testing 1.70 L - Resolved
CL4528 | 2024-05-18 | Chengalpattu | T | ATG values not shown due to ATG Cable failure | Breakdown | Suneel Sagar and Vigneshwaran | 2024-05-18 | - | New ATG cable connected and working in good condition - Attended
CL4529 | 2024-05-18 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-18 | - | Redeem Litre- 72.89 L Amount Rs-4360 Total No's of Redeem vehicle -21 Auto-18 Car-3 - Completed
CL4530 | 2024-05-18 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-18 | - | Redeem Litre- 302.49 L Amount Rs- 18121.74 Total No's of Redeem vehicle -103 Auto-103 Car-0 - Completed
CL4531 | 2024-05-18 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-18 | - | Redeem Litre- 264.89 L Amount Rs- 15864 Total No's of Redeem vehicle -78 Auto-73 Car-5 - Completed
CL4532 | 2024-05-20 | Pudukkottai | G | Unloading Training | Preventive | Nepolean | 2024-05-20 | - | Unloading and operator training provided -Work completed.
CL4533 | 2024-05-20 | Madurai-Villapuram | D | Dispenser-A and B side slow delivery | Breakdown | Kathiresan | 2024-05-20 | - | Slow delivery problem rectified by changing of dispenser filter, Working in good condition. Testing 10 ltrs - Resolved
CL4534 | 2024-05-20 | Kattupakkam | C | Stamping work | Certification | Suneel Sagar | 2024-05-20 | - | Stamping done - Completed
CL4535 | 2024-05-20 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-20 | - | Redeem Litre- 232.97 L Amount Rs- 13956 Total No's of Redeem vehicle -70 Auto-66 Car-4 - Completed
CL4536 | 2024-05-20 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-20 | - | Redeem Litre- 124.67 L Amount Rs- 7456.10 Total No's of Redeem vehicle -37 Auto-36 Car-1 - Completed
CL4537 | 2024-05-20 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-20 | - | Redeem Litre- 294.96 L Amount Rs- 17671.00 Total No's of Redeem vehicle -93 Auto-92 Car-1 - Completed
CL4538 | 2024-05-20 | Aravakurichi | D | Dispenser both side nozzle hose defect | Breakdown | Thirumalaisamy | 2024-05-20 | - | Outlet both side 5 m nozzle hose changed. PMR done. Testing 1.26 litres - Completed
CL4539 | 2024-05-21 | Thiruvaiyaru | D | Dispenser A side is in slow delivery - Dispensing and decanding air hose damaged | Breakdown | Pandi Durai | 2024-05-21 | - | Solenoid low and high flow coil cleaned. Dispensing and decanding air hose replaced by 90 meter new air hose . Pump working in good condition - Completed A side testing = 14.21 ltr B side testing = 5.02 ltr Total testing = 19.23 ltr
CL4540 | 2024-05-21 | Musiri | R | Offline ups problem due to 12 volt 7 AH battery failure and master solenoid coil air leakage. | Breakdown | Nivas | 2024-05-21 | - | Offline ups problem rectified by replacing new 12 volt 7 AH battery and master solenoid coil air leakage arrested by interchange of unloading coil - Completed
CL4541 | 2024-05-21 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-21 | - | Redeem Litre- 71.57 L Amount Rs- 4280 Total No's of Redeem vehicle -25 Auto-23 Car-2 - Completed
CL4542 | 2024-05-21 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-21 | - | Redeem Litre- 274.04 L Amount Rs- 16417.79 Total No's of Redeem vehicle -87 Auto-87 Car-0 - Completed
CL4543 | 2024-05-21 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-21 | - | Redeem Litre- 279.24 L Amount Rs- 16728 Total No's of Redeem vehicle -78 Auto-72 Car-6 - Completed
CL4544 | 2024-05-22 | Udumalpet | D | Dispenser C side hose outer layer slightly peeling off and problem in tank 1 motor Lovejoy coupling. | Breakdown | Gowtham | 2024-05-22 | - | C nozzle hose recrimping done - Tank 1 motor Lovejoy coupling replaced. New fire bucket 2 nos purchased and kept. PMR completed. Testing ltr - 0.90 ltr - Completed
CL4545 | 2024-05-22 | Vedachandur | T | Unloading work | Preventive | Kamaraj | 2024-05-22 | - | Unloading done - Completed
CL4546 | 2024-05-22 | Virudhunagar | D | Dispenser A side key pad not working - B side nozzle defect - Off line UPS under problem due to short circuit - 25 NB ballvalve with ROV vapour line LPG leakage | Breakdown | Kathiresan | 2024-05-22 | - | A side key pad and B side spare nozzle replaced - Dispensing 25 NB vapour line ballvalve with ROV LPG leakage arrested by tightening the nut of stem - PMR done - Testing 0.95 litres - Completed
CL4547 | 2024-05-22 | Ariyamangalam | T | Unloading pump (EBSRAY) fitting and testing. | Preventive | Nepolean | 2024-05-22 | - | Unloading pump (EBSRAY) fitting and testing work completed - Kept under observation for few unloading.
CL4548 | 2024-05-22 | Cantonment | D | Pump E side nozzle leakage due to NRV centre oring damaged. C nozzle leakage due to nozzle teeth worn out. | Breakdown | Chandrasekar | 2024-05-22 | - | E side nozzle leakage rectified by changing of damaged NRV centre oring. E Testing.0.93 litre - C nozzle leakage resolved by changing of 4 nos of teeth hammer -Both Nozzles working in good condition- C side reading.4813212.13-Completed
CL4549 | 2024-05-22 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-22 | - | Redeem Litre- 131.09 L Amount Rs-7840 Total No's of Redeem vehicle -39 Auto-37 Car-2 - Completed
CL4550 | 2024-05-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-22 | - | Redeem Litre- 231.80 L Amount Rs- 13886 Total No's of Redeem vehicle -71 Auto-70 Car-1 - Completed
CL4551 | 2024-05-22 | Ayothiyapattinam | T | Unloading Training | Preventive | Prabu | 2024-05-22 | - | Unloading and operator training provided -Work completed.
CL4552 | 2024-05-22 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-22 | - | Redeem Litre- 178.88 L Amount Rs- 10716 Total No's of Redeem vehicle -60 Auto-58 Car-2 - Completed
CL4553 | 2024-05-23 | Mulanur | D | Continuous running of compressor due to dispenser line pneumatic hose leakage - Dispensing liquid line ROV lpg leak problem. | Breakdown | Thirumalaisamy | 2024-05-23 | - | Dispenser line pneumatic hose newly changed and dispensing liquid line ROV lpg leak arrested by tightening the nut - A nozzle centre mound O ring replaced to arrest the nozzle leakage. PMR done. Automation equipment maintenance completed - Work completed
CL4554 | 2024-05-23 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-23 | - | Redeem Litre- 67.21 L Amount Rs- 4020 Total No's of Redeem vehicle -21 Auto-20 Car-1 - Completed
CL4555 | 2024-05-23 | Cantonment | A | Loyalty program redeem | Development | Navaneetha Krishnan | 2024-05-23 | - | Redeem Litre- 130.30 L Amount Rs- 7807 Total No's of Redeem vehicle - 43 Auto-42 Car-1 - Completed
CL4556 | 2024-05-23 | Krishnagiri | R | Control panel booting problem due to servo stabilizer display board problem because of EB wiring short circuited - Dispenser reading reversal | Breakdown | Prabu | 2024-05-23 | - | Control panel booted with servo stabilizer working in by pass mode - Dispenser reading reverse problem cleared in the back end - Dispenser line pneumatic hose replaced to arrest the leakage - Work completed
CL4557 | 2024-05-23 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-23 | - | Redeem Litre - 222.91 L Amount Rs- 13354 Total No's of Redeem vehicle - 67 Auto- 57 Car-10 - Completed
CL4558 | 2024-05-24 | Kangeyam | T | CP failure | Breakdown | Gowtham | 2024-06-03 | - | New CP installed. Existing Anodes are defected and totally 4 nos.of Anodes and 1 no of reference Electrode replaced.Working in good condition. Reading after commissioning = - 1.426 DCV.
CL4559 | 2024-05-24 | Avadi | D | Dispenser A side hose leakage | Breakdown | Suneel Sagar | 2024-05-24 | - | A side hose replaced by recrimped hose -Work completed
CL4560 | 2024-05-24 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-24 | - | Redeem Litre- 61.86 L Amount Rs- 3700 Total No's of Redeem vehicle - 20 Auto- 19 Car-1 - Completed
CL4561 | 2024-05-24 | Krishnagiri | R | Stabilizer display board and coil replacement | Breakdown | Prabu | 2024-05-24 | - | Stabilizer display board and coil changed. Input - R 235, Y 251, B 250, Output R 226, Y 234, B 229. Stabilizer mode working in good condition - Work completed.
CL4562 | 2024-05-24 | Cantonment | A | Loyalty program redeem | Development | Navaneetha Krishnan | 2024-05-24 | - | Redeem Litre- 152.80 L Amount Rs- 9151.17 Total No's of Redeem vehicle - 46 Auto- 45 Car-1 - Completed
CL4563 | 2024-05-24 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-05-24 | - | Redeem Litre- 79.21 L Amount Rs- 4744 Total No's of Redeem vehicle - 23 Auto- 19 Car-4 - Completed
CL4564 | 2024-05-25 | Kattupakkam | T | Dispensing motor replacement due to MOL error | Breakdown | Suneel Sagar | 2024-05-25 | 10 Hours | New dispensing motor replaced - Outlet operation found satisfactory - Attended
CL4565 | 2024-05-25 | Cantonment | D | A nozzle leakage | Breakdown | Chandrasekar | 2024-05-25 | - | Nozzle hammer teeth 4 nos replaced at A side - Leakage arrested - A- side reading: 10466472.87 - Resolved
CL4566 | 2024-05-25 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-25 | - | Redeem Litre- 93.92 L Amount Rs- 5627 Total No's of Redeem vehicle - 31 Auto- 28 Car-3 - Completed
CL4567 | 2024-05-25 | T.V.Kovil | D | C nozzle leakage | Breakdown | Pandi Durai | 2024-05-25 | - | Nozzle hammer teeth 4 nos replaced at C side - Leakage arrested - Resolved
CL4568 | 2024-05-25 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-25 | - | Redeem Litre- 71.07 L Amount Rs- 4250 Total No's of Redeem vehicle - 21 Auto- 16 Car-5 - Completed
CL4569 | 2024-05-25 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-25 | - | Redeem Litre- 75.08 L Amount Rs- 4499.68 Total No's of Redeem vehicle - 25 Auto- 25 Car-0 - Completed
CL4570 | 2024-05-26 | Uthamacholapuram | D | Dispenser bottom side air hose and FRL fitting leakage. | Breakdown | Prabu | 2024-05-26 | - | Dispenser bottom side air hose leakage arrested by changing of new one. FRL fitting leakage rectified by cleaning and servicing the FRL - Work completed.
CL4571 | 2024-05-26 | Kattupakkam | T | Dispensing pump with motor is not working | Breakdown | Suneel sagar, Chandrasekar and Lingeshwaran | 2024-05-28 | 12 Hours | Spare dispensing motor from velachery is replaced - Sales started - Dispensing motor is working without VFD in both EB and Genset mode - Working satisfactory - Attended
CL4572 | 2024-05-27 | Pudukkottai | G | Unloading Training | Preventive | Nepolean | 2024-05-27 | - | Unloading and operator training provided -Work completed.
CL4573 | 2024-05-27 | Cantonment | D | Pump A side On/Off switch not working | Breakdown | Suresh Kumar | 2024-05-27 | - | New switch replaced -Working in good condition.
CL4574 | 2024-05-27 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-27 | - | Redeem Litre- 152.83 L Amount Rs- 9155 Total No's of Redeem vehicle - 47 Auto- 46 Car-1 - Completed
CL4575 | 2024-05-27 | Ariyamangalam | D | Dispenser D side On/Off switch not working | Breakdown | Pandi Durai | 2024-05-27 | - | New switch replaced -Working in good condition.
CL4576 | 2024-05-27 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-05-27 | - | Redeem Litre- 6.88 L Amount Rs- 412 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL4577 | 2024-05-27 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-27 | - | Redeem Litre- 27.75 L Amount Rs- 1660 Total No's of Redeem vehicle - 10 Auto- 10 Car-0 - Completed
CL4578 | 2024-05-27 | Ariyamangalam | D | Dispenser C Side display hanging | Breakdown | Pandi Durai | 2024-05-27 | - | C Side display hanging problem resolved by rectify the loose connection of cable.Working in good condition-Work completed. C side testing = 43.69 ltr D side testing = 3.34 ltr Total testing = 47.03 ltr
CL4579 | 2024-05-28 | Paramathi Velur | R | Outlet not working in EB mode | Breakdown | Thirumalaisamy | 2024-05-28 | - | Outlet changeover shifter lever reassembled and properly seated. Now EB mode working normal.Work completed.
CL4580 | 2024-05-28 | Palladam 1 | D | Yenen dispenser D side hose defect | Breakdown | Gowtham | 2024-05-28 | - | Yenen dispenser D side hose assembly fully replaced from existing Batchen dispenser. Here after only yenen dispenser will be under use. Testing ltr. - 1.85 ltr -Work completed
CL4581 | 2024-05-28 | Ariyamangalam | D | Dispenser D side On/Off switch problem | Breakdown | Nepolean | 2024-05-28 | - | New switch replaced -Working in good condition.D side testing -4.34 litre
CL4582 | 2024-05-28 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-28 | - | Redeem Litre- 115.01 L Amount Rs- 6890.57 Total No's of Redeem vehicle - 41 Auto- 40 Car-1 - Completed
CL4583 | 2024-05-28 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-05-28 | - | Redeem Litre- 35.46 L Amount Rs- 2120 Total No's of Redeem vehicle - 12 Auto- 12 Car-0 - Completed
CL4584 | 2024-05-28 | Krishnagiri | D | Panel booting problem due to dispensing motor wire burnt and Servo stabilizer Y phase fuse damaged. Decanding R phase MCB burned. | Breakdown | Nivas | 2024-05-29 | 11 Hours | Panel booting problem rectified by reconnecting with new wire inside of motor junction box.Servo stabilizer Y phase problem resolved by change of new fuse. Decanding MCB R phase replaced by New MCB. Pump working in good condition -Work completed R=7.0 Amps Y=6.8 Amps B=6.3 Amps
CL4585 | 2024-05-29 | Vellakoil | D | Outlet FRL unit air leakage due to bowl damaged. | Breakdown | Thirumalaisamy | 2024-05-30 | - | New FRL unit assembly changed.PMR completed.
CL4586 | 2024-05-29 | Cantonment | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-29 | - | Redeem Litre- 69.77 L Amount Rs- 4180.48 Total No's of Redeem vehicle - 26 Auto- 26 Car-0 - Completed
CL4587 | 2024-05-29 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-29 | - | Redeem Litre- 44.64 L Amount Rs- 2670 Total No's of Redeem vehicle - 15 Auto- 15 Car-0 - Completed
CL4588 | 2024-05-29 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-05-29 | - | Redeem Litre- 34.64 L Amount Rs- 2075 Total No's of Redeem vehicle - 8 Auto- 7 Car-1 - Completed
CL4589 | 2024-05-29 | Dindigul | D | Outlet dispensing line air hose and nitrogen machine air filling hose damaged. | Breakdown | Kamaraj | 2024-05-29 | - | Ddispensing line air hose and nitrogen machine air filling hose changed. Working in good condition- Work completed
CL4590 | 2024-05-30 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-30 | - | Redeem Litre- 29.79 L Amount Rs- 1780 Total No's of Redeem vehicle - 11 Auto- 10 Car-1 - Completed
CL4591 | 2024-05-30 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-30 | - | Redeem Litre- 84.05 L Amount Rs- 5036 Total No's of Redeem vehicle - 27 Auto- 27 Car-0 - Completed
CL4592 | 2024-05-30 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-05-30 | - | Redeem Litre- 36.94 L Amount Rs- 2212 Total No's of Redeem vehicle - 10 Auto- 9 Car-1 - Completed
CL4593 | 2024-05-31 | Vedachandur | T | Dispensing and unloading area air hose line air leakage. | Breakdown | Kamaraj | 2024-05-31 | - | Dispensing and unloading area air hose line air leakage arrested by changing of new air hose. Working in good condition.-Work completed.
CL4594 | 2024-05-31 | Ellis Nagar | D | Dispenser D side spare nozzle leakage | Breakdown | Kathiresan | 2024-05-31 | - | D side nozzle leakage arrested by changing spare nozzle.Working good condition -Work completed. Testing = 0.82 ltrs
CL4595 | 2024-05-31 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-05-31 | - | Redeem Litre- 23.58 L Amount Rs- 1410 Total No's of Redeem vehicle - 7 Auto- 7 Car-0 - Completed
CL4596 | 2024-05-31 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-05-31 | - | Redeem Litre- 97.40 L Amount Rs- 5834 Total No's of Redeem vehicle - 29 Auto- 22 Car-7 - Completed
CL4597 | 2024-05-31 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-05-31 | - | Redeem Litre- 56.65 L Amount Rs- 3395 Total No's of Redeem vehicle - 20 Auto- 18 Car-2 - Completed
CL4598 | 2024-05-31 | Ariyamangalam | D | C side nozzle improper LPG flow | Breakdown | Nepolean | 2024-05-31 | - | C side nozzle LPG flow problem rectified by interchanging of solenoid coil.Working in good condition.Work completed. C side testing : 9.05 lit.
CL4599 | 2024-05-31 | Dharmapuri | T | Dispensing liquid line ROV inside air leakage. | Breakdown | Prabu | 2024-05-31 | - | Tank area dispensing liquid line ROV inside air Leakage arrested by interchanging of unloading liquid line ROV.Working in good condition-Work completed.
CL4600 | 2024-05-31 | Krishnagiri | R | General inspection | Preventive | Prabu | 2024-05-31 | - | Checking of outlet EB box to changeover and panel to dispensing motor wiring measurement and voltage check up done -Work completed.
CL4601 | 2024-05-31 | Dharapuram | G | General inspection | Preventive | Gowtham | 2024-05-31 | - | PMR completed. Compressor oil changed.
CL4602 | 2024-06-01 | Palladam-1 | G | PMR work | Preventive | Gowtham | 2024-06-01 | - | PMR completed.
CL4603 | 2024-06-01 | Palladam-2 | G | PMR work | Preventive | Gowtham | 2024-06-01 | - | PMR completed.
CL4604 | 2024-06-01 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-06-01 | - | Redeem Litre- 56.08 L Amount Rs- 3241 Total No's of Redeem vehicle - 16 Auto- 13 Car-3 - Completed
CL4605 | 2024-06-01 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-06-01 | - | Redeem Litre- 10.90 L Amount Rs- 628.30 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4606 | 2024-06-01 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-01 | - | Redeem Litre- 71.31 L Amount Rs- 4121 Total No's of Redeem vehicle - 23 Auto- 23 Car-0 - Completed
CL4607 | 2024-06-01 | Erode | T | Tank area unloading vapour line ROV LPG leakage and B side jumping problem. | Breakdown | Avinash | 2024-06-01 | - | Tank area unloading vapour line ROV LPG leakage arrested by tightening the nut and B side jumping problem rectified by adjusting the DP valve spring. PMR completed.Working in good condition. Testing A= 0.98 Lts B= 0.99 Lts
CL4608 | 2024-06-01 | Kattupakkam | G | General inspection | Preventive | Suneel Sagar | 2024-06-01 | - | Dispensing motor alignment checked and outlet general check up done - Good condition
CL4609 | 2024-06-03 | Viruthachalam | D | Dispenser reading reverse | Breakdown | Pandi Durai | 2024-06-03 | - | Probem rectified by Automation team in back end with in 30 minutes. A Side = 21.140
CL4610 | 2024-06-03 | Namakkal 3 | R | FRL unit bowl damage. | Breakdown | Nivas | 2024-06-03 | - | New FRL unit assembly changed. Working in good condition.
CL4611 | 2024-06-03 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-06-03 | - | Redeem Litre- 54.55 L Amount Rs- 3153 Total No's of Redeem vehicle - 18 Auto- 14 Car-4 - Completed
CL4612 | 2024-06-03 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-03 | - | Redeem Litre- 11.09 L Amount Rs- 640 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL4613 | 2024-06-03 | Ariyamangalam | G | Mosquito problem | Preventive | Nepolean | 2024-06-03 | - | Mosquito repellent has been sprayed to control mosquito problem.
CL4614 | 2024-06-03 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-03 | - | Redeem Litre- 57.04 L Amount Rs- 3296 Total No's of Redeem vehicle - 19 Auto- 19 Car-0 - Completed
CL4615 | 2024-06-03 | Palladam 2 | T | Outlet C.P failure,reading comes below the average value (before -0.620 dcV). | Breakdown | Gowtham | 2024-07-09 | - | C.P problem rectified by cathotic protection re-build with new reference cell and anode 1.no. replaced. Now received adequate voltage after this. (-1.181 dcV).Work completed.
CL4616 | 2024-06-04 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-06-04 | - | Redeem Litre- 41.90 L Amount Rs- 2422 Total No's of Redeem vehicle - 13 Auto- 11 Car-2 - Completed
CL4617 | 2024-06-04 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-04 | - | Redeem Litre- 36.03 L Amount Rs- 2083 Total No's of Redeem vehicle - 14 Auto- 14 Car-0 - Completed
CL4618 | 2024-06-05 | T.V.Kovil | D | Dispenser A and B side nozzle hammer teeth worn out | Breakdown | Vigneshwaran | 2024-06-05 | - | Dispenser A and B side nozzle hammers 8 nos changed. A side nozzle front 'o ring' replaced. Totalizer "A" side =7426691.47 Totalizer "B" side =7667091.72
CL4619 | 2024-06-05 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-06-05 | - | Redeem Litre- 51.71 L Amount Rs- 2987 Total No's of Redeem vehicle - 14 Auto- 9 Car-05 - Completed
CL4620 | 2024-06-05 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-05 | - | Redeem Litre- 28.59 L Amount Rs- 1652 Total No's of Redeem vehicle - 8 Auto- 8 Car-0 - Completed
CL4621 | 2024-06-05 | Aravakuruchi | T | Outlet motor conductor(M1) activation problem. | Breakdown | Thirumalaisamy | 2024-06-05 | - | Motor conductor(M1) activation problem rectified by replaced with spare conductor. Working in good condition.-Work completed.
CL4622 | 2024-06-05 | Kattupakkam | T | Old motor servicing | Preventive | Suneel Sagar | 2024-06-05 | - | Old motor rewinding done and fixed with old pump - Alignment done - Kept ready for usage - Attended
CL4623 | 2024-06-06 | Attur | G | Fire extinguisher service and renewal work and training to pump staffs | Preventive | Nivas | 2024-06-06 | - | Fire extinguisher service and renewal work completed and training given to pump staffs
CL4624 | 2024-06-06 | Attur | G | Fire extinguisher maintenance | Preventive | Nivas | 2024-06-06 | - | In 75 kg both wheels,CO2 hoses(2kg) 2 nos replaced. In 9 kg DCP type replaced by ABC type - Attended
CL4625 | 2024-06-06 | Salem 2 | G | Outlet commissioning work | New project | Navaneetha Krishnan and Chandrasekar | 2024-06-09 | - | Commissioning work done - Attended
CL4626 | 2024-06-06 | Chinnasalem | G | Fire extinguisher service and renewal work and training to pump staffs | Preventive | Nivas | 2024-06-06 | - | Fire extinguisher service and renewal work completed and training given to pump staffs
CL4627 | 2024-06-06 | Viruthachalam | D | Dispenser "B" side low flow slow delivery and unloading vent pipeline dust problem. | Breakdown | Pandi Durai | 2024-06-06 | - | "B" side low flow delivery problem resolved by interchanging of high and low flow solenoid coil. Unloading vent pipeline rectified by cleaning of dust formed.Unloading and safety traiining given to pump staff. Working in good condition.-Work completed.
CL4628 | 2024-06-06 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-06-06 | - | Redeem Litre- 30.27 L Amount Rs- 1749 Total No's of Redeem vehicle - 9 Auto- 8 Car-1 - Completed
CL4629 | 2024-06-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-06 | - | Redeem Litre- 33.09 L Amount Rs- 1913 Total No's of Redeem vehicle - 12 Auto- 12 Car-0 - Completed
CL4630 | 2024-06-07 | Nasiyanur | T | Unloading training | Preventive | Avinash | 2024-06-07 | - | Unloading and operator training provided -Work completed.
CL4631 | 2024-06-07 | Ammapet | R | Compressor continuous running | Breakdown | Avinash | 2024-06-07 | - | Problem rectified by changing of damaged tank area dispensing line air hose with spare hose and N2 machine air filling problem rectified. Working in good condition.
CL4632 | 2024-06-07 | Dharapuram | G | Outlet printer not working | Breakdown | Gowtham | 2024-07-12 | - | Outlet printer serviced,installed and working in good condition.
CL4633 | 2024-06-07 | Villapuram | D | Dispenser "Off line" UPS push button not working. | Breakdown | Kathiresan | 2024-06-07 | - | Dispenser "Off line" UPS push button problem resolved by replacing of new one. Working in good condition.
CL4634 | 2024-06-07 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-07 | - | Redeem Litre- 47.71 L Amount Rs- 2756.66 Total No's of Redeem vehicle - 16 Auto- 14 Car-2 - Completed
CL4635 | 2024-06-07 | T.V.Kovil | D | Dispenser C side keypad not working. | Breakdown | Pandi Durai | 2024-06-07 | - | C side keypad problem rectified by changing of new one. Working in good condition.
CL4636 | 2024-06-07 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-06-07 | - | Redeem Litre- 15.33 L Amount Rs- 886 Total No's of Redeem vehicle - 7 Auto- 5 Car-2 - Completed
CL4637 | 2024-06-07 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-07 | - | Redeem Litre- 12.31 L Amount Rs- 710 Total No's of Redeem vehicle - 3 Auto- 2 Car-1 - Completed
CL4638 | 2024-06-08 | Devakottai | D | Control panel to dispenser air hose and control panel to main flang air hose defect. | Breakdown | Nepolean | 2024-06-08 | - | Control panel to dispenser air hose and control panel to main flange air hose probem resolved by changing of new one and air line fittings 6 nos changed.Compressor working in good condition. PMR work completed.
CL4639 | 2024-06-08 | Villapuram | D | Dipener "B" Side nozzle swivel mount leakage. | Breakdown | Kathiresan | 2024-06-08 | - | "B" Side nozzle Swivel mount leakage rectified by changing of new nozzle -Working in good condition.
CL4640 | 2024-06-08 | T.V.Kovil | G | ALDS and N2 both compressor oil -Check up | Preventive | Pandi Durai | 2024-06-08 | - | ALDS and N2 both compressor oil changed and totally checked. PMR completed.
CL4641 | 2024-06-08 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-08 | - | Redeem Litre- 27.51 L Amount Rs- 1590 Total No's of Redeem vehicle - 9 Auto- 9 Car-0 - Completed
CL4642 | 2024-06-08 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-06-08 | - | Redeem Litre- 16.95 L Amount Rs- 979 Total No's of Redeem vehicle - 4 Auto- 3 Car-1 - Completed
CL4643 | 2024-06-08 | Vellakoil | D | Outlet fuel flow reading jumping problem while filling full tank | Breakdown | Thirumalaisamy | 2024-06-08 | - | Fuel flow reading jumping problem is temporarely resolved by adjusting the valve in the equalizer line - Kept under observation
CL4644 | 2024-06-09 | Rasipuram | T | Unloading training | Preventive | Nivas | 2024-06-09 | - | Unloading and operator training provided -Work completed.
CL4645 | 2024-06-09 | Manapparai | R | Outlet control panel operator switch not working. | Breakdown | Nepolean | 2024-06-09 | - | Switch problem rectified by changing of new 1 Amp.fuse in control panel transformer.Working in good condition.-Work completed.
CL4646 | 2024-06-10 | Pudukkottai | G | Diesel generator oil service | Preventive | Nepolean | 2024-06-10 | - | Oil service completed and pump working in good condition.
CL4647 | 2024-06-10 | T.V.Kovil | A | Loyalty program redeem | Development | Suresh Kumar | 2024-06-10 | - | Redeem Litre- 15.42 L Amount Rs- 891 Total No's of Redeem vehicle - 5 Auto- 5 Car-0 - Completed
CL4648 | 2024-06-10 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-10 | - | Redeem Litre- 31.27 L Amount Rs- 1806 Total No's of Redeem vehicle - 9 Auto- 9 Car-0 - Completed
CL4649 | 2024-06-10 | Palayam | D | Dispenser B nozzle leakage | Breakdown | Thirumalaisamy | 2024-06-10 | - | B nozzle leakage arrested by changing of centre mount blue O ring.Working in good condition. Testing=1.10ltrs.
CL4650 | 2024-06-11 | Perundurai | R | Compressor continuous running | Breakdown | Avinash | 2024-06-11 | - | Compressor continuonus running resolved by changing of damaged outlet valve with new one and air leakage arrested.Working in good condition.
CL4651 | 2024-06-11 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-11 | - | Redeem Litre- 57.45 L Amount Rs- 3317.56 Total No's of Redeem vehicle - 16 Auto- 15 Car-1 - Completed
CL4652 | 2024-06-11 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-06-11 | - | Redeem Litre- 15.61 L Amount Rs- 902 Total No's of Redeem vehicle - 5 Auto- 5 Car-0 - Completed
CL4653 | 2024-06-11 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-06-11 | - | Redeem Litre- 11.39 L Amount Rs- 657.30 Total No's of Redeem vehicle - 2 Auto- 1 Car-1 - Completed
CL4654 | 2024-06-11 | Kumbakonam | D | Dispenser "B" side nozzle leakage. | Breakdown | Pandi Durai | 2024-06-11 | - | "B" side nozzle leakage arrested by changing with spare nozzle.Working in good condition. .B side testing = 0.91 ltr
CL4655 | 2024-06-11 | Thanjavur | R | Compressor continous running. | Breakdown | Pandi Durai | 2024-06-11 | - | Compressor continous running problem rectified by arresting of air leakage with changing of 2 nos of new master and dispensing solenoid coil.Working in good condition.
CL4656 | 2024-06-12 | Madurai-3(Pandikoil) | G | Outlet commissioning work | New project | Chandrasekar and Sureshkumar | 2024-06-14 | - | Commissioning work done - Attended
CL4657 | 2024-06-12 | T.V.Kovil | D | Dispenser B side nozzle damaged. | Breakdown | Vigneshwaran | 2024-06-12 | - | B side nozzle has been replaced by spare nozzle due to damage. Testing : B side :1.18 litre
CL4658 | 2024-06-12 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-12 | - | Redeem Litre- 2.25 L Amount Rs- 130 Total No's of Redeem vehicle - 1 Auto- 1 Car-0 - Completed
CL4659 | 2024-06-12 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-12 | - | Redeem Litre- 20.56 L Amount Rs- 1188 Total No's of Redeem vehicle - 8 Auto- 8 Car-0 - Completed
CL4660 | 2024-06-13 | Madurai-3(Pandikoil) | G | Outlet commissioning work | New project | Vigneshwaran | 2024-06-15 | - | Commissioning work done and Dispenser Calibration and Stamping Completed .
CL4661 | 2024-06-13 | Bodi | R | Outlet internet problem | Breakdown | Kamaraj | 2024-06-13 | - | Internet problem by hanging rectified through Automation team and system and camera return back to online.Pump general check up done.Working in good condition
CL4662 | 2024-06-13 | Cantonment | D | Dispenser A, C and D side nozzles problem. | Breakdown | Pandi Durai | 2024-06-13 | - | A, C and D side nozzles problem rectified by changing of 3 new nozzles.Working in good condition. A" side testing = 1.15 Ltr "C" side testing = 0.96 Ltr "D" side testing = 0.96 Ltr Total testing = 3.07 Ltr
CL4663 | 2024-06-13 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-13 | - | Redeem Litre- 7.97 L Amount Rs- 460 Total No's of Redeem vehicle - 3 Auto- 2 Car-1 - Completed
CL4664 | 2024-06-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-13 | - | Redeem Litre- 20.75 L Amount Rs- 1199 Total No's of Redeem vehicle - 6 Auto- 5 Car-1 - Completed
CL4665 | 2024-06-14 | T.V.Kovil | D | Outlet dispenser "B" side nozzle leakage. | Breakdown | Pandi Durai | 2024-06-14 | - | "B" side nozzle leakage arrested by changing of new spare one.Working in good condition. "B" side testing = 1.26 Ltr
CL4666 | 2024-06-14 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-14 | - | Redeem Litre- 4.51 L Amount Rs- 260 Total No's of Redeem vehicle - 2 Auto- 1 Car-1 - Completed
CL4667 | 2024-06-14 | T.V.Kovil | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-14 | - | Redeem Litre- 36.91 L Amount Rs- 2132 Total No's of Redeem vehicle - 8 Auto- 6 Car-2 - Completed
CL4668 | 2024-06-14 | Avadi | D | Dispensing motor spider problem. | Breakdown | Suneel Sagar | 2024-06-14 | - | PMR completed. Dispensing motor spider problem rectified by replacing of new one.Working in good condition.
CL4669 | 2024-06-14 | Salem 2 | C | Dispenser stamping and calibration work. | Certification | Prabu | 2024-06-14 | - | Stamping and calibration work completed.
CL4670 | 2024-06-14 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-14 | - | Redeem Litre- 32.45 L Amount Rs- 1876 Total No's of Redeem vehicle - 11 Auto- 9 Car-2 - Completed
CL4671 | 2024-06-14 | Madurai-3(Pandikoil) | G | Outlet commissioning work | New project | Kathiresan | 2024-06-14 | - | Outlet EB shifting, Automation testing and Pollards pipe painting work completed.
CL4672 | 2024-06-15 | Salem 2 | G | Dispenser opening reading . | New project | Prabu | 2024-06-15 | - | Dispenser opening reading 08/06/2024 night shift A side 344.60 B side 327.68 Tank 78%
CL4673 | 2024-06-15 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-06-15 | - | Redeem Litre- 16.66 L Amount Rs- 962.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-1 - Completed
CL4674 | 2024-06-15 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-15 | - | Redeem Litre- 29.36 L Amount Rs- 1697 Total No's of Redeem vehicle - 9 Auto- 9 Car-0 - Completed
CL4675 | 2024-06-15 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi Durai | 2024-06-15 | - | Redeem Litre- 4.16 L Amount Rs- 240 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL4676 | 2024-06-16 | Virudhachalam | R | Outlet offline ups back up issue and dispenser A side nozzle problem. | Breakdown | Pandi Durai | 2024-06-16 | - | Offline ups back up issue rectified by changing of new 12V 7AH battery and "A" side nozzle problem resolved by changing of damaged front 'O' ring. Working in good condition.
CL4677 | 2024-06-16 | Madurai-3(Pandikoil) | G | Outlet commissioning work | New project | Krishna Balaji | 2024-06-16 | - | Outlet PESO inspection has been completed and got approval to operate the station. Outlet opened to Public - Completed
CL4678 | 2024-06-17 | Theni | T | Unloading training | Preventive | Kamaraj | 2024-06-17 | - | Unloading and operator training provided -Work completed.
CL4679 | 2024-06-17 | Kattupakkam | G | PMR work | Preventive | Suneel Sagar | 2024-06-17 | - | PMR Completed
CL4680 | 2024-06-17 | Madurai-3(Pandikoil) | G | General outlet visit | Preventive | Kathiresan | 2024-06-17 | - | Outlet all equipments working in good condition. Total Testing - 11 ltrs
CL4681 | 2024-06-18 | Namakkal-3 | G | Outlet DG diesel tank outlet hose damaged. | Breakdown | Nivas | 2024-06-18 | - | DG diesel tank outlet damaged hose replaced by new one.Working in good condition.PMR completed,
CL4682 | 2024-06-18 | Madurai Villapuram | G | Outlet fire extinguisher renewal and service and opreating training for pump staffs. | Preventive | Kathiresan | 2024-06-25 | - | Fire extinguisher renewal and service's done and 75 kg fire extinguisher-2 nos new DCP powder changed. Fire extinguisher opreating training given to pump Staffs.Work completed.
CL4683 | 2024-06-18 | Madurai Ellis nagar | G | Outlet fire extinguisher renewal and service and opreating training for pump staffs. | Preventive | Kathiresan | 2024-06-18 | - | Fire extinguisher renewal and service's done. Fire extinguisher opreating training given to pump Staffs.
CL4684 | 2024-06-19 | Ariyamangalam | R | E.B power problem and running in DG mode | Breakdown | Nepolean | 2024-06-19 | - | E. B power problem-one phase low voltage rectified.Pump running in E.B mode.Working in good condition.
CL4685 | 2024-06-19 | Ariyamangalam | G | Outlet Compressor problem | Breakdown | Nepolean | 2024-06-21 | - | Comprosser oil service work completed.Working in good condition
CL4686 | 2024-06-19 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-19 | - | Redeem Litre- 41.87 L Amount Rs- 2419 Total No's of Redeem vehicle - 12 Auto- 12 Car-0 - Completed
CL4687 | 2024-06-19 | Madurai Ellis nagar | T | Outlet tank 1 dispensing liquid line LPG leakage and oil dispenser flow meter problem. | Breakdown | Kathiresan | 2024-06-19 | - | Station Tank 1 dispensing Liquid line LPG leakage arrested by tightening the nuts and oil dispenser flow meter problem rectified by cleaning the flow meter.Working in good condition. Oil dispenser testing - 3.10 ltrs
CL4688 | 2024-06-20 | Ariyamangalam | D | Outlet D side pump1 nozzle service. | Preventive | Nepolean | 2024-06-20 | - | D side pump1 old 3 nozzles serviced and tested.Working in good condition.
CL4689 | 2024-06-20 | Ariyamangalam | D | Outlet pump D side testing work. | Preventive | Nepolean | 2024-06-20 | - | D side testing work.Working in good condition. Testing : 3.13 lit
CL4690 | 2024-06-20 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-20 | - | Redeem Litre- 41.83 L Amount Rs- 2416 Total No's of Redeem vehicle - 10 Auto- 9 Car-1 - Completed
CL4691 | 2024-06-20 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-06-20 | - | Redeem Litre- 6.59 L Amount Rs- 380 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL4692 | 2024-06-20 | Chengalpattu | R | Outlet online ups problem. | Breakdown | Suneel Sagar | 2024-06-20 | - | Online ups problem resolved by replacing of 2 batteries and general inspection has done.Working in good condition.
CL4693 | 2024-06-21 | Ariyamangalam | D | Dispenser D side kumbakonam nozzle service work. | Preventive | Nepolean | 2024-06-21 | - | D side kumbakonam nozzle service work completed.Working in good condition. . D side Testing : 3.80lit.
CL4694 | 2024-06-21 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-06-21 | - | Redeem Litre- 2.87 L Amount Rs- 166 Total No's of Redeem vehicle - 1 Auto- 1 Car-0 - Completed
CL4695 | 2024-06-21 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-21 | - | Redeem Litre- 11.31 L Amount Rs- 654 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4696 | 2024-06-22 | Pudukkottai | G | Outlet D.G Service work | Preventive | Nepolean | 2024-06-22 | - | D.G service work completed. Working in good condition.
CL4697 | 2024-06-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-22 | - | Redeem Litre- 49.01 L Amount Rs- 2832 Total No's of Redeem vehicle - 12 Auto- 12 Car-0 - Completed
CL4698 | 2024-06-22 | Eral | D | Dispensing line air hose damaged.On line "UPS" push button,pneumatic fittings and dispenser " A" side key pad problem. | Breakdown | Kathiresan | 2024-06-22 | - | Dispensing line damaged air hose 36 mtrs changed. On line "UPS" push Button replaced and all pneumatic fittings changed. PMR completed. " A" side key pad to be replaced. Work completed Reports; CP value = - 1.24 Earth. = 0.8 (v) Amps. = 8.95,6.68,7.08.
CL4699 | 2024-06-23 | Musiri | D | Dispenser A side fueling problem | Breakdown | Nivas | 2024-06-22 | - | A side fueling problem rectified by replacing the damaged solenoid coil fuse by new one.Working in good condition.
CL4700 | 2024-06-23 | Tiruchengode | D | Dispenser A side jumping problem. | Breakdown | Avinash | 2024-06-23 | - | A side jumping problem resolved by replacing of damaged outer area DP value teflon membrane by new one. Working in good condition. Testing = 1.78 Lts. .
CL4701 | 2024-06-24 | Bhavani | T | Outlet unloading DOL starter problem. | Breakdown | Avinash | 2024-06-24 | - | Unloading DOL starter problem rectified by changing of damaged signal wire and CP Signal wire has been used for unloading. DOL starter works fine.Work completed.
CL4702 | 2024-06-24 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-06-24 | - | Redeem Litre- 13.35 L Amount Rs- 770 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4703 | 2024-06-24 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-24 | - | Redeem Litre- 11.12 L Amount Rs- 643 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4704 | 2024-06-24 | Vadivelan nagar | C | PMR work | Certification | Suneel Sagar | 2024-06-24 | - | PMR completed
CL4705 | 2024-06-25 | Perambalur | T | Outlet unloading area fill point vapour & liquid line ROV closing problem . Tank side unloading liquid line ROV opening & closing problem. | Breakdown | Pandidurai | 2024-07-22 | - | Unloading area fill point vapour & liquid line ROV closing problem rectified by cleaning of dust formed and tank side.Unloading liquid line service ROV 1 no fitted after servicing from H.O.Working in good condition.Unloading training given to pump staffs and PMR also completed.Work completed.
CL4706 | 2024-06-25 | Avinashi | D | Dispenser B side metering unit leakage and B side metering unit is worning out. | Breakdown | Gowtham | 2024-06-25 | - | Dispenser B side metering unit leakage arrested by replacing of seal kit and dispenser B side metering unit is worning rectified. Testing ltr- 61.75 ltr.
CL4707 | 2024-06-25 | T.V.Kovil | D | Dispenser B side nozzle switch and air machine tyre inflator problem. | Breakdown | Vigneshwaran | 2024-06-25 | - | Dispenser B side nozzle switch and air machine tyre inflator changed.Working in good condition.
CL4708 | 2024-06-25 | Ariyamangalam | R | Online UPS problem, | Breakdown | Nepolean | 2024-06-25 | - | Online UPS problem resolved by replacing of new UPS. Working in good condition.
CL4709 | 2024-06-25 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-25 | - | Redeem Litre- 18.86 L Amount Rs- 1091 Total No's of Redeem vehicle - 8 Auto- 7 Car-1 - Completed
CL4710 | 2024-06-26 | Rasipuram | T | Dispensing vapour ROV air leakage problem. | Breakdown | Nivas | 2024-06-26 | - | Dispensing vapour ROV air leakage rectified by interchanging of unloading vapour ROV.All leak checked. PMR completed.
CL4711 | 2024-06-26 | Paramathi velur | C | Calibration and stamping work. | Certification | Thirumalaisamy and Vigneshwaran | 2024-06-26 | - | Calibration and stamping completed. Calibration Report : A Side 10 ltrs = 9.98 B Side 10 ltrs = 9.98 K Factor Report : K factor no changes A Side K factor = 10000 B Side K factor = 10000 Testing Report ; A Side = 148.45ltrs B Side = 156.25ltrs Total = 304.70ltrs.
CL4712 | 2024-06-26 | Palladam 1 | D | Batchen dispenser the both pipelines were blocked and its electrical, automation connections also problem. | Breakdown | Gowtham | 2024-06-26 | - | Here after only Yenen dispenser will be in service.
CL4713 | 2024-06-26 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-26 | - | Redeem Litre- 8.64 L Amount Rs- 500 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL4714 | 2024-06-27 | Theni | D | Dispensing motor love jay coupling and spider problem. | Breakdown | Kamaraj | 2024-06-27 | - | Dispensing motor love jay coupling chenged and spider replaced by new one.General checkup done.Working in good condition.
CL4715 | 2024-06-27 | Salem 2 | T | Outlet unloading work. | Preventive | Prabu | 2024-06-27 | - | Unloading completed. HLA and ATG 85% cut-off working condition normal.
CL4716 | 2024-06-27 | Kodungaiyur | C | PMR work. | Certification | Suneel Sagar | 2024-06-27 | - | PMR work completed.
CL4717 | 2024-06-27 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-27 | - | Redeem Litre- 30.19 L Amount Rs- 1745 Total No's of Redeem vehicle - 9 Auto- 8 Car-1 - Completed
CL4718 | 2024-06-28 | Palayam | C | Calibration and stamping work. | Certification | Thirumalaisamy and Vigneshwaran | 2024-06-28 | - | Calibration and stamping completed. Calibration Report : A Side 10 ltrs = 10.01 B Side 10 ltrs = 9.98 K Factor Report : K factor no changes A Side K factor = 10000 B Side K factor = 10010 Testing Report ; A Side = 153.88 ltrs B Side = 152.07 ltrs Total = 305.95 ltrs.
CL4719 | 2024-06-28 | Devakottai | G | Outlet camara cable line problem. | Breakdown | Nepolean | 2024-06-28 | - | Camara cable line problem rectified and despenser area all cable champer pip seal applied. All camara line working in good condition.Staff training given to pump operator and pump staffs.Work completed.
CL4720 | 2024-06-28 | Madurai-3(Pandikoil) | T | Outlet unloading. | Preventive | Kathiresan | 2024-06-28 | - | Unloading completed. Tank area leakage tested.Work completed. ATG cut off working 84% .
CL4721 | 2024-06-28 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-28 | - | Redeem Litre- 20.82 L Amount Rs- 1203 Total No's of Redeem vehicle - 7 Auto- 7 Car-0 - Completed
CL4722 | 2024-06-28 | Thiruvaiyaru | A | Redeem bill updation done. | Development | Pandithurai | 2024-06-28 | - | Updation completed. Outlet testing liters. A Nozzle - 12.11 ltr Total testing - 12.11 ltr
CL4723 | 2024-06-29 | Krishnagiri | R | Outlet system CPU heating problem. | Breakdown | Prabu | 2024-06-29 | - | System CPU heating issue resolved by changing with spare CPU. Automation maintenance done.Work completed.
CL4724 | 2024-06-29 | Dharmapuri | R | Outlet EB line main MCB and control panel indicator problem. | Breakdown | Prabu | 2024-06-29 | - | EB line main MCB 1 number and control panel indicator light 3 nos changed.Work completed.
CL4725 | 2024-06-29 | Thuraiyur | R | Outlet CPU heating issue. | Breakdown | Nivas | 2024-06-29 | - | Outlet CPU heating issue resolved by cleaning the CPU. Automation maintenance done.All leakage tested . PMR also completed.
CL4726 | 2024-06-29 | Kodumudi | G | Outlet hikvision camera hard drive problem. | Breakdown | Thirumalaisamy | 2024-06-29 | - | Hikvision camera hard drive serviced and working in normal.
CL4727 | 2024-06-29 | Thanjavur | A | Redeem bill updation. | Development | Pandithurai | 2024-06-29 | - | Redeem bill updation completed
CL4728 | 2024-06-29 | Kumbakonam | A | Redeem bill updation. | Development | Pandithurai | 2024-06-29 | - | Redeem bill updation completed
CL4729 | 2024-06-29 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-06-29 | - | Redeem Litre- 17.49 L Amount Rs- 1010 Total No's of Redeem vehicle - 5 Auto- 4 Car-1 - Completed
CL4730 | 2024-06-30 | Sulur | R | Outlet compressor continuous running problem. | Breakdown | Gowtham | 2024-06-30 | - | Compressor continuous running problem resolved by replacing of damaged dispenser air hose with new one and dispensing solenoid valve replaced by new one.Compressor working in normal.Work completed.
CL4731 | 2024-06-30 | Perambalur | A | Redeem bill updation. | Development | Pandithurai | 2024-06-30 | - | Redeem bill updation completed
CL4732 | 2024-07-01 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-01 | - | Redeem Litre- 11.74 L Amount Rs- 668.02 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4733 | 2024-07-02 | Namakkal 1 | T | Outlet unloading and unloading training. | Preventive | Nivas | 2024-07-02 | - | Unloading completed and training given to pump staff.
CL4734 | 2024-07-02 | Thuraiyur | A | Redeem bill updation. | Development | Nivas | 2024-07-03 | - | Redeem bill updation completed
CL4735 | 2024-07-02 | Pudukkottai | A | Redeem bill updation. | Development | Pandidurai | 2024-07-02 | - | Redeem bill updation completed
CL4736 | 2024-07-02 | Manapparai | A | Redeem bill updation. | Development | Pandidurai | 2024-07-02 | - | Redeem bill updation completed
CL4737 | 2024-07-02 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-02 | - | Redeem Litre- 6.46 L Amount Rs- 368 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL4738 | 2024-07-03 | Musiri | A | Redeem bill updation. | Development | Nivas | 2024-07-03 | - | Redeem bill updation and PMR completed
CL4739 | 2024-07-03 | Ariyalur | A | Redeem bill updation. | Development | Pandidurai | 2024-07-03 | - | Redeem bill updation completed
CL4740 | 2024-07-03 | Virudhachalam | A | Redeem bill updation. | Development | Pandidurai | 2024-07-03 | - | Redeem bill updation completed
CL4741 | 2024-07-03 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-03 | - | Redeem Litre- 39.20 L Amount Rs- 2231 Total No's of Redeem vehicle - 13 Auto- 11 Car-2 - Completed
CL4742 | 2024-07-03 | Madurai Villapuram | D | Outlet dispensing motor problem. | Breakdown | Kathiresan | 2024-07-03 | - | Dispensing motor problem resolved by re-alignment.Now running under normal vibration and sound.Work completed.
CL4743 | 2024-07-03 | Kattupakkam | T | Outlet tank 1 unloding vapour ROV problem. | Breakdown | Suneel Sagar | 2024-07-03 | - | Tank 1 unloding vapour ROV problem rectified by replacing of new one.Working in good condition.
CL4744 | 2024-07-04 | Krishnagiri | D | Outlet dispensing motor cable line and EB to DG changeover in & out stabilizer in &out cable problem. | Breakdown | Prabu | 2024-07-04 | - | The problem rectified by changing of dispensing motor cable line and EB to DG changeover in & out stabilizer in & out cable.New changeover 1 no's changed.Working in good condition.PMR done.
CL4745 | 2024-07-04 | Namakkal 2 | T | Outlet unloading area fill point liquid line problem. | Breakdown | Nivas | 2024-07-04 | - | Unloading area fill point liquid line resolved by servicing and fixing of ROV. N2 Compressor oil changed.Working in good condition. PMR completed.
CL4746 | 2024-07-04 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-04 | - | Redeem Litre- 12.37 L Amount Rs- 704 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4747 | 2024-07-05 | Chinnasalem | C | Calibration and stamping work. | Certification | Chandrasekar and Pandidurai | 2024-07-05 | - | Calibration and stamping completed. Calibration Report : A Side 10 ltrs = 9.95 B Side 10 ltrs = 9.95 K Factor Report : K factor no changes A Side K factor = 10000 B Side K factor = 10010 Testing Report ; A Side = 152.45 ltrs B Side = 152.69 ltrs Total = 305.14 ltrs. General check up done and total leakage checked. PMR also completed.
CL4748 | 2024-07-05 | Bodi | R | Outlet online ups input power supply filter board and battery pack up problem.Automatiom Cisco switch fault. | Breakdown | Kamaraj and Kathiresan | 2024-07-12 | - | Online ups input power supply filter board short circuit due to power fluctuations and battery pack up problem.Problem resolved.Pump working in online.
CL4749 | 2024-07-05 | Rasipuram | D | Outlet dispensing motor cooling fan damaged. | Breakdown | Nivas | 2024-07-05 | - | The damaged dispensing motor cooling fan replaced by new one.Working fine.and kept under observation. Damaged unloading tanker earth clip changed by new one.
CL4750 | 2024-07-05 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-05 | - | Redeem Litre- 14.78 L Amount Rs- 840 Total No's of Redeem vehicle - 3 Auto- 1 Car-2 - Completed
CL4751 | 2024-07-05 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-05 | - | Redeem Litre- 9.55 L Amount Rs- 544 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL4752 | 2024-07-05 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-05 | - | Redeem Litre- 14.78 L Amount Rs- 840 Total No's of Redeem vehicle - 3 Auto- 1 Car-2 - Completed
CL4753 | 2024-07-06 | Perundurai | G | Outlet Infonet internet problem. | Breakdown | Avinash | 2024-07-06 | - | Infonet internet problem resolved by changing of new fiber net connection. working fine
CL4754 | 2024-07-06 | Erode | R | Outlet genset problem. | Breakdown | Avinash | 2024-07-06 | - | Genset oil and diesel filter changed by new one and general service done by service person.Genset working in good condition.
CL4755 | 2024-07-06 | Madurai Ellis nagar | D | Dispenser "C" side leakage problem. | Breakdown | Kathiresan | 2024-07-06 | - | "C" side leakage arrested by changing of spare nozzle. Testing = 0.92 lit
CL4756 | 2024-07-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-06 | - | Redeem Litre- 14.62 L Amount Rs- 832 Total No's of Redeem vehicle - 5 Auto- 5 Car-0 - Completed
CL4757 | 2024-07-08 | Udumalpet | D | Outlet Yenen dispenser reading reverse problem. | Breakdown | Gowtham | 2024-07-08 | - | Dispenser reading reverse problem due to power cut and ups battery power drain. Now working normal and back to online Reverse Reading details: D - 125.730 ltr C - 98.110 ltr
CL4758 | 2024-07-08 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-08 | - | Redeem Litre- 21.59 L Amount Rs- 1228 Total No's of Redeem vehicle - 6 Auto- 6 Car-0 - Completed
CL4759 | 2024-07-09 | T.V.Kovil | D | Dispenser C side LPG 5m hose Damaged. | Breakdown | Nepolean | 2024-07-09 | - | C side LPG 5m hose replaced by new one.Working in good condition. C side testing: 0.83 lit.
CL4760 | 2024-07-09 | Ariyamangalam | D | Dispenser B side nozzle LPG 5 m hose damaged. | Breakdown | Nepolean | 2024-07-09 | - | B side nozzle LPG 5 m hose replaced by new one.Working in good condition. B side testing : 1.06 lit.
CL4761 | 2024-07-09 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-09 | - | Redeem Litre- 5.63 L Amount Rs- 320 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL4762 | 2024-07-09 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-09 | - | Redeem Litre- 33.76 L Amount Rs- 1919 Total No's of Redeem vehicle - 7 Auto- 6 Car-1 - Completed
CL4763 | 2024-07-09 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-09 | - | Redeem Litre- 7.29 L Amount Rs- 415 Total No's of Redeem vehicle - 2 Auto- 1 Car-1 - Completed
CL4764 | 2024-07-09 | Dharmapuri | R | Outlet stabilizer output high problem. | Breakdown | Prabu | 2024-07-09 | - | Stabilizer output high problem resolved by changing of stabilizer inside carbon brush and limit switch.Working in good condition. Stabilizer output leakage checked.PMR done.Work completed.
CL4765 | 2024-07-10 | Kumbakonam | D | Outlet dispenser "B" side keypad and EB room to dispenser air line hose damaged. | Breakdown | Pandidurai | 2024-07-10 | - | "B" side 1 no new keypad changed and damaged air lne hose from EB room to dispenser replaced by new one. 2 nos of new canopy light installed. Total all leakage checked and PMR also completed.
CL4766 | 2024-07-10 | Madurai-Villapuram | C | Calibration and stamping work | Certification | Vigneshwaran | 2024-07-10 | - | Calibration and stamping work completed.
CL4767 | 2024-07-10 | Hosur | G | New office shifting work | Preventive | Prabu and Chandrasekar | 2024-07-10 | - | New office shifting work unrer progress.
CL4768 | 2024-07-10 | Dharapuram | A | Outlet going offline. | Breakdown | Gowtham | 2024-07-10 | - | Dispenser readings: A nozzle - 178416.25 B nozzle - 170019.35 Outlet back online. PMR completed.
CL4769 | 2024-07-10 | Kodungaiyur | G | Truck Audit | Preventive | Suneel Sagar and Navaneethakrishnan | 2024-07-10 | - | Truck Audit completed. Truck No: TN45BS6067
CL4770 | 2024-07-10 | Vadivelan nagar | G | Truck Audit | Preventive | Suneel Sagar and Navaneethakrishnan | 2024-07-10 | - | Truck Audit completed. Truck No:TN45BR1767.
CL4771 | 2024-07-10 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-10 | - | Redeem Litre- 16.07 L Amount Rs- 915 Total No's of Redeem vehicle - 6 Auto- 6 Car-0 - Completed
CL4772 | 2024-07-11 | Madurai-Villapuram | G | Outlet near EB post working. | Breakdown | Kathiresan | 2024-07-11 | 2 hours only. | E.B work completed and outlet sales started.
CL4773 | 2024-07-11 | T.V.Kovil | G | Fire extinguisher service work. | Preventive | Nepolean | 2024-07-11 | - | Fire extinguisher service work completed and got renewal certificate.
CL4774 | 2024-07-11 | Madurai Ellis nagar | C | Calibration and stamping work | Certification | Kathiresan | 2024-07-11 | - | Calibration and stamping completed. Calibration Report : A Side 10 ltrs = 9.98 B Side 10 ltrs = 9.98 C Side 10 ltrs = 9.97 D Side 10 ltrs = 9.99 K Factor Report : A Side = 10000 B Side = 10000 C Side = 10000 D Side =10000 Testing Report ; A Side = 105.60 ltrs B Side = 108.12 ltrs C Side = 107.26 ltrs D Side = 187.00 ltrs Total = 507.98 ltrs.
CL4775 | 2024-07-11 | Madurai-Villapuram | C | Calibration and stamping work | Certification | Kathiresan | 2024-07-11 | - | Calibration and stamping completed. Calibration Report : A Side 10 ltrs = 10.05 B Side 10 ltrs = 10.02 C Side 10 ltrs = 10.03 D Side 10 ltrs = 9.95 K Factor Report : A Side = 10000 B Side = 10000 C Side = 10300 D Side = 10150 Testing Report ; A Side = 442.63 ltrs B Side = 165.12 ltrs C Side = 138.72 ltrs D Side = 150.17 ltrs Total = 896.64 ltrs.
CL4776 | 2024-07-11 | Melur | C | Calibration and stamping work | Certification | Kathiresan | 2024-07-11 | - | Calibration and stamping completed. Calibration Report : A Side 10 ltrs = 9.90 B Side 10 ltrs = 9.90 K Factor Report : A Side = 10180 B Side = 10180 Testing Report ; A Side = 119.84 ltrs B Side = 124.65 ltrs Total = 244.49 ltrs.
CL4777 | 2024-07-11 | Namakkal 1 | G | PMR work | Preventive | Nivas | 2024-07-11 | - | PMR completed.
CL4778 | 2024-07-11 | Ariyamangalam | R | Outlet online ups change. | Breakdown | Nepolean | 2024-07-11 | - | Old serviced online ups( Numeric HP 1000) one changed and working condition normal and kept under under observation for one week..
CL4779 | 2024-07-11 | Madurai Ellis nagar | D | Outlet "A" Side DP valve damage. | Breakdown | Kathiresan | 2024-07-11 | - | The damaged "A" Side DP valve diaphragm changed. Working in good condition. Testing - 5 ltrs.
CL4780 | 2024-07-11 | Chengalpattu | G | Truck Audit | Preventive | Suneel Sagar and Navaneethakrishnan | 2024-07-11 | - | Truck Audit completed. Truck No: TN45BS5167.
CL4781 | 2024-07-11 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-11 | - | Redeem Litre- 13.79 L Amount Rs- 785 Total No's of Redeem vehicle - 5 Auto- 5 Car-0 - Completed
CL4782 | 2024-07-12 | Bodi | R | Outlet online UPS input power supply problem. | Breakdown | Kamaraj | 2024-07-12 | - | Online UPS input power supply resolved by replacing of new filter board and changing of 3 nos of 12 volt 7AH battery.Back up time 15 minutes. Working in good condition. PMR also completed.
CL4783 | 2024-07-12 | Madurai Ellis nagar | D | Outlet "C" side breakaway problem. | Breakdown | Kathiresan | 2024-07-12 | - | "C" side breakaway removed by refitting.Working in good condition. Testing- 0.88ltrs.
CL4784 | 2024-07-12 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-12 | - | Redeem Litre- 14.35 L Amount Rs- 816.40 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL4785 | 2024-07-13 | Ariyamangalam | R | Outlet power problem due to servo stabilizer servo mode problem ( Low voltage). | Breakdown | Nepolean | 2024-07-13 | - | Power problem rectified by replacing with new servo stablizer.Working in good condition. A side testing : 10.91.
CL4786 | 2024-07-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-13 | - | Redeem Litre- 8.34 L Amount Rs- 474.00 Total No's of Redeem vehicle - 1 Auto- 0 Car-1 - Completed
CL4787 | 2024-07-15 | Tirunelveli | T | Outlet control panel tank 1 HLA card and D side LPG hose damaged. | Breakdown | Kathiresan | 2024-07-15 | - | Control panel tank 1 HLA card replaced with new one and "D" Side 5 mtrs LPG hose changed and nozzle 2 nos serviced. Working in good condition. Tank 2 "STB motor" line LPG leakage arrested by tighting the nuts. PMR also done. CP value : Tank 1= -1.22 Tank 2 = -1.19 Earth value = 1.2(v)
CL4788 | 2024-07-15 | Hosur | G | Site office shifing work | Preventive | Prakash and Chandrasekar | 2024-07-15 | - | Site office shifing work completed.
CL4789 | 2024-07-15 | Avadi | D | Outlet dispensing nozzle came out from filler valve. | Breakdown | Suneel Sagar | 2024-07-15 | - | Dispensing nozzle came out from filler valve due to it is non standard and pump boy found LPG leakage,dispenser emergency switch activated immediately.Filler valve refixed promptly. Work completed.
CL4790 | 2024-07-15 | Cantonment | D | Outlet B side nozzle problem. | Breakdown | Lingeshwaran | 2024-07-15 | - | B side nozzle problem resolved by replacing of 4 nos of new one.Working in good condition.
CL4791 | 2024-07-15 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-15 | - | Redeem Litre- 527.09 L Amount Rs- 29983.89 Total No's of Redeem vehicle - 141 Auto- 135 Car-6 - Completed
CL4792 | 2024-07-15 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-15 | - | Redeem Litre- 111.41 L Amount Rs- 6330.00 Total No's of Redeem vehicle - 30 Auto- 29 Car-1 - Completed
CL4793 | 2024-07-15 | Ariyamangalam | D | Outletd dispenser 1 light problem. | Breakdown | Nepolean | 2024-07-15 | - | Dispenser 1 light problem resolved by changing of new 5 w light one number.Working in good condition.
CL4794 | 2024-07-15 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-15 | - | Redeem Litre- 197.13 L Amount Rs- 11215.19 Total No's of Redeem vehicle - 58 Auto- 58 Car-0 - Completed
CL4795 | 2024-07-16 | Madurai Villapuram | D | Outlet dispenser C side nozzle and offline UPS problem. | Breakdown | Kathiresan | 2024-07-16 | - | C side spare nozzle changed due to leakage. Then off line back up and power drop problem rectified by replacing of UPS battery 12(v) 7 Ah two numbers.Work completed.
CL4796 | 2024-07-16 | Salem 2 | G | PESO inspection | Development | Prabu | 2024-07-16 | - | PESO inspection completed
CL4797 | 2024-07-16 | Kinathukadavu | T | Outlet tank installation work. | New project | Gowtham | 2024-07-16 | - | Outlet tank installation work completed with application of gasket and coal thaar paint.Work completed.
CL4798 | 2024-07-16 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-16 | - | Redeem Litre- 236.57 L Amount Rs- 13441.20 Total No's of Redeem vehicle - 59 Auto- 56 Car-03 - Completed
CL4799 | 2024-07-16 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-16 | - | Redeem Litre- 650.41 L Amount Rs- 36989.00 Total No's of Redeem vehicle - 151 Auto- 146 Car-05 - Completed
CL4800 | 2024-07-16 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-16 | - | Redeem Litre- 245.14 L Amount Rs- 13945.78 Total No's of Redeem vehicle - 64 Auto- 64 Car-0 - Completed
CL4801 | 2024-07-17 | Madurai-3(Pandikoil) | R | Outlet compressor starter and water dispenser problem. | Breakdown | Kathiresan | 2024-07-17 | - | Compressor 415(v) new starter replaced (Warranty Period) due to started automatically in sometimes. New water dispenser installed.
CL4802 | 2024-07-17 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-17 | - | Redeem Litre- 196.07 L Amount Rs- 11139.50 Total No's of Redeem vehicle - 50 Auto- 47 Car-03 - Completed
CL4803 | 2024-07-17 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-17 | - | Redeem Litre- 406.59 L Amount Rs- 23124.00 Total No's of Redeem vehicle - 100 Auto- 90 Car-10 - Completed
CL4804 | 2024-07-17 | Ariyamangalam | G | Fire extinguisher service and renewal work. | Preventive | Nepolean | 2024-07-17 | - | Fire extinguisher service and renewal work completed.
CL4805 | 2024-07-17 | Kinathukadavu | T | Outlet concrete work in tank and canopy pillars. | New project | Gowtham | 2024-07-17 | - | Concrete pouring work done in tank and canopy piller foundation.Work completed.
CL4806 | 2024-07-17 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-17 | - | Redeem Litre- 772.59 L Amount Rs- 43937.11 Total No's of Redeem vehicle - 188 Auto- 184 Car-04 - Completed
CL4807 | 2024-07-18 | Ariyamangalam | R | Outlet old servo stabilizer problem. | Breakdown | Nepolean | 2024-07-20 | - | Old servo stablizer problem is rectified. R phase new reversible synchronous motor one no and carbon 3 nos changed.New leg 4 sq mm 10 nos changed. Motor input voltage : 220v and speed 60 RPM. Servo stablizer working condition normal and kept for 2 days under observation.
CL4808 | 2024-07-18 | Avinashi | D | Outlet nozzle servicing & PMR work. | Preventive | Gowtham | 2024-07-18 | - | Nozzle 1 no. serviced and PMR completed.
CL4809 | 2024-07-18 | Madurai Villapuram | G | Outlet genset maintenance and battery leg problem. | Breakdown | Kathiresan | 2024-07-18 | - | Genset maintenance done by changing of engine oil and filter.Then battery leg 2 nos changed.Working in good condition.
CL4810 | 2024-07-18 | T.V.Kovil | A | Loyalty program redeem | Development | Sureshkumar | 2024-07-18 | - | Redeem Litre- 455.64 L Amount Rs- 25918.13 Total No's of Redeem vehicle - 115 Auto- 107 Car-08 - Completed
CL4811 | 2024-07-18 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-18 | - | Redeem Litre- 159.20 L Amount Rs- 9045.50 Total No's of Redeem vehicle - 37 Auto- 33 Car-04 - Completed
CL4812 | 2024-07-18 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-18 | - | Redeem Litre- 382.21 L Amount Rs- 21740.07 Total No's of Redeem vehicle - 91 Auto- 90 Car-01 - Completed
CL4813 | 2024-07-19 | Sulur | D | Outlet B side dispensing hose damage. | Breakdown | Gowtham | 2024-07-26 | - | The damaged B side dispensing hose reinstalled after recrimp work and the old hose removed and kept. Air machine compressor belt replaced.Work completed.
CL4814 | 2024-07-19 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-19 | - | Redeem Litre- 277.69 L Amount Rs- 15797.00 Total No's of Redeem vehicle - 70 Auto- 65 Car-05 - Completed
CL4815 | 2024-07-19 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-19 | - | Redeem Litre- 278.92 L Amount Rs- 15865.13 Total No's of Redeem vehicle - 73 Auto- 71 Car-02 - Completed
CL4816 | 2024-07-19 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-19 | - | Redeem Litre- 70.51 L Amount Rs- 4006.10 Total No's of Redeem vehicle - 21 Auto- 19 Car-02 - Completed
CL4817 | 2024-07-20 | Kinathukadavu | T | Kinathukadavu outlet tank hydro test. | New project | Chandrasekar,Gowtham and Sureshkumar | 2024-07-20 | - | Outlet tank hydro test completed.Testing pressure 29 kg cm'2.The bed marking for dispensing and decanting motor completed.
CL4818 | 2024-07-20 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-20 | - | Redeem Litre- 163.81 L Amount Rs- 9315.27 Total No's of Redeem vehicle - 33 Auto- 29 Car-04 - Completed
CL4819 | 2024-07-20 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-20 | - | Redeem Litre- 319.95 L Amount Rs- 18198.94 Total No's of Redeem vehicle - 78 Auto- 74 Car-04 - Completed
CL4820 | 2024-07-20 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-20 | - | Redeem Litre- 32.58 L Amount Rs- 1850.00 Total No's of Redeem vehicle - 10 Auto- 09 Car-01 - Completed
CL4821 | 2024-07-20 | Ayothiyapattinam | T | Outlet unloading liquid line ROV inside leakage problem. | Breakdown | Prabu | 2024-07-20 | - | Unloading liquid line ROV inside leakage problem rectified by cleaning and tightaning the screws. PMR completed.
CL4822 | 2024-07-21 | Tharamangalam | R | Outlet stabilizer inside sparking and wire melting and stabilizer input MCB trip problem. | Breakdown | Prabu | 2024-07-25 | 1 Hour | Outlet stabilizer round electronic dimmer stat 1 no's changed and stabilizer mode working condition. Output R 230 Y 231 B 230 voltage.
CL4823 | 2024-07-22 | Perambalur | D | Outlet "B" side nozzle leakage problem | Breakdown | Pandidurai | 2024-07-22 | - | "B" side nozzle leakage problem rectified by changing 4 nos of hammer teeths.
CL4824 | 2024-07-22 | Ariyamangalam | R | Online ups battery problem, | Breakdown | Nepolean | 2024-07-22 | - | Online UPS problem resolved by changing of new battery 3 nos(12 v / 42 ah exide).Working in good condition.
CL4825 | 2024-07-22 | Madurai Ellis nagar | D | Outlet D side "New nozzle" changed. | Preventive | Kathiresan | 2024-07-22 | - | D side new nozzle changed due to it runs more than 9.40000 lakhs ltrs.Outlet compressor and air compressors oil changed. Working in good condition. Testing = 0.85ltrs
CL4826 | 2024-07-22 | Vadivelan nagar | D | Outlet C side nozzle problem. | Breakdown | Suneel Sagar | 2024-07-22 | - | C side nozzle problem rectified by replaced by new one. Testing 0.91 ltrs.
CL4827 | 2024-07-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-22 | - | Redeem Litre- 147.01 L Amount Rs- 8364.00 Total No's of Redeem vehicle - 42 Auto- 41 Car-01 - Completed
CL4828 | 2024-07-22 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-22 | - | Redeem Litre- 212.31 L Amount Rs- 12076.99 Total No's of Redeem vehicle - 52 Auto- 45 Car-07 - Completed
CL4829 | 2024-07-22 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-22 | - | Redeem Litre- 87.68 L Amount Rs- 4980.50 Total No's of Redeem vehicle - 24 Auto- 21 Car-03 - Completed
CL4830 | 2024-07-23 | Saravanampatty | T | Outlet unloading "50 NB" ROV problem and leak in STP chamber closing valve lever. | Breakdown | Gowtham | 2024-07-23 | - | Unloading "50 NB" ROV replaced by existing old one and Safety training provided to pump staffs.STP chamber closing valve lever leak arrested. Dispensing (5 mtr) new hose is kept as spsre in Sulur, Udumalai and Saravanampatty outlets.PMR completed.
CL4831 | 2024-07-23 | Madurai Ellis nagar | T | Outlet slow delivery problem. | Breakdown | Kathiresan | 2024-07-26 | - | Slow delivery problem is rectified by changing of " 40 NB" ROV rotation spring set changed and serviced. Now working in good condition.Then "A & B" side nozzle hammer teeth 8 nos replaced due to running more than 3.50000 lakhs ltrs. Nozzle working good.
CL4832 | 2024-07-23 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-23 | - | Redeem Litre- 74.86 L Amount Rs- 4259.69 Total No's of Redeem vehicle - 22 Auto- 19 Car-03 - Completed
CL4833 | 2024-07-23 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-23 | - | Redeem Litre- 71.45 L Amount Rs- 4060.00 Total No's of Redeem vehicle - 19 Auto- 18 Car-01 - Completed
CL4834 | 2024-07-23 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-23 | - | Redeem Litre- 379.79 L Amount Rs- 21603.00 Total No's of Redeem vehicle - 90 Auto- 88 Car-02 - Completed
CL4835 | 2024-07-24 | Bhavani | T | Outlet unloading and unloading training | Preventive | Avinash | 2024-07-24 | - | Unloading and unloading training completed.
CL4836 | 2024-07-24 | Virudhunagar | D | Outlet display card and display faded condition and B side nozzle leakage problem. | Breakdown | Kathiresan | 2024-07-24 | - | Display front card changed due to faded condition."B" Side nozzle leakage arrested by changing of spare nozzle teeth and front 'O' ring.Then dispensing solenoid valve and decanting solenoid valve inter changed. Working in good condition. Testing 0.94 ltrs.
CL4837 | 2024-07-24 | Tiruchengodu | D | Ourtlet dispenser reading reverse problem. | Breakdown | Avinash | 2024-07-24 | - | Dispenser reading reverse problem due to E.B voltage fluctuations. Reverse reading. A = - 147.81 Lts B = - 192.20 Lts
CL4838 | 2024-07-24 | Karur | D | Outlet C nozzle leakage problem. | Breakdown | Thirumalaisamy | 2024-07-24 | - | C nozzle leakage arrested by chaning of hammer 4 nos and centre mound O ring.Work completed.
CL4839 | 2024-07-24 | Ammapettai | A | Outlet going to offline for redeem program update work . | Development | Avinash | 2024-07-24 | - | Ofline reading A-267808.06 B-172980.07
CL4840 | 2024-07-24 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-24 | - | Redeem Litre- 138.96 L Amount Rs- 7902.67 Total No's of Redeem vehicle - 32 Auto- 26 Car-06 - Completed
CL4841 | 2024-07-24 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-24 | - | Redeem Litre- 58.43 L Amount Rs- 3320.00 Total No's of Redeem vehicle - 16 Auto- 13 Car-03 - Completed
CL4842 | 2024-07-24 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-24 | - | Redeem Litre- 163.48 L Amount Rs- 9297.19 Total No's of Redeem vehicle - 43 Auto- 41 Car-02 - Completed
CL4843 | 2024-07-25 | Ammapettai | A | Outlet Redeem updation work. | Development | Avinash | 2024-07-24 | - | Redeem program updation work completed and new billing application installed Now sales back in online. Reading A-267836.63 B-172980.07
CL4844 | 2024-07-25 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-25 | - | Redeem Litre- 28.34 L Amount Rs- 1610.60 Total No's of Redeem vehicle - 8 Auto- 8 Car-0 - Completed
CL4845 | 2024-07-25 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-25 | - | Redeem Litre- 39.63 L Amount Rs- 2254.09 Total No's of Redeem vehicle - 8 Auto- 6 Car-02 - Completed
CL4846 | 2024-07-25 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-25 | - | Redeem Litre- 160.16 L Amount Rs- 9110.00 Total No's of Redeem vehicle - 42 Auto- 42 Car-0 - Completed
CL4847 | 2024-07-26 | Trichengode | A | Outlet going offline for redeem program. | Development | Avinash | 2024-07-26 | - | Ofline reading A-420763.29 B-277054.10
CL4848 | 2024-07-26 | Namakkal-2 | A | Outlet going offline for redeem program. | Development | Nivas | 2024-07-26 | - | Offline reading. A-1023846.67 B-847594.64
CL4849 | 2024-07-26 | Trichengode | A | Outlet Redeem program updation work. | Development | Avinash | 2024-07-26 | - | Redeem program updation work completed and new billing application installed. Now sales back in online. Reading A-420763.29 B-277116.71
CL4850 | 2024-07-26 | Namakkal-3 | A | Outlet going offline for redeem program. | Development | Nivas | 2024-07-26 | - | Offline reading A-568324.31 B-413772.70
CL4851 | 2024-07-26 | Namakkal-2 | A | Outlet Redeem program updation work. | Development | Nivas | 2024-07-26 |  | Redeem program updation work completed and new billing application installed. Now sales back in online. Reading : A-1023863.63 B-847612.50
CL4852 | 2024-07-26 | Namakkal-3 | A | Outlet Redeem program updation work. | Development | Nivas | 2024-07-26 | - | Redeem program updation work completed and new billing application installed. Now sales back in online. Reading: A-568477.83 B-413808.42
CL4853 | 2024-07-26 | Kodungaiyur | C | Rule19 work. | Certification | Chandrasekar and Sureshkumar | 2024-07-26 | - | Rule -19 work started at 9.45 am. 1260 kgs product transferred from tank to lorry
CL4854 | 2024-07-26 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-26 | - | Redeem Litre- 205.98 L Amount Rs- 11715.69 Total No's of Redeem vehicle - 49 Auto- 45 Car-04 - Completed
CL4855 | 2024-07-26 | Kinathukadavu | T | CP Installation work | New project | Gowtham | 2024-07-26 | - | CP Installation work completed. Reading : R1 C 1 - -0.574 DCV R C2 - -0.574 dcv RA1 - -1.720 RA2 - -1.731 RA3 - -1.698 RA4 - -1.719 After Loop - -1.593 dcv(Soil not filled)
CL4856 | 2024-07-27 | Kodungaiyur | C | Rule19 work. | Certification | Suneel sagar, Chandrasekar and Sureshkumar | 2024-07-28 | 33 Hours | Outlet sales started at 07.00 pm. Opening reading : A-2550412.62 B- 1688945.89 Total testing - 10 litrs A- 5 litres B- 5 litres
CL4857 | 2024-07-27 | Ariyamangalam | D | Outlet C side nozzle,display and on/off switch problem. | Breakdown | Nepolean | 2024-07-27 | - | C side display cable and on/off switch problem rectified by replacing. and C side nozzle cleaned and placed .working condition normal.
CL4858 | 2024-07-27 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-27 | - | Redeem Litre- 27.10 L Amount Rs- 1540.00 Total No's of Redeem vehicle - 5 Auto- 4 Car-01 - Completed
CL4859 | 2024-07-27 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-27 | - | Redeem Litre- 123.89 L Amount Rs- 7047.00 Total No's of Redeem vehicle - 32 Auto- 31 Car-01 - Completed
CL4860 | 2024-07-28 | Madurai 3 | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-07-28 | - | Redeem program updation work completed and new billing app. installed. Now sales started in Online.
CL4861 | 2024-07-29 | Paramathi velur | D | Outlet nozzle leak problem. | Breakdown | Thirumalaisamy | 2024-07-29 | - | Nozzle leak arrested by changing of damaged latch by spare one.Automation system heating issue resolved by service and kept under observation.PMR completed.Automation equipment maintenance completed.
CL4862 | 2024-07-29 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-29 | - | Redeem Litre- 61.49 L Amount Rs- 3493.30 Total No's of Redeem vehicle - 12 Auto- 8 Car-04 - Completed
CL4863 | 2024-07-29 | Rasipuram | A | Outlet going offline for redeem program updation work . | Development | Nivas | 2024-07-29 | - | Offline reading: : A-2563810.75 B-2207542.47
CL4864 | 2024-07-29 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-29 | - | Redeem Litre- 25.86 L Amount Rs- 1471.00 Total No's of Redeem vehicle - 7 Auto- 6 Car-01 - Completed
CL4865 | 2024-07-29 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-29 | - | Redeem Litre- 144.12 L Amount Rs- 8198.28 Total No's of Redeem vehicle - 36 Auto- 34 Car-02 - Completed
CL4866 | 2024-07-29 | Rasipuram | A | Outlet Redeem program updation work. | Development | Nivas | 2024-07-29 | - | Redeem program updation work completed and new billing application installed Now sales back in online. Reading : A-2563937.62 B-2207630.00
CL4867 | 2024-07-30 | Chinnasalem | A | Outlet going offline. | Development | Pandidurai | 2024-07-30 | - | Offline for redeem program update work Offline reading : A-482176.32 B-435006.90
CL4868 | 2024-07-30 | Chinnasalem | A | Outlet Redeem program updation work. | Development | Pandidurai | 2024-07-30 | - | Redeem program updation work completed and sales back in online. Reading : A-482205.26 B-435006.90
CL4869 | 2024-07-30 | Ariyalur | D | Dispensing pump noise problem. | Breakdown | Pandidurai | 2024-07-30 | - | Dispensing pump noise problem rectified by changing of one number new spider. Working in good condition.Total all leakage checked and PMR also completed.
CL4870 | 2024-07-30 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-07-30 | - | Redeem Litre- 34.67 L Amount Rs- 1970.00 Total No's of Redeem vehicle - 5 Auto- 3 Car-02 - Completed
CL4871 | 2024-07-30 | Ariyamangalam | G | Outlet E.B power one phase problem. | Breakdown | Nepolean | 2024-07-30 | - | EB problem rectified by E.B officials and pump working in EB mode.
CL4872 | 2024-07-30 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-30 | - | Redeem Litre- 62.83 L Amount Rs- 3574.00 Total No's of Redeem vehicle - 17 Auto- 12 Car-05 - Completed
CL4873 | 2024-07-30 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-30 | - | Redeem Litre- 121.18 L Amount Rs- 6894.00 Total No's of Redeem vehicle - 38 Auto- 38 Car-0 - Completed
CL4874 | 2024-07-30 | Hosur,Krishnagiri,Tharamangalam,Dharmapuri,Omalur and Salem-2 | A | Outlet Redeem program updation work. | Development | Prabu | 2024-07-30 | - | Redeem program updation work completed and now sales back in online.
CL4875 | 2024-07-31 | Ariyamangalam | D | Outlet dispenser A and B side keypad and B side LPG hose problem. | Breakdown | Nepolean | 2024-07-31 | - | Dispenser A and B side preset litre keypad problenm resolved by changing of 2 nos of key pad B side LPG 5 m hose one number with one side recrimming work is fitted for testing purpose only.Working in good condition. B side testing : 1.43 lit.
CL4876 | 2024-07-31 | Ramanathapuram | T | Outlet ATG probe and consual wiring problem. | Breakdown | Kathiresan | 2024-07-31 | - | ATG probe and consual wiring problem rectified by re connection and installed new configuration.Dispenser DP valve diaphragm checked. Working in good condition. Fire Extinguisher 9 kg one number is failure and to be replaced. Compressor 'NRV' serviced. Working fine. Diaphragm Testing= 0.12 ltrs .
CL4877 | 2024-07-31 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-07-31 | - | Redeem Litre- 22.70 L Amount Rs- 1290.00 Total No's of Redeem vehicle - 7 Auto- 6 Car-1 - Completed
CL4878 | 2024-07-31 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-07-31 | - | Redeem Litre- 128.77 L Amount Rs- 7326.64 Total No's of Redeem vehicle - 41 Auto- 41 Car-0 - Completed
CL4879 | 2024-07-31 | T.V.Kovil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-07-31 | - | Redeem Litre- 44.44 L Amount Rs- 2528.00 Total No's of Redeem vehicle - 11 Auto- 9 Car-02 - Completed
CL4880 | 2024-07-31 | Uthamacholapuram and Ayothiyapattinam | A | Outlet Redeem program updation work. | Development | Prabu | 2024-07-31 | - | Redeem program updation work completed and now sales back in online.
CL4881 | 2024-08-01 | Bodi | D | Outlet dispensing line air hose air leakage problem. | Breakdown | Kamaraj | 2024-08-01 | - | Dispensing line air hose air leakage arrested by cleaning and tighting of screws.Automation maintenance and general check up done.
CL4882 | 2024-08-01 | Uthamapalayam | G | General check up work | Preventive | Kamaraj | 2024-08-01 | - | Outlet automation maintenance and all leakage tested.
CL4883 | 2024-08-01 | Madurai Ellis nagar | D | Outlet dispenser "A" hose leakage and oil dispenser mother board problem. | Breakdown | Kathiresan | 2024-08-01 | - | Dispenser "A" hose leakage tested,no problem and oil dispenser mother board totalizer reading problem resolved by making totalizer reading in to Zero as per oil company instruction. Oil oulet hose 5 mtrs changed. "A" side Testing=0.73 ltrs
CL4884 | 2024-08-01 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-01 | - | Redeem Litre- 44.93 L Amount Rs- 2552.80 Total No's of Redeem vehicle - 12 Auto- 10 Car-02 - Completed
CL4885 | 2024-08-01 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-01 | - | Redeem Litre- 25.79 L Amount Rs- 1450.00 Total No's of Redeem vehicle - 7 Auto- 7 Car-0 - Completed
CL4886 | 2024-08-01 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-01 | - | Redeem Litre- 87.63 L Amount Rs- 4984.56 Total No's of Redeem vehicle - 23 Auto- 21 Car-03 - Completed
CL4887 | 2024-08-02 | Karur | D | Outlet "D" nozzle DP valve diaphragm damaged. | Breakdown | Thirumalaisamy | 2024-08-02 | - | "D" nozzle DP valve diaphragm changed due to damaged condition."C"nozzle DP valve diaphragm checked.Working in good condition. Testing=3.86 liters.
CL4888 | 2024-08-02 | Vellakoil | G | Outlet fire extinguisher service and training. | Preventive | Thirumalaiasamy | 2024-08-02 | - | Fire extinguisher renewal work and training completed.Certificate obtained.Automation equipment maintenance completed.
CL4889 | 2024-08-02 | Dharapuram | G | Outlet fire extinguisher service and training work. | Preventive | Gowtham | 2024-08-02 | - | Fire extinguisher service and training completed. 70 kg extinguisher CO2 delivery hose 1 no. replaced.Renewal certificate obtained.
CL4890 | 2024-08-02 | Vadivelan nagar | D | Outlet A,C & D side nozzle display glass damage. | Breakdown | Suneel Sagar | 2024-08-02 | - | The damaged A, C & D side nozzle display glass replaced by new one.
CL4891 | 2024-08-02 | Vedachandur | G | Outlet fire extinguisher service and training work. | Preventive | Kamaraj | 2024-08-02 | - | Fire extinguisher renewal work and training completed.Certificate obtained.
CL4892 | 2024-08-02 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-02 | - | Redeem Litre- 32.75 L Amount Rs- 1860.30 Total No's of Redeem vehicle - 9 Auto- 7 Car-02 - Completed
CL4893 | 2024-08-02 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-02 | - | Redeem Litre- 78.56 L Amount Rs- 4468.00 Total No's of Redeem vehicle - 18 Auto- 15 Car-03 - Completed
CL4894 | 2024-08-02 | Melur | G | Outlet fire extinguisher service and training work. | Preventive | Kathiresan | 2024-08-02 | - | Fire extinguisher renewal work and training completed.Certificate obtained.
CL4895 | 2024-08-03 | Kinathukadavu | G | Material unloading work | New project | Gowtham | 2024-08-03 | - | Material unloading work completed.
CL4896 | 2024-08-03 | Pudukkottai | R | Outlet servo stablizer R phase problem. | Breakdown | Nepolean | 2024-08-03 | - | Servo stablizer R phase problem resolved by servicing and working condition normala and kept under observation for two days.
CL4897 | 2024-08-03 | Cantonment | D | Outlet dispensing pump motor problem. | Breakdown | Chandrasekar | 2024-08-03 | - | Dispensing pump motor problem rectified by changing of one new spider.working in good condition.
CL4898 | 2024-08-03 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-03 | - | Redeem Litre- 42.38 L Amount Rs- 2416.00 Total No's of Redeem vehicle - 7 Auto- 4 Car-03 - Completed
CL4899 | 2024-08-03 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-03 | - | Redeem Litre- 67.60 L Amount Rs- 3858.00 Total No's of Redeem vehicle - 17 Auto- 15 Car-02 - Completed
CL4900 | 2024-08-04 | Avadi | T | Outlet dispensing motor pump noise level is abnormal. | Breakdown | Suneel Sagar | 2024-08-04 | - | Dispensing motor abnormal pump noise rectified to normal by replacing of two bolts. Drawing current 6.2A, 5.9A and 6.05A respectively in R, Y and B phases.
CL4901 | 2024-08-04 | Kattupakkam | T | Outlet tank1 Rochester gauge dial is broken. | Breakdown | Suneel Sagar | 2024-08-04 | - | Tank1 Rochester broken gauge dial one no screw replaced by new one and found dispensing pump spider is good condition and motor drawing current 7.02, 6.92 and 6.2 respectively in R, Y and B phases.
CL4902 | 2024-08-04 | Attur | A | Outlet Redeem program updation work. | Development | Nivas | 2024-08-04 | - | Redeem program updation completed and new IP Board and billing application installed. Now sales back in online. C- 1978861.91 D- 1804387.87
CL4903 | 2024-08-04 | Bhavani | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-04 | - | Redeem program updation completed and new billing application installed Now sales back in online.
CL4904 | 2024-08-04 | Palladam 1 | A | Outlet Redeem program updation work. | Development | Gowtham | 2024-08-04 | - | Redeem program updation completed and new billing application installed Now sales back in online.
CL4905 | 2024-08-05 | Avinashi | A | Outlet Redeem program updation work. | Development | Gowtham | 2024-08-05 | - | Redeem program updation completed and new billing application installed Now sales back in online.
CL4906 | 2024-08-05 | Udumalpet | A | Outlet Redeem program updation work. | Development | Gowtham | 2024-08-05 | - | Redeem program updation completed and new billing application installed Now sales back in online.
CL4907 | 2024-08-05 | Palladam 2 | A | Outlet Redeem program updation work. | Development | Gowtham | 2024-08-05 | - | Redeem program updation completed and new billing application installed Now sales back in online.
CL4908 | 2024-08-05 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-05 | - | Redeem Litre- 51.79 L Amount Rs- 2957.00 Total No's of Redeem vehicle - 14 Auto- 13 Car-01 - Completed
CL4909 | 2024-08-05 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-05 | - | Redeem Litre- 21.73 L Amount Rs- 1240.00 Total No's of Redeem vehicle - 6 Auto- 5 Car-01 - Completed
CL4910 | 2024-08-05 | T.V.Koil | D | Outlet dispenser B side nozzle hose damage. | Breakdown | Vigneshwaran | 2024-08-05 | - | Dispenser B side damaged nozzle hose replaced by new one. Testing liter:1.2 ltr.
CL4911 | 2024-08-05 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-05 | - | Redeem Litre- 20.42 L Amount Rs- 1165.00 Total No's of Redeem vehicle - 6 Auto- 6 Car-0 - Completed
CL4912 | 2024-08-06 | Ammapettai | T | Outlet DP value CP value check up. | Breakdown | Avinash | 2024-08-06 | - | Outlet DP value leak checked and CP value ( -0.710) is dropped,kept under observation. PMR completed. Redeem application training given to pump staff , one new mobile app installed for billing.
CL4913 | 2024-08-06 | Eral | D | Outlet "R" phase winding carbon bush' and key pad problem. | Breakdown | Kathiresan | 2024-08-06 | - | "R" phase winding carbon bush and "A" side key pad problems resolved by changing of new one.ALDS panel "FRL" unit changed and dispenser bottom Side LPG leakage arrested by cleaning and tightening of nuts.Working in good condition.
CL4914 | 2024-08-06 | Kodungaiyur | R | Outlet control panel soft starter problem. | Breakdown | Suneel Sagar | 2024-08-06 | 4.30 Hrs | Outlet control panel divert into by pass mode and soft starter checked motor condition both in EB and DG found satisfactory.
CL4915 | 2024-08-06 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-06 | - | Redeem Litre- 15.67 L Amount Rs- 895.00 Total No's of Redeem vehicle - 4 Auto- 3 Car-01 - Completed
CL4916 | 2024-08-06 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-06 | - | Redeem Litre- 20.70 L Amount Rs- 1180.00 Total No's of Redeem vehicle - 4 Auto- 2 Car-02 - Completed
CL4917 | 2024-08-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-06 | - | Redeem Litre- 31.43 L Amount Rs- 1794.20 Total No's of Redeem vehicle - 10 Auto- 10 Car-0 - Completed
CL4918 | 2024-08-06 | Kinathukadavu | T | Outlet tank spares installation work. | New project | Gowtham | 2024-08-06 | - | Tank inside 2 nos. of liquid suction line welding and testing completed. Both flanges are installed after cleaning and fixing of excess flow valve completed. Welding work going on.
CL4919 | 2024-08-07 | Pudukkottai | R | Outlet servo stablizer problem. | Breakdown | Nepolean | 2024-08-07 | - | Servo stablizer problem rectified by changing of new linear resistance.Working in good condition. Servo Input voltage : 232, 247, 248 Output voltage : 229, 232, 233 PMR work completed.
CL4920 | 2024-08-07 | Bhavani | D | Outlet dispenser D side keypad problem. | Breakdown | Avinash | 2024-08-07 | - | Dispenser D side keypad problem resolved by changing of new one.Redeem application training given to pump staff.PMR completed. DP value checked Testing A side 0.44 lts.
CL4921 | 2024-08-07 | Omalur | R | Outlet control panel booting problem. | Breakdown | Prabu | 2024-08-07 | - | Control panel booting problem resolved by servicing of office room emergency switch element.Now working condition. Panel CC indicator light 1 no's changed.PMR completed and Redeem application training given to pump staff.Leak and DP value checked.
CL4922 | 2024-08-07 | Namakkal 1 | D | Outlet dispenser B side keypad problem. | Breakdown | Nivas | 2024-08-07 | - | B side keypad problem rectified by replacing of new one.Working in good condition.
CL4923 | 2024-08-07 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-08-07 | - | Redeem Litre- 11.75 L Amount Rs- 670.00 Total No's of Redeem vehicle - 3 Auto- 2 Car-1 - Completed
CL4924 | 2024-08-07 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-07 | - | Redeem Litre- 41.52 L Amount Rs- 2370.00 Total No's of Redeem vehicle - 12 Auto- 12 Car-0 - Completed
CL4925 | 2024-08-07 | Madurai Villapuram | G | Outlet ATG reconfiguration work. | Breakdown | Kathiresan | 2024-08-07 | - | ATG reconfiguration and 3 (v) battery newly changed. Working in good condition. ATG cut off 85 % Working condition.
CL4926 | 2024-08-07 | Vellakoil | D | Outlet dispenser reading jumping problem. | Breakdown | Thirumalaisamy | 2024-08-07 | - | Dispenser filter cleaned and LPG flow adjusted and jumping problem in full tank vehicle reading under observation.
CL4927 | 2024-08-08 | Trichengode | D | Outlet dispenser A side jumping problem and general check up. | Breakdown | Avinash | 2024-08-08 | - | A side jumping problem rectified by changing of New DP membrane.Kept under observation. Leak, DP value checked.Automation maintenance done .PMR completed and Redeem application training given to pump staff. Testing A side 5.04 lts.
CL4928 | 2024-08-08 | Kinathukadavu | G | Welding work and canopy installation work. | New project | Gowtham | 2024-08-08 | - | Welding work and canopy installation work under progress.
CL4929 | 2024-08-08 | Thanjavur | D | Outlet A and B side display glass and "A" side keypad problem. Dispensing liquid line ROV closing problem. | Breakdown | Pandidurai | 2024-08-08 | - | A and B side faded display glass are changed by new one and "A" side keypad replaced by new one. Dispensing liquid line ROV closing problem resolved by interchanging of unloading ROV. Automation maintenance done. PMR also completed.
CL4930 | 2024-08-08 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-08 | - | Redeem Litre- 74.97 L Amount Rs- 4279.91 Total No's of Redeem vehicle - 19 Auto- 18 Car-01 - Completed
CL4931 | 2024-08-08 | Vadivelan nagar | T | Outlet tank pressure low problem. | Breakdown | Suneel Sagar | 2024-08-08 | - | Tank pressure low, 5kg after unloding resoved by adjusting the by pass valve and brought the dispensing pressure to 13 kg.
CL4932 | 2024-08-08 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-08 | - | Redeem Litre- 21.96 L Amount Rs- 1253.00 Total No's of Redeem vehicle - 4 Auto- 3 Car-01 - Completed
CL4933 | 2024-08-08 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-08 | - | Redeem Litre- 11.22 L Amount Rs- 640.00 Total No's of Redeem vehicle - 4 Auto- 3 Car-01 - Completed
CL4934 | 2024-08-08 | Mettupalayam | A | Outlet Redeem program updation work. | Development | Gowtham | 2024-08-08 | - | Redeem program upgradation completed except mobile application installation.
CL4935 | 2024-08-08 | Dharapuram | A | Outlet Redeem program updation work. | Development | Gowtham | 2024-08-08 | - | Redeem program upgradation completed except mobile application installation.
CL4936 | 2024-08-09 | Vellakoil | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-09 | - | Redeem program upgradation completed except mobile application installation.
CL4937 | 2024-08-09 | Paramathi velur | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-09 | - | Redeem program upgradation completed except mobile application installation.
CL4938 | 2024-08-09 | Sangagiri | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-09 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4939 | 2024-08-09 | Paramathi velur | G | Outlet fire extinguisher service and general check up. | Preventive | Thirumalaisamy | 2024-08-09 | - | Fire extinguisher service and training completed.Redeem application training given to pump staffs.DP valve diaphragm checked working normal.
CL4940 | 2024-08-09 | Perundurai | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-09 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4941 | 2024-08-09 | Erode | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-09 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4942 | 2024-08-09 | Sangagiri | G | Outlet Fire extinguisher service and renewal work and unloading solenoid coil energizing problem. | Preventive | Avinash | 2024-08-09 | - | PMR completed and Redeem application and Fire extinguisher training given to pump staff. Fire extinguisher service and renewal completed . Leak , DP value checked and unloading solenoid coil energizing problem resolved by replacing ogf new one.
CL4943 | 2024-08-09 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-09 | - | Redeem Litre- 60.86 L Amount Rs- 3473.43 Total No's of Redeem vehicle - 14 Auto- 14 Car-0 - Completed
CL4944 | 2024-08-09 | Kodumudi | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-09 | - | Outlet going to offline for redeem program update work A-429239.32 B-428185.94.
CL4945 | 2024-08-09 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-09 | - | Redeem Litre- 13.48 L Amount Rs-769.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-1 - Completed
CL4946 | 2024-08-09 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-09 | - | Redeem Litre- 31.91 L Amount Rs- 1820.00 Total No's of Redeem vehicle - 9 Auto- 6 Car-3 - Completed
CL4947 | 2024-08-09 | Kodumudi | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-09 | - | Redeem program updation completed and newbilling application installed Now sales back in online. A-429256.79 B- 428238.97
CL4948 | 2024-08-10 | Ayothiyapattinam | G | Outlet fire extinguisher service and renewal and dispenser nozzle teeth problem. | Preventive | Prabu | 2024-08-10 | - | Outlet fire extinguisher service and training completed.Redeem application training given to pump staffs.DP valve diaphragm checked working normal. Dispenser both sides nozzle problem resolved by changing of teeth.PMR done.
CL4949 | 2024-08-10 | Omalur | G | Outlet fire extinguisher service and renewal and dispenser nozzle teeth problem. | Preventive | Prabu | 2024-08-10 | - | Outlet fire extinguisher service and training completed.Redeem application training given to pump staffs.DP valve diaphragm checked working normal. Dispenser both sides nozzle problem resolved by changing of teeth.PMR done.
CL4950 | 2024-08-10 | Rasipuram | G | Outlet Fire extinguisher service and renewal work. | Preventive | Nivas | 2024-08-10 | - | Fire extinguisher service completed. Training given to pump staff's Mr. Chandru, Saran kumar and suresh kumar.
CL4951 | 2024-08-10 | Mulanur | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-10 | - | Outlet going to offline for redeem program updation work . A-783322.71 B-558079.90
CL4952 | 2024-08-10 | Palayam | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-10 | - | Outlet going to offline for redeem program updation work . A-447380.13 B-406582.45
CL4953 | 2024-08-10 | Ariyamangalam | G | N2 air M/c fitting problem. | Breakdown | Nepolean | 2024-08-10 | - | N2 air M/c fitting problem resolved by changing of one new one.Working condition normal
CL4954 | 2024-08-10 | Nasiyanur | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-10 | - | Outlet going offline for redeem program updation work . .Ofline reading: A-225303.52 B-165677.80
CL4955 | 2024-08-10 | Perundurai | G | Outlet PMR work and Redeem application training. | Preventive | Avinash | 2024-08-10 | - | PMR completed and Redeem application training given to pump staff . Leak, DP value checked .Working in good condition
CL4956 | 2024-08-10 | Nasiyanur | A | Outlet Redeem program updation and general check up | Development | Avinash | 2024-08-10 | - | Redeem program updation completed and new billing application installed Now sales back in online and Redeem application training given to pump staff Reading: A-225323.64 B-165678.03 PMR completed Leak and DP value checked.Automation maintenance done. one 9 kg ABC fire extinguisher pressure dropped . A side testing: 0.23 Lts
CL4957 | 2024-08-10 | Mulanur | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-10 | - | Redeem program updation completed and new billing application installed and now sales back in online. A-783366.18 B-558098.80
CL4958 | 2024-08-10 | Palayam | A | Outlet Redeem program updation work. | Development | Thirumalaisamy | 2024-08-10 | - | Redeem program updation completed and new billing application installed. Now sales back in online. A-447392.95 B-406612.71
CL4959 | 2024-08-10 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-10 | - | Redeem Litre- 6.18 L Amount Rs- 353.00 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL4960 | 2024-08-10 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-10 | - | Redeem Litre- 59.88 L Amount Rs- 3418.00 Total No's of Redeem vehicle - 14 Auto- 12 Car-02 - Completed
CL4961 | 2024-08-10 | Kodumudi | G | Prevention of fire accident in customer vehicle. | Preventive | Thirumalaisamy | 2024-08-10 | - | One customer vehicle came to our outlet around 4.00PM. After fueling the vehicle went away 100 meters from our station then fire occurred in the vehicle due to a petrol leak from the engine inlet valve, Then suddenly our pump staff Mr.Eswara moorthi controlled and stopped the fire by using our 9 kg ABC cylinder fire extinguisher.
CL4962 | 2024-08-10 | Madurai Villapuram | D | Outlet "C" Side spare nozzle and 4 side display problem. | Breakdown | Kathiresan | 2024-08-10 | - | "C" side spare Nozzle problem rectified by changing of mount. Then faded 4 side display glasses changed.Working in good condition.
CL4963 | 2024-08-10 | Madurai Ellis nagar | D | Outlet "B" Side nozzle NRV and nozzle casting damaged. | Breakdown | Kathiresan | 2024-08-10 | - | The damaged "B" Side nozzle NRV and nozzle casting changed by spare nozzle. Nozzle Reading: Old = 873533.220 New= 1187339.630
CL4964 | 2024-08-10 | Kinathukadavu | G | Outlet pipeline work. | New project | Gowtham | 2024-08-10 | - | Pipeline welding work completed and hydrotest done in 48 kg / cm² pressure .While testing leakage found in 2" Tee joint due to fitting crack, then reweld and retest done, now no leak, found satisfactory. Tomorrow planned to motor shed welding.
CL4965 | 2024-08-11 | Dharmapuri | A | Outlet Redeem application training and general check up. | Development | Prabu | 2024-08-11 | - | Redeem application training given to pump staffs. Automation maintenance done.Dispenser DP valve diaphragm checked. Working in good condition.
CL4966 | 2024-08-11 | Theni | R | Outlet servo stabilizer board, control panel SMBS board and Batchen dispenser power card damaged due to short circute. | Breakdown | Kamaraj and Chandrasekar | 2024-08-12 | - | Due to heavy rain, voltage fluctuations the damaged control panel SMBS board and batchen dispenser power card replaced. Pump working condition is normal. only servo stabilizer board will be changed by tomorrow. Now stabilizer working on by pass mode.
CL4967 | 2024-08-11 | Tirunelveli | R | Outlet control panel R1 contactor and Panel 20 amps fuse short-circuit Problem. | Breakdown | Kathiresan | 2024-08-11 | 2 Hrs | Control panel R1 contactor and panel 20 amps fuse short-circuit problem temporarely resolved by working in by pass mode.
CL4968 | 2024-08-12 | Tirunelveli | R | Outlet control panel problem. | Breakdown | Kathiresan | 2024-08-12 | - | Control panel problem rectified by changing of "ESR 240(v)" contactor and "20" AMPS fuse. Panel working in good condition. EB panel nutral 25sqm leg changed and working fine.
CL4969 | 2024-08-12 | Batlagundu | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-12 | - | Outlet for going to offline for Redeem points updation work. Dispenser closing Reading: A = 525399.08 B = 525059.64
CL4970 | 2024-08-12 | Bodi | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-12 | - | Outlet for going to offline for Redeem point updation work. Dispenser closing Reading: A = 162628.70 B = 158341.41
CL4971 | 2024-08-12 | Devakottai | A | Outlet Redeem program updation work. | Development | Nepolean | 2024-08-12 | - | Outlet for going to offline for Redeem point updation work. . Dispenser closing Reading : A : 266539.77 B : 293624.25
CL4972 | 2024-08-12 | Thiruvaiyaru | D | Outlet dispensing pump noise and dispensing liquid line ROV leakage problem. | Breakdown | Prasath,Nepolean and Pandidurai | 2024-08-12 | - | Dispensing pump noise problem resolved by changing of one damaged spider and kept under observation. Dispensing liquid line ROV leakage arrested by cleaning and tightening of screws. Total all leakage checked and PMR also completed.
CL4973 | 2024-08-12 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-12 | - | Redeem Litre- 46.20 L Amount Rs- 2638.00 Total No's of Redeem vehicle - 12 Auto- 12 Car-0 - Completed
CL4974 | 2024-08-12 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-12 | - | Redeem Litre- 19.43 L Amount Rs- 1109.00 Total No's of Redeem vehicle - 5 Auto- 4 Car-01 - Completed
CL4975 | 2024-08-12 | Devakottai | A | Outlet Redeem program updation work. | Development | Nepolean | 2024-08-12 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4976 | 2024-08-12 | Batlagundu | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-12 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4977 | 2024-08-12 | Bodi | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-12 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4978 | 2024-08-13 | Madurai Ellis nagar | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading : A : 1085268.670 B : 1191459.190 C: 754820.130 D : 976728.000
CL4979 | 2024-08-13 | Madurai Villapuram | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading : A : 1307151.810 B : 1461552.110 C: 740497.020 D : 874065.530
CL4980 | 2024-08-13 | Eral | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A : 349270.050 B : 268936.120
CL4981 | 2024-08-13 | Melur | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A : 364150.150 B : 378396.830
CL4982 | 2024-08-13 | Madurai Ellis nagar | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4983 | 2024-08-13 | Madurai Villapuram | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4984 | 2024-08-13 | Eral | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4985 | 2024-08-13 | Melur | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4986 | 2024-08-13 | Thuraiyur | T | Outlet unloading solenoid coil problem. | Breakdown | Nivas | 2024-08-13 | - | Unloading solenoid coil problem resolved by replacing of new coil. A side teeth 4 nos changed and redeem application training given to pump staff.
CL4987 | 2024-08-13 | Tirunelveli | T | Outlet tank 1 Turbo drive power board " MOV " short circuit problem. | Breakdown | Kathiresan | In process | - | Tank 1 Turbo drive power board " MOV " short circuit problem temporarely resolved by pass mode.Working normal.
CL4988 | 2024-08-13 | Tharamangalam | T | Outlet unloading ROV rotation solenoid coil problem. | Breakdown | Prabu | 2024-08-13 | - | Unloading ROV rotation solenoid coil problem rectified by cleaning and now working in good condition. Redeem application training given to pump staffs. PMR done.
CL4989 | 2024-08-13 | Theni | R | Outlet for servo stabilizer board change work. | Breakdown | Kamaraj | 2024-08-13 | - | Servo stabilizer board new one replaced. Work condition is normal. Panel input supply: R phase- 232(v), Y phase-231(v)- B phase -230(v). Earthing Resistance - 0.3 Ohm. PMR also completed.
CL4990 | 2024-08-13 | Ramanathapuram | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A : 950109.210 B : 1008805.250
CL4991 | 2024-08-13 | Tenkasi | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A- 168157.520 B- 188463.440
CL4992 | 2024-08-13 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-13 | - | Redeem Litre- 5.26 L Amount Rs- 300.00 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL4993 | 2024-08-13 | Erode | G | Outlet PMR work. | Preventive | Avinash | 2024-08-13 | - | PMR completed and leak and DP value checked.
CL4994 | 2024-08-13 | Virudhunagar | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A- 1051229.050 B- 994978.780
CL4995 | 2024-08-13 | Uthamapalayam | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-13 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A-23819.40 B-28813.93
CL4996 | 2024-08-13 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-13 | - | Redeem Litre- 12.49 L Amount Rs- 713.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-01 - Completed
CL4997 | 2024-08-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-13 | - | Redeem Litre- 30.47 L Amount Rs- 1739.00 Total No's of Redeem vehicle - 7 Auto- 4 Car-03 - Completed
CL4998 | 2024-08-13 | Tenkasi | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL4999 | 2024-08-13 | Virudhunagar | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5000 | 2024-08-13 | Ramanathapuram | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-13 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5001 | 2024-08-14 | Tirunelveli | A | Outlet Redeem program updation work. | Development | Kathiresan | 2024-08-14 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A : 203831.620 B : 307909.590
CL5002 | 2024-08-14 | Uthamapalayam | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-14 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5003 | 2024-08-14 | Theni | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-14 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5004 | 2024-08-14 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-14 | - | Redeem Litre- 50.76 L Amount Rs- 2898.00 Total No's of Redeem vehicle - 13 Auto- 12 Car-01 - Completed
CL5005 | 2024-08-14 | Sulur | T | Outlet unloading motor problem. | Breakdown | Gowtham | 2024-08-19 | - | EB mainline MCB 63 A , stabilizer 40A MCB replaced due to some electrical complaint.Unloading motor run problem rectified by interchanging of Y and B phase in genset and unloading done.Panel shut off problem in observation. Unloading solid valve coil replaced by spare.
CL5006 | 2024-08-14 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-14 | - | Redeem Litre- 8.52 L Amount Rs- 486.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-01 - Completed
CL5007 | 2024-08-14 | Chengalpattu | A | Outlet Redeem program updation work. | Development | Suneel Sagar | 2024-08-14 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5008 | 2024-08-14 | Avadi | A | Outlet Redeem program updation work. | Development | Suneel Sagar | 2024-08-14 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5009 | 2024-08-14 | Vadivelan nagar | A | Outlet Redeem program updation work. | Development | Suneel Sagar | 2024-08-14 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5010 | 2024-08-15 | Thuraiyur | D | Outlet dispenser B side on/off switch Problem. | Breakdown | Nivas | 2024-08-15 | - | B side On/Off switch problem.resolved vby changing of new one. Working in good condition. PMR also completed. Testing lit - 5.69.
CL5011 | 2024-08-15 | Ariyamangalam | G | Outlet N2 air M/C inside air fitting problem. | Breakdown | Nepolean | 2024-08-15 | - | N2 air M/C inside air fitting problem resolved by changing of new one.Working in good condition.
CL5012 | 2024-08-15 | Kattupakkam | A | Outlet Redeem program updation work. | Development | Suneel Sagar | 2024-08-15 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5013 | 2024-08-15 | Kodungaiyur | A | Outlet Redeem program updation work. | Development | Suneel Sagar | 2024-08-15 | - | Redeem program updation completed and new billing application installed. Now sales back in online.
CL5014 | 2024-08-15 | Omalur | G | Outlet Nitrogen air machine display problem. | Breakdown | Prabu | 2024-09-02 | - | Nitrogen air machine display problem rectified by replacing of new display board with warranty period.
CL5015 | 2024-08-15 | Madurai Villapuram | D | Outlet dispensing vapour line "25 NB" ROV problem. | Breakdown | Kathiresan | 2024-08-15 | - | Dispensing vapour line "25 NB" ROV problem rectified by interchanging of unloading "25 NB" ROV.Working in good condition.
CL5016 | 2024-08-16 | Vedachandur | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-16 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A-601600.74 B-566175.62
CL5017 | 2024-08-16 | Namakkal 1 | A | Outlet Redeem program updation work. | Development | Nivas | 2024-08-16 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A-1148282.52 B-757456.07
CL5018 | 2024-08-16 | Sangagiri | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-16 | - | Outlet going to offline for Redeem point updation work. Dispenser Reading A-642994.52 B-459168.22
CL5019 | 2024-08-16 | Sangagiri | A | Outlet Redeem program updation work. | Development | Avinash | 2024-08-16 | - | Redeem program updation completed and new billing application installed. Now sales back in online. A-643082.89 B-459266.12
CL5020 | 2024-08-16 | Vedachandur | A | Outlet Redeem program updation work. | Development | Kamaraj | 2024-08-16 | - | Redeem program updation completed and new billing application installed. Now sales back in online. A-601796.02 B-566379.73
CL5021 | 2024-08-16 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-16 | - | Redeem Litre- 12.62 L Amount Rs- 720.00 Total No's of Redeem vehicle - 3 Auto- 1 Car-02 - Completed
CL5022 | 2024-08-16 | Ariyamangalam | C | Outlet Rule 18 work. | Certification | Nepolean | 2024-08-16 | - | Rule 18 work completed.
CL5023 | 2024-08-16 | Namakkal 1 | A | Outlet Redeem program updation work. | Development | Nivas | 2024-08-16 | - | Redeem program updation completed and new billing application installed. Now sales back in online. A-1148490.57 B-757629.52
CL5024 | 2024-08-16 | Perambalur | D | Outlet 'B' side nozzle hose and N2 air machine inside air hose damaged. | Breakdown | Sureshkumar | 2024-08-16 | - | The damaged 'B' side nozzle hose and N2 air machine inside air hose replaced by new one.Working in good condition. Testing littres:0.870
CL5025 | 2024-08-16 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-16 | - | Redeem Litre- 24.48 L Amount Rs- 1397.00 Total No's of Redeem vehicle - 6 Auto- 5 Car-01 - Completed
CL5026 | 2024-08-17 | T.V.Koil | C | Outlet Rule 18 work. | Certification | Nepolean | 2024-08-17 | - | Rule 18 work completed.
CL5027 | 2024-08-17 | Renganathan Outlet | D | Outlet yenen dispenser nozzle problem. | Breakdown | Vigneshwaran | 2024-08-17 | - | Dispenser nozzle problem resolved by changing of one new nozzle.Workng in good condition.
CL5028 | 2024-08-17 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-17 | - | Redeem Litre- 22.89 L Amount Rs- 1307.00 Total No's of Redeem vehicle - 8 Auto- 7 Car-01 - Completed
CL5029 | 2024-08-18 | Chennai Velacherry | G | Pump materials unloading work . | Breakdown | Chandrasekar | 2024-08-18 | - | Pump materials unloading work completed.
CL5030 | 2024-08-18 | Virudhunagar | G | Outlet canopy light damage and "ATG" veedor root display problem. | Breakdown | Kathiresan | 2024-08-18 | - | The damaged 8 nos of canopy light to be replaced. "ATG" Veedor Root display problem. Dispenser DP valve diaphragm puncher checked. Tank area compund civil work inspected.Working in good condition. Testing = 0.55 ltrs.
CL5031 | 2024-08-19 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-19 | - | Redeem Litre- 34.00 L Amount Rs- 1939.87 Total No's of Redeem vehicle - 7 Auto- 5 Car-02 - Completed
CL5032 | 2024-08-19 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-19 | - | Redeem Litre- 3.57 L Amount Rs- 204.00 Total No's of Redeem vehicle - 1 Auto- 1 Car-0 - Completed
CL5033 | 2024-08-19 | Neelambur | G | Outlet PMR work. | Preventive | Gowtham | 2024-08-19 | - | PMR completed and compressor oil changed.
CL5034 | 2024-08-20 | Avinashi | G | Outlet canopy false ceiling work. | Preventive | Gowtham | 2024-08-20 | - | Canopy false ceiling work will starts from tomorrow. Safety instructions and work process are discussed with dealer.
CL5035 | 2024-08-20 | Ayothiyapattinam | D | Outlet dispenser nozzle problem. | Breakdown | Prabu | 2024-08-20 | - | Dispenser nozzle problem rectified by servicing and changing of one number of front oring.Work completed.
CL5036 | 2024-08-20 | Chinnasalem | R | Outlet online UPS problem. | Breakdown | Prabu | 2024-08-20 | - | Online UPS problem rectified by servicing the fan and ups and replacing of 3 nos of batteries.Working in good condition.
CL5037 | 2024-08-20 | T.V.Koil | D | Outlet 'A' side nozzle teeth problem. | Breakdown | Sureshkumar | 2024-08-20 | - | A' side nozzle teeth problem resolved by changing of 4 nos of new hummer teeths.Working in good condition.
CL5038 | 2024-08-20 | Cantonment | C | Outlet Rule 18 work. | Certification | Nepolean and Vigneshwaran | 2024-08-20 | - | Rule 18 work completed.
CL5039 | 2024-08-20 | Bavani | D | Outlet A side keypad problem and.C and D side auto off problem. | Breakdown | Avinash | 2024-08-20 | - | A side keypad problem resolved by replaced by a new one.C and D side auto off problem while tank full is rectified by claening of filter and flow adjusted and kept for observation.
CL5040 | 2024-08-20 | Madurai Ellis nagar | D | Outlet "A" side nozzle latch lock set damaged. | Breakdown | Kathiresan | 2024-08-20 | - | The damaged "A" Side nozzle latch lock set replaced by new one.Working in good condition.
CL5041 | 2024-08-20 | Ariyamangalam | D | Outlet "D" side On/Off switch problem. | Breakdown | Pandidurai | 2024-08-20 | - | "D" side On/Off switch replaced by new one.Working in good condition.
CL5042 | 2024-08-20 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-20 | - | Redeem Litre- 21.58 L Amount Rs- 1233.00 Total No's of Redeem vehicle - 6 Auto- 6 Car-0 - Completed
CL5043 | 2024-08-21 | Hosur | C | Rule 18 and Stamping work | Certification | Prabu and Vigneshwaran | 2024-08-22 | - | Rule 18 and Stamping and Calibration completed.
CL5044 | 2024-08-21 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-21 | - | Redeem Litre- 12.10 L Amount Rs- 690.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-01 - Completed
CL5045 | 2024-08-21 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-21 | - | Redeem Litre- 10.11 L Amount Rs- 577.00 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL5046 | 2024-08-22 | Thiruvaiyaru | A | Outlet dispenser automation SMPS problem. | Breakdown | Pandidurai | 2024-08-22 | - | Dispenser automation SMPS problem rectified by replacing of new one.Working in good condition.
CL5047 | 2024-08-22 | Ariyamangalam | D | Outlet dispenser D side display cable problem. | Breakdown | Nepolean | 2024-08-22 | - | D side display cable problem resolved replacing of one new cable.Working in good condition. D side testing : 2.97 lit.
CL5048 | 2024-08-22 | Bhavani | R | Outlet online UPS problem. | Breakdown | Avinash | 2024-08-24 | - | Online UPS problem due to cooling fan issue now replaced by new fan and backup 10 mins.Battery to replaced. Now ups working in good condition.
CL5049 | 2024-08-22 | Krishnagiri | C | Stamping and Calibration work | Certification | Prabu and Vigneshwaran | 2024-08-22 | - | Stamping and Calibration completed
CL5050 | 2024-08-22 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-08-22 | - | Redeem Litre- 5.09 L Amount Rs- 290.00 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL5051 | 2024-08-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-22 | - | Redeem Litre- 23.01 L Amount Rs- 1313.00 Total No's of Redeem vehicle - 6 Auto- 6 Car-0 - Completed
CL5052 | 2024-08-22 | T.V.Koil | A | Loyalty program redeem | Development | Vigneshwaran | 2024-08-22 | - | Redeem Litre- 9.962 L Amount Rs- 566.00 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL5053 | 2024-08-23 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-23 | - | Redeem Litre- 58.71 L Amount Rs- 3351.00 Total No's of Redeem vehicle - 13 Auto- 10 Car-03 - Completed
CL5054 | 2024-08-23 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-08-23 | - | Redeem Litre- 11.23 L Amount Rs- 640.00 Total No's of Redeem vehicle - 3 Auto- 1 Car-02 - Completed
CL5055 | 2024-08-23 | Dharmapuri | C | Outlet Rule 18 work. | Certification | Prabu and Vigneshwaran | 2024-08-23 | - | Rule 18 work completed, Unloading earth cable 4m extended and earth pit regenerator work and C.P voltage normal. Earth regenerated.
CL5056 | 2024-08-23 | Krishnagiri | T | Outlet Rule 18 work and tank area inspection. | Breakdown | Prabu and Vigneshwaran | 2024-08-23 | - | Rule 18 work completed.Tank area side pipe line and GI flat and flange corrosion formed and vapour pipe line corrosion formed.Tank area side painting work must.
CL5057 | 2024-08-24 | Devakottai | G | Outlet N2 Air M/C and SMPS box problem. | Breakdown | Nepolean | 2024-08-24 | - | N2 air M/C problem rectified by replacing of new SMPS box with one on/off switch fuse. New PCB board one no changed.Working in good condition.
CL5058 | 2024-08-24 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-24 | - | Redeem Litre- 45.21 L Amount Rs- 2580.00 Total No's of Redeem vehicle - 10 Auto- 8 Car-02 - Completed
CL5059 | 2024-08-25 | Uthamapalayam | D | Outlet dispensing line air hose leakage. | Breakdown | Kamaraj | 2024-08-25 | - | Dispensing line air leakage arrestedby tigtening of all nuts and all leakage tested.Both Compressor oil changed.and PMR also completed. Dp valve diaphragm checked my all outlets.
CL5060 | 2024-08-25 | Kumbakonam | D | Outlet 'A' side DP diaphragm damaged. | Breakdown | Sureshkumar | 2024-08-25 | - | A' side the damaged DP diaphragm replaced by new one.'A' side working condition normal.Both side nozzle rope changed. Dispenser vapour line ROV gas leakage problem rectified by cleaning. Total testing : 20.84 ltr. yesterday testing :6.65 ltr
CL5061 | 2024-08-25 | Erode | D | Outlet DP value checking work. | Preventive | Avinash | 2024-08-25 | - | DP value checking completed. Testing liters: A side -0.14 Lts
CL5062 | 2024-08-25 | Ammapettai | D | Outlet DP value checking work. | Preventive | Avinash | 2024-08-25 | - | DP value checking completed. Testing liters: B side -0.47 Lts
CL5063 | 2024-08-25 | Namakkal 1 | G | Outlet N2 air inflator filling problem, | Breakdown | Nivas | 2024-08-25 | - | N2 air inflator filling problem resolved by cleaning of solenoid coil.Working in good condition.
CL5064 | 2024-08-25 | T.V.Koil | D | Outlet DP value checking work. | Preventive | Vigneshwaran | 2024-08-25 | - | Dispenser DP value has been checked. DP value condition normal. Testing liter: 0.49 ltr
CL5065 | 2024-08-25 | Avadi | D | Outlet DP value checking work. | Preventive | Suneel Sagar | 2024-08-25 | - | No problem with dp valve diaphram in 4 nozzles
CL5066 | 2024-08-25 | Virudhunagar | D | Outlet DP value checking work. | Preventive | Kathiresan | 2024-08-25 | - | DP value checking completed. Testing liters: B side -0.63 Lts
CL5067 | 2024-08-25 | Tirunelveli | D | Outlet DP value checking work. | Preventive | Kathiresan | 2024-08-25 | - | DP value checking completed. Testing liters: B side -0.51 Lts
CL5068 | 2024-08-25 | Madurai Villapuram | D | Outlet DP value checking work. | Preventive | Kathiresan | 2024-08-25 | - | DP value checking completed. Testing liters: B side -1.99 Lts
CL5069 | 2024-08-25 | Madurai Ellis nagar | D | Outlet DP value checking work. | Preventive | Kathiresan | 2024-08-25 | - | DP value checking completed. Testing liters: B side -1.87 Lts
CL5070 | 2024-08-25 | Tenkasi | D | Outlet DP value checking work. | Preventive | Kathiresan | 2024-08-25 | - | DP value checking completed. Testing liters: B side -0.40 Lts
CL5071 | 2024-08-25 | Maduari 3 | D | Outlet DP value checking work. | Preventive | Kathiresan | 2024-08-25 | - | DP value checking completed. Testing liters: B side -0.34 Lts
CL5072 | 2024-08-25 | Palladam 1 | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-25 | - | No problem with DP valve diaphram in both sides,.
CL5073 | 2024-08-25 | Palladam 2 | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-25 | - | No problem with DP valve diaphram in both sides,.
CL5074 | 2024-08-25 | Sulur | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-25 | - | No problem with DP valve diaphram in both sides,.
CL5075 | 2024-08-25 | Saravanampatty | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.01 lts B side -0.02 Lts
CL5076 | 2024-08-25 | Dharapuram | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-25 | - | No problem with DP valve diaphram in both sides,.
CL5077 | 2024-08-25 | Udumalpet | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-25 | - | No problem with DP valve diaphram in 4 nozzles
CL5078 | 2024-08-25 | Vadivelan nagar | D | Outlet DP value checking work. | Preventive | Suneel Sagar | 2024-08-25 | - | No problem with DP valve diaphram in 4 nozzles. Testing liters: A side : 0.61 lts B side -0.37 Lts C side - 0.23 Lts D side - 0.17 Lts
CL5079 | 2024-08-25 | Ayothiyapattinam | D | Outlet 'B' side DP diaphragm damaged. | Breakdown | Prabu | 2024-08-25 | - | B' side DP diaphragm starting stage punchar and replaced by new one. Working in good condition. Total testing litre: 5.24 ltr.
CL5080 | 2024-08-25 | Chengalpattu | D | Outlet DP value checking work. | Preventive | Suneel Sagar | 2024-08-25 | - | No problem with DP valve diaphram in 2 nozzles
CL5081 | 2024-08-25 | Devakottai | D | Outlet DP value checking work. | Preventive | Nepolean | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -0.02 Lts
CL5082 | 2024-08-25 | Pudukkottai | D | Outlet DP value checking work. | Preventive | Nepolean | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -0.00 Lts
CL5083 | 2024-08-25 | Manapparai | D | Outlet DP value checking work. | Preventive | Nepolean | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -0.05 Lts
CL5084 | 2024-08-25 | Cantonment | D | Outlet DP value checking work. | Preventive | Lingeshwaran | 2024-08-25 | - | No problem with DP valve diaphram in 4 nozzles. Testing liters: C side : 0.06 lts D side -0.31 Lts E side - 0.27 Lts F side - 0.59 Lts
CL5085 | 2024-08-25 | Krishnagiri | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -0.02 Lts
CL5086 | 2024-08-25 | Hosur | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -0.00 Lts
CL5087 | 2024-08-25 | Dharmapuri | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.16 lts B side -0.05 Lts
CL5088 | 2024-08-25 | Tharamangalam | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.01 lts B side -0.06 Lts
CL5089 | 2024-08-25 | Ayothiyapattinam | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -5.27 Lts
CL5090 | 2024-08-25 | Omalur | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.00 lts B side -0.04 Lts
CL5091 | 2024-08-25 | Salem 2 | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.01 lts B side -0.00 Lts
CL5092 | 2024-08-25 | Uthamacholapuram | D | Outlet DP value checking work. | Preventive | Prabu | 2024-08-25 | - | DP value checking completed. Testing liters: A side : 0.03 lts B side -0.02 Lts
CL5093 | 2024-08-26 | Sangagiri | C | Rule 18 work | Certification | Avinash and Sureshkumar | 2024-08-26 | - | Rule 18 work completed.Earth value tested and regenerated and leak checked.
CL5094 | 2024-08-26 | Kodungaiyur | D | Outlet DP value checking work. | Preventive | Suneel Sagar | 2024-08-26 | - | No problem with DP valve diaphram in 2 nozzles. Testing ltrs without mobile. A- 0.25 B- 0.67
CL5095 | 2024-08-26 | Kattupakkam | D | Outlet DP value checking work. | Preventive | Suneel Sagar | 2024-08-26 | - | No problem with DP valve diaphram in 4 nozzles.
CL5096 | 2024-08-26 | Avinashi | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-26 | - | No problem with DP valve diaphram in 4 nozzles.
CL5097 | 2024-08-26 | Kankeyam | D | Outlet DP value checking work. | Preventive | Gowtham | 2024-08-26 | - | No problem with DP valve diaphram in 4 nozzles.
CL5098 | 2024-08-26 | Dindugal | D | Outlet dispensing motor Lovejoy spider damaged. | Breakdown | Kamaraj | 2024-08-26 | - | The damaged dispensing motor Lovejoy spider is replaced by new one.Working in good condition.
CL5099 | 2024-08-26 | Sangagiri | C | Stamping and Calibration work | Certification | Avinash and Sureshkumar | 2024-08-26 | - | Stamping and Calibration work completed. Calibration report: A side testing -151.15 B side testing - 214.00 Total testing -365.15 K Factor no changes A- 10100 B- 10100 A side 10 Lts =9.97 B side 10 Lts =9.98
CL5100 | 2024-08-26 | Tiruchengode | C | Stamping and Calibration work | Certification | Avinash and Sureshkumar | 2024-08-26 | - | Stamping and Calibration work completed. Calibration report: A side testing -208.64 B side testing - 152.18 Total testing -360.82 K Factor no changes A- 10000 B- 10000 A side 10 Lts = 10.06 B side 10 Lts = 10.02
CL5101 | 2024-08-26 | Avadi | D | Outlet B side dispensing hose damaged. | Breakdown | Suneel Sagar | 2024-08-26 | - | The damaged B side dispensing hose replaced by new one and old one has been sent for recrimpling.
CL5102 | 2024-08-26 | Ariyamangalam | D | Outlet "A" side nozzle leakage problem. | Breakdown | Pandidurai | 2024-08-26 | - | "A" side nozzle leakage problem rectified by changing of one new front 'O' ring.Working in good condition.
CL5103 | 2024-08-26 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-08-26 | - | Redeem Litre- 22.26 L Amount Rs- 1270.00 Total No's of Redeem vehicle - 5 Auto- 3 Car-02 - Completed
CL5104 | 2024-08-26 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-26 | - | Redeem Litre- 25.89 L Amount Rs- 1478.00 Total No's of Redeem vehicle - 7 Auto- 7 Car-0 - Completed
CL5105 | 2024-08-27 | Thiruvaiyaru | D | Outlet dispenser "A" and "B" both side LED tube light and "A" side preset amount not working. | Breakdown | Pandidurai | 2024-08-27 | - | Dispenser "A" and "B" both side LED tube light 2 no's changed. "A" side preset amount not working problem resolved by re-connecting of cable.Working in good condition.
CL5106 | 2024-08-27 | Tiruchengode | C | Outlet Rule 18 work. | Certification | Avinash and Sureshkumar | 2024-08-27 | - | Rule 18 work completed and earth regenerated, Earth value and leakage checked. DP value checked.Work completed.
CL5107 | 2024-08-27 | Velacherry | G | Fire extinguisher service | Preventive | Suneel Sagar | 2024-08-27 | - | Fire extinguisher service completed and renewal certificate obtained
CL5108 | 2024-08-27 | Ayothiyapattinam | C | Stamping and Calibration work | Certification | Prabu and Sureshkumar | 2024-08-27 | - | Stamping and Calibration work completed. Calibration report: A side testing -150.20 B side testing - 152.18 Total testing -302.38 K Factor no changes A- 10000 B- 10000 A side 10 Lts =9.97 B side 10 Lts =9.97
CL5109 | 2024-08-27 | Tharamangalam | C | Stamping and Calibration work | Certification | Prabu and Sureshkumar | 2024-08-27 | - | Stamping and Calibration work completed. Calibration report: A side testing -153.61 B side testing - 125.63 Total testing -279.24 K Factor no changes A- 10250 B- 10250 A side 10 Lts =9.92 B side 10 Lts =10.00
CL5110 | 2024-08-27 | Madurai Ellis nagar | D | Outlet 'A and B' dispenser bottom side "25NB" ROV rotation problem. | Breakdown | Kathiresan | 2024-09-09 | - | Outlet "A&B" dispenser bottom side ROV problem resolved by interchanging of Tank 2 unloading point ROV. Working Fine. Then "B" side nozzle hammer teeth 4 nos changed and Tank 1 dispensing solenoid coil interchanged to Tank 1 unloading solenoid coil.Working in good condition. PMR also completed.
CL5111 | 2024-08-27 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-27 | - | Redeem Litre- 37.54 L Amount Rs- 2142.46 Total No's of Redeem vehicle - 11 Auto- 10 Car-01 - Completed
CL5112 | 2024-08-28 | Palladam 2 | G | PMR Work | Preventive | Gowtham | 2024-08-28 | - | PMR work completed.
CL5113 | 2024-08-28 | Ariyamangalam | A | Loyalty program redeem | Development | Pandidurai | 2024-08-28 | - | Redeem Litre- 5.08 L Amount Rs- 290.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-01 - Completed
CL5114 | 2024-08-28 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-28 | - | Redeem Litre- 10.23 L Amount Rs- 584.00 Total No's of Redeem vehicle - 4 Auto- 4 Car-0 - Completed
CL5115 | 2024-08-29 | Musiri | D | Outlet DP valve testing purpose. | Preventive | Nivas | 2024-08-29 | - | Day shift DP valve testing completed. Testing - 0.13 lit
CL5116 | 2024-08-29 | Mulanur | G | Outlet PMR work and Automation equipment maintenance. | Preventive | Thirumalaisamy | 2024-08-29 | - | PMR completed and Automation equipment maintenance completed.
CL5117 | 2024-08-29 | Perambalur | G | Outlet online ups back up issue and unloading fill point vapour line ROV leakage problem. | Breakdown | Pandidurai | 2024-08-29 | - | Online ups back up issue problem rectified by changing of 3 nos of new 12V 7AH batteries. Unloading fill point vapour line ROV leakage arrested by claening and tightening ogf screws. The damaged Air machine clip connector 1 No changed. Total leakage checked and PMR also completed. DP valve checked Working in good condition.
CL5118 | 2024-08-29 | Madurai Villapuram | D | Outlet 'C & D' dispenser DP Valve diaphragm and "D" Side LPG Hose 5 mtrs damaged. | Breakdown | Kathiresan | 2024-08-29 | - | C & D' dispenser DP Valve diaphragm changed due to 3 years of usage and started to damage.The damaged "D" Side LPG Hose 5 mtrs replaced.Working in good condition. Testing : C side = 5 ltrs. D side = 6.43 ltrs. Total = 11.43.ltrs
CL5119 | 2024-08-29 | Kankeyam | D | Outlet dispensing motor cooling fan damage. | Breakdown | Gowtham | 2024-08-29 | - | The damaged dispensing motor cooling fan replaced with new pvc cooling fan.Working normal.
CL5120 | 2024-08-29 | Kinathukadavu | G | Outlet general visit work. | Preventive | Gowtham | 2024-08-29 | - | Outlet general visit completed.
CL5121 | 2024-08-30 | Udumalpet | G | Outlet PMR and DP valve function work. | Preventive | Gowtham | 2024-08-30 | - | PMR completed and DP valve function checked. Work completed.
CL5122 | 2024-08-30 | Kumbakonam | D | Outlet DP valve testing purpose. | Preventive | Pandidurai | 2024-08-30 | - | DP valve testing completed. Testing =0.16 lit
CL5123 | 2024-08-30 | Namakkal 2 | A | Outlet Automation Testing. | Preventive | Nivas | 2024-08-30 | - | Automation testing completed :. Testing -2 lit.
CL5124 | 2024-08-30 | Velacherry | G | Outlet commissioning and all equipment installation work. | New project | Prakash and Chandrasekar | 2024-08-30 | - | Commissioning work completed. All equipment working. ATG installation planned tomorrow. Dispenser stamping completed.
CL5125 | 2024-08-30 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-30 | - | Redeem Litre- 54.02 L Amount Rs- 3083.00 Total No's of Redeem vehicle - 13 Auto- 12 Car-01 - Completed
CL5126 | 2024-08-31 | Avinashi | G | Outlet General check up work | Preventive | Gowtham | 2024-08-31 | - | Fencing painting work completed and pipeline painting going on. Canopy false ceiling completed.
CL5127 | 2024-08-31 | Perundurai | D | Outlet dispensing motor spider damaged. | Breakdown | Avinash | 2024-08-31 | - | The damaged dispensing motor spider replaced by new one.Work completed.
CL5128 | 2024-08-31 | Namakkal 1 | D | Outlet dispenser A side nozzle leakage problem. | Breakdown | Nivas | 2024-08-31 | - | Dispenser A side nozzle leakage problem rectified by changing of new one.Working in good condition. Testing - 0.83 lit.
CL5129 | 2024-08-31 | Madurai Villapuram | A | Outlet Automation TP-link access point problem. | Breakdown | Kathiresan | 2024-08-31 | - | Automation TP-link access point problem resolved by installation of new one and control panel tank 1 motor indicator changed.Work completed.
CL5130 | 2024-08-31 | Virudhachalam | D | Outlet DP valve testing purpose. | Preventive | Pandidurai | 2024-08-31 | - | DP valve testing completed. Testing =0.19 lit
CL5131 | 2024-08-31 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-08-31 | - | Redeem Litre- 48.84 L Amount Rs- 2786.52 Total No's of Redeem vehicle - 11 Auto- 10 Car-01 - Completed
CL5132 | 2024-09-01 | Bhavani | R | Outlet online UPS backup issue and nozzle DP valve checkup work. | Breakdown | Avinash | 2024-09-01 | - | Online UPS back up issue rectified by replacing of 3 nos of new 12 V 40 Ah batteries. All nozzle DP value functioning checked. Testing B side = 0.48 Lts
CL5133 | 2024-09-01 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-01 | - | Redeem Litre- 18.52 L Amount Rs- 1079.00 Total No's of Redeem vehicle - 5 Auto- 4 Car-01 - Completed
CL5134 | 2024-09-02 | Kinathukadavu | G | Outlet general visit | New project | Gowtham | 2024-09-02 | - | Outlet electrical work going on.
CL5135 | 2024-09-02 | Madurai Villapuram | D | Outlet "B" side nozzle switch problem. | Breakdown | Kathiresan | 2024-09-02 | - | "B" side nozzle switch problem rectified by changing of new " NO' element ".Working in good condition.
CL5136 | 2024-09-02 | Velacherry | T | Outlet new ATG configuration work. | Preventive | Suneel sagar | 2024-09-02 | - | New ATG configuration and displaying in both tanks levels is completed.
CL5137 | 2024-09-03 | Vedachandur | C | Rule 18 work | Certification | Sureshkumar and Nepolean | 2024-09-03 | - | Rule 18 completed
CL5138 | 2024-09-03 | Vedachandur | C | Calibration and Stamping work | Certification | Sureshkumar and Nepolean | 2024-09-03 | - | Stamping report :A side k factor : 10080 B side k factor : 10100 Both side k factor no changes. A side testing : 315.48 lit B side testing : 166.60 lit A side 10.00 lit =9.99 B side 10.00 lit= 9.98
CL5139 | 2024-09-03 | Vedachandur | T | Outlet bothside side DP valve Diaphragm and in tank area earth pit problem. | Breakdown | Sureshkumar and Nepolean | 2024-09-03 | - | Dispenser both side DP valve diaphragm changed by new one and working in good condition. Tank area side Earth pit 2 no GI pita damaged two earth pit problem to be rectfive. All emergency switchs are working in good condition.
CL5140 | 2024-09-03 | Kinathukadavu | G | Outlet general inspection | New project | Gowtham | 2024-09-03 | - | Cables are received today and .GI flat welding and cable conduit laying work going on.
CL5141 | 2024-09-03 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-03 | - | Redeem Litre- 12.22 L Amount Rs- 713.00 Total No's of Redeem vehicle - 5 Auto- 5 Car-0 - Completed
CL5142 | 2024-09-04 | Kodungaiyur | G | Outlet PMR and unloding training work. | Preventive | Suneel Sagar | 2024-09-04 | - | PMR and unloding training is given to outlet person completed.
CL5143 | 2024-09-04 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-04 | - | Redeem Litre- 2.13 L Amount Rs- 124.00 Total No's of Redeem vehicle - 1 Auto- 1 Car-0 - Completed
CL5144 | 2024-09-05 | Chinnasalem | G | Outlet General inspection. | Preventive | Pandidurai | 2024-09-05 | - | Online ups serviced and fitting work completed. Dispenser both sides DP valve checked working fine. All leakage checked and PMR also completed.
CL5145 | 2024-09-05 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-05 | - | Redeem Litre- 6.67 L Amount Rs- 389.00 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL5146 | 2024-09-06 | Vellakoil | D | Outlet dispensing motor alignment problem. | Breakdown | Thirumalaisamy | 2024-09-06 | - | Dispensing motor alignment problem rectified by application of grease applied in dispensing pump.PMR completed.Automation equipment maintenance completed and DP valve diaphragm checked .Working in good condition.
CL5147 | 2024-09-06 | Madurai Ellis nagar | C | Outlet oil dispenser Re-Stamping work. | Certification | Kathiresan | 2024-09-06 | - | Oil dispenser Re-Stamping work completed. Open reading = 35 .00
CL5148 | 2024-09-06 | Ariyamangalam | C | Outlet dispenser calibration work: | Certification | Nepolean | 2024-09-06 | - | Dispenser calibration work comlpleted :Testing: A side: 159.37 B side: 168.29 C side: 158.24 D side: 151.04 Total :636.94 lit
CL5149 | 2024-09-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-06 | - | Redeem Litre- 13.29 L Amount Rs- 774.00 Total No's of Redeem vehicle - 3 Auto- 3 Car-0 - Completed
CL5150 | 2024-09-06 | Velacherry | R | General inspection | Preventive | Suneel Sagar | 2024-09-06 | - | Outlet internet connection work completed.Rate changed and printers configured. Ready for sales at tomorrow morning 6am.
CL5151 | 2024-09-07 | Velacherry | G | General inspection | Preventive | Suneel Sagar | 2024-09-07 | - | Outlet sales started at 6.30 am and all nozzles are in operation.
CL5152 | 2024-09-07 | Nasiyanur | R | Outlet online UPS problem. | Breakdown | Avinash | 2024-09-07 | - | Online UPS problem rectified by replacing of new 2 nos 12 v 40 Ah batteries with warranty.Working in good condition.
CL5153 | 2024-09-07 | Uthamacholapuram | R | Outlet online UPS problem. | Breakdown | Gowtham | 09-0-2024 | - | Online UPS problem resolved by replacing of new 1kva online UPS and installation completed.Working in good condition.
CL5154 | 2024-09-09 | T.V.Koil | D | Outlet dispenser B side nozzle problem. | Breakdown | Vigneshwaran | 2024-09-09 | - | Dispenser B side nozzle problem resolved by changing of 4 nos of hammer.Working in good condition.
CL5155 | 2024-09-09 | Velacherry | T | Outlet tank 1 unloding ROV and B side dispenser keypad problem. | Breakdown | Suneel Sagar | 2024-09-09 | - | Tank 1 unloding ROV problem resolved by changed by new one and B side dispenser keypad replaced and found Tank 2 ATG low and high relay cut off working satisfactory while unloding.
CL5156 | 2024-09-09 | Ariyamangalam | C | Stamping and calibration work | Certification | Nepolean | 2024-09-09 | - | F2 station today Stamping work completed. Calibration report: :K factor: Old A= 100180 B = 100143 C = 99766 D = 106600 A side D side new k factor changed A = 100990 D = 109260 Testing liter: B side: 150.14 lit A side: 501.61 lit D side : 748.15 lit
CL5157 | 2024-09-09 | Erode | C | Rule 19 work |  | Avinash | 2024-09-09 | - | Rule 19 work started. Dispenser reading: A -1289900.16 B -1585410.19 ATG - 5329 Tank to Tanker loading weight =3.335.
CL5158 | 2024-09-09 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-09 | - | Redeem Litre- 3.98 L Amount Rs- 232.00 Total No's of Redeem vehicle - 1 Auto- 1 Car-0 - Completed
CL5159 | 2024-09-10 | Mettala | G | New Outlet tank pit marking work. | New project | Nivas | 2024-09-10 | - | Tank pit marking completed.
CL5160 | 2024-09-10 | Erode | G | Outlet re commissioning work. | Preventive | Prakash | 2024-09-10 | - | Outlet re commissioning work started.
CL5161 | 2024-09-10 | Velacherry | T | Outlet ATG low relay problem. | Breakdown | Suneel Sagar | 2024-09-17 | 45 Munites | ATG relays reconfigured and found satisfactory.
CL5162 | 2024-09-10 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-10 | - | Redeem Litre- 8.60 L Amount Rs- 501.00 Total No's of Redeem vehicle - 2 Auto- 1 Car-01 - Completed
CL5163 | 2024-09-11 | Erode | G | Outlet re commissioning work. | Preventive | Prakash | 2024-09-11 | - | Outlet Rule 19 work completed. sales started all equipment working properly.
CL5164 | 2024-09-11 | Erode | C | Outlet Rule 19 and 18 work. | Certification | Avinash,Thirumalaisamy, Chandraselar and Lingeshwaran | 2024-09-11 | - | Rule 19 and 18 work completed and all area leak checked. Earth regenerated.Work completed.
CL5165 | 2024-09-11 | Ariyamangalam | T | Outlet tank area main flang air hose damaged. | Breakdown | Nepolean | 2024-09-11 | - | The damaged tank area main flang air hose rectified by changing with new air hose.( Tank area and Dispenser line and spear line) and compressor working condition normal and working in good condition.
CL5166 | 2024-09-11 | Aravakuruchi | C | Rule 19 work | Certification | Thirumalaisamy,Chandraselar and Lingeshwaran | 2024-09-11 | - | Outlet Rule 19 work started. Dispenser close reading: A -2243089.95 B -1761767.74 Tank-43%(Weight bridge not available).
CL5167 | 2024-09-12 | Namakkal 3 | C | Stamping and Calibration work | Certification | Nivas | 2024-09-12 | - | Stamping and calibration work completed Calibration report: A side testing -145.34 B side testing -160.61 Total testing - 305.95 K Factor No changes A- 10000 B- 10000 A side 10 Lts =9.97 B side 10 Lts =9.99
CL5168 | 2024-09-12 | Palladam 2 | D | Outlet A side nozzle hammer damaged. | Breakdown | Gowtham | 2024-09-12 | - | The damaged A side nozzle hammer 4 nos. replaced. Reading -835191.71
CL5169 | 2024-09-12 | Aravakuruchi | C | Rule 19 work | Certification | Prakash and Vigneshwaran | 2024-09-13 | - | Rule 19 work completed
CL5170 | 2024-09-12 | Velacherry | R | Outlet stevilzer Y phase variac and tank 2 HLA element problem. | Breakdown | Suneel Sagar | 2024-09-12 | - | The damaged(burnt) stevilzer Y phase variac replaced by new one. Tank 2 HLA element problem persists and same to be replaced by new one and now working in by pass mode.
CL5171 | 2024-09-12 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-12 | - | Redeem Litre- 14.37 L Amount Rs- 836.14 Total No's of Redeem vehicle - 1 Auto- 1 Car-01 - Completed
CL5172 | 2024-09-13 | Aravakuruchi | C | Outlet rule 18 and 19 work. | Certification | Thirumalaisamy | 2024-09-13 | - | Outlet rule 18 and 19 work completed.All pipe line leak checked and earth regenerated.Both motor shed work completed.EB room rubber mat provided.
CL5173 | 2024-09-13 | Chengalpattu | D | Outlet dispensing pump mp spider problem. | Breakdown | Suneel Sagar | 2024-09-13 | - | Dispensing pump mp spiderproblem resolved by replaced by new one. PMR also completed
CL5174 | 2024-09-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-13 | - | Redeem Litre- 16.48 L Amount Rs- 961.00 Total No's of Redeem vehicle - 6 Auto- 6 Car-01 - Completed
CL5175 | 2024-09-14 | Aravakuruchi | G | Outlet unloading training and Automation equipment maintenance work. | Preventive | Thirumalaisamy | 2024-09-14 | - | Unloading training given to pump staff and PMR completed.Automation equipment maintenance completed.
CL5176 | 2024-09-14 | Cantonment | D | Outlet dispenser C side nozzle hose sleeve damage. | Breakdown | Chandrasekar | 2024-09-14 | - | The damaged C side nozzle hose sleeve replaced by new 5 metre hose.Working in good condition. Testing -0.85 litre Reading-5088400.54
CL5177 | 2024-09-14 | Avadi | G | PMR Work | Preventive | Suneel Sagar | 2024-09-14 | - | PMR completed
CL5178 | 2024-09-14 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-14 | - | Redeem Litre- 8.65 L Amount Rs- 504.00 Total No's of Redeem vehicle - 2 Auto- 2 Car-0 - Completed
CL5179 | 2024-09-16 | Thanjavur | C | Rule 18 work | Certification | Pandidurai,Chandrasekar & Lingeshwaran | 2024-09-16 | - | Rule - 18 work completed and earth regenerated. Total all leakage checked.The damaged unloading air line hose, tank area to EB room replaced by new one. Control panel input online ups working in good condition.
CL5180 | 2024-09-17 | Vellakoil | R | Outlet online UPS mother board issue. | Breakdown | Thirumalaisamy | 2024-10-05 | - | Online UPS motherboard issue resolved by installation of new UPS.
CL5181 | 2024-09-18 | Palladam 2 | C | Stamping and Calibration work | Certification | Gowthan and Sureshkumar | 2024-09-18 | - | Calibration details:- K Factor A&B - 10000 A side - 9.94/10.00 B side - 9.93/10.00 Testing ltr - 330.18 ltr
CL5182 | 2024-09-18 | Avinashi | C | Stamping and Calibration work | Certification | Gowthan and Sureshkumar | 2024-09-18 | - | Avinashi calibration details:- A side - 10.05/10.00 B side - 9.93/10.00 C side - 10.05/10.00 D side - 10.05/10.00 K Factor A side - 103500 B side - 100000 C side old / New - 10100/10000 D side - 10000 Testing ltr - 921.73 ltr
CL5183 | 2024-09-19 | Thuraiyur | R | Outlet online UPS and dispensing air hose problem. | Breakdown | Nivas | 2024-09-19 | - | Online UPS problem due to failure of 2 batteries and complaint raised for warranty claim. Now system power given in offline ups . Dispensing air hose replaced by new one .
CL5184 | 2024-09-19 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-19 | - | Redeem Litre- 6.15 L Amount Rs- 358.00 Total No's of Redeem vehicle - 1 Auto- 1 Car-0 - Completed
CL5185 | 2024-09-20 | Rasipuram | R | Outlet online UPS and dispensing solenoid coil air leak problem. | Breakdown | Nivas | 2024-09-20 | - | Online UPS problem rectified by changing of bold nut in battery due to rust formed and wire reconnected.Working in good condition and kept under observation.Dispensing solenoid coil air leak problem resolved by interchanging of new unloading coil.Work completed.
CL5186 | 2024-09-20 | Madurai Villapuram | G | Outlet office container main electrical and borewell motor MCB problem. | Breakdown | Kathiresan | 2024-09-20 | - | Office container main electrical problem resolved by reworked and bore motor MCB newly changed, Working in good condition.PMR also completed.
CL5187 | 2024-09-20 | Palladam 1 | R | Outlet gone to offline | Breakdown | Gowtham | 2024-09-20 | - | Outlet gone to offline due to replacement of new yenen board. .Reading : C side-1099166.32 D side - 908960.83
CL5188 | 2024-09-20 | Palladam 1 | R | Outlet gone to offline | Breakdown | Gowtham | 2024-09-20 | - | Outlet back online and working in good condition.
CL5189 | 2024-09-21 | Ramanathapuram | R | Outlet EB Panel 63 and stabilizer PCB board problem. | Breakdown | Kathiresan | 2024-09-24 | - | Servo stabilizer main "PCB board" and on line UPS PCB board replaced. Servo mode working fine. Dispenser DP valve diaphragm checked. Working in good condition.
CL5190 | 2024-09-21 | Neelambur | C | Stamping and Calibration work | Certification | Gowtham & Sureshkumar | 2024-09-21 | - | Calibration details:- K Factor : A&B -10035 Testing ltr - 317.48 ltr
CL5191 | 2024-09-21 | Sulur | C | Stamping and Calibration work | Certification | Gowtham & Sureshkumar | 2024-09-21 | - | Calibration details:- K Factor : A&B- 10175 Testing ltr - 385.76 ltr
CL5192 | 2024-09-21 | Saravanampatty | C | Stamping and Calibration work | Certification | Gowtham & Sureshkumar | 2024-09-21 | - | Calibration details:- K Factor: A- 9920 K Factor : B - 10015 Testing ltr - 370.11 ltr
CL5193 | 2024-09-21 | Kangeyam | C | Stamping and Calibration work | Certification | Gowtham & Sureshkumar | 2024-09-21 | - | Calibration details : C&D K factor - 10100 Testing ltr. - 597.23
CL5194 | 2024-09-21 | Bhavani | D | Outlet A,C,D nozzle teeth problem. | Breakdown | Avinash | 2024-09-21 | - | A,C,D nozzle teeth problem rectified by changing of new one and C,D nozzle serviced and spring tension problem solved.Working in good condition. Testing : C = 0.83 Lts D = 0.87 Lts.
CL5195 | 2024-09-21 | Vellakoil | C | Stamping and Calibration work | Certification | Thirumalaisamy & Sureshkumar | 2024-09-21 | - | Dispenser all electronics components changed and testing completed.Calibration and stamped both(batchen and yenen) completed.
CL5196 | 22-0-2024 | Kinathukadavu | G | Outlet general visit | Preventive | Gowtham | 2024-09-22 | - | Outlet general visit completed.
CL5197 | 22-0-2024 | T.V.Koil | D | Outlet 'D' side on /off switch problem. | Breakdown | Sureshkumar | 2024-09-22 | - | D' side on /off switch problem resolved by changing of one number of new switch.Working in good condition.
CL5198 | 2024-09-23 | Vadivelan nagar | D | Outlet A and B side dispensing hose and nozzle prpoblem. | Breakdown | Suneel Sagar | 2024-09-23 | - | A & B side dispensing hose replaced by reclimpled hose and B side nozzle replaced by new one. Working in good condition. 'A side testing 0.87 ltrs 'B side testing 0.88 ltrs
CL5199 | 2024-09-23 | Dindugal | G | Outlet general visit | Preventive | Kamaraj | 2024-09-23 | - | Outlet all leakage tested. PMR completed.
CL5200 | 2024-09-23 | Vadivelan nagar | C | Rule-18,Rule-19 and Stamping work | Certification | Chandrasekar and Sureshkumar | 2024-09-23 | - | Started Rule-19 work
CL5201 | 2024-09-24 | T.V.Koil | D | Outlet dispenser C side nozzle On/Off switch problem. | Breakdown | Vigneshwaran | 2024-09-24 | - | Dispenser C side nozzle On/Off switch problem rectified by changing of new one.
CL5202 | 2024-09-24 | Vadivelan nagar | C | Calibration and Stamping work | Certification | Suneel Sagar | 2024-09-24 | - | calibration details:- 'A side - 10.10/10.00 'B side - 10.13/10.00 'C side - 10.10/10.00 'D side - 10.11/10.00 'Testing details: A-168.95 B-208.55 C-192.94 D-138.20 Total testing littre:708.64 K Factor : A side - 10070 B side - 10070 C side -10080 D side - 10080
CL5203 | 2024-09-24 | Batlagundu | G | Outlet general visit and PMR work. | Preventive | Kamaraj | 2024-09-24 | - | All leakage tested and PMR completed.
CL5204 | 2024-09-24 | Madurai 3 | D | Outlet Error 07 and flow valve problem. | Breakdown | Kathiresan | 2024-09-24 | - | Error 07 problem solved by adjusting the flow vave.DP valve diaphragm checked Working in good condition. Testing : 'A Side = 0.23 'B Side = 0.53 ltrs
CL5205 | 2024-09-24 | Velecherry | C | Re-calibration work | Certification | Suneel Sagar | 2024-09-24 | - | Re-calibration work completed.All nozzle k-factor changed. calibration details:- 'A side - 10.16/10.00 B side - 10.16/10.00 C side - 10.16/10.00 D side - 10.10/10.00 Testing details: A-147.30 B-230.75 C-286.87 D-150.85 Total testing littre:815.77 K Factor : A side old k-factor - 10000 A side New k-factor-9820 B side old k-factor-10000 B side New k-factor-9830 C side old k-factor-10000 C side New k-factor-9830 D side old k-factor-10000 D side New k-factor-9880
CL5206 | 2024-09-24 | Velecherry | C | Rule-18 work | Certification | Sunnel sagar,Chandrasekar and Sureshkumar | 2024-09-24 | - | Rule-18 work completed
CL5207 | 2024-09-25 | Madurai Ellis nagar | R | Outlet online UPS error 41 problem. | Breakdown | Kathiresan | 2024-09-27 | - | "On Line UPS" 12 v 42 ah battery backup problem rectified by changing of 3 nos of 12(v) 42 ah batteries and now Automation Working on-line UPS mode. Backup timing more than 15 min. DP valve diaphragm checked Working fine. Testing ; "A" Side = 0.42 "B" Side = 0.15 "C" Side = 0.52 "D" Side = 0.55 Total = 1.64 ltrs
CL5208 | 2024-09-25 | Tiruchengode | R | Outlet offline ups and ATG signal problem. | Breakdown | Avinash | 2024-09-25 | - | Offline ups problem rectified by replacing of one new 12 v 7 Ah battery and ATG signal problem in genset mode rectified.Working in good condition.
CL5209 | 2024-09-25 | Namakkal 1 | C | Rule 19 work | Certification | Nivas and Thirumalaisamy | 2024-09-27 | 34 Hrs | Rule 19 work started. Dispenser close reading A -2199618.07 B -793602.00 ATG-2050 Tanker weight-1.030 Rrule 18 and 19 work completed.All pipe line leak checked and both motor shed work completed.EB room rubber mat provided.Working in good condition.
CL5210 | 2024-09-25 | Vadivelan nagar | C | Rule 19 work | Certification | Suneel Sagar | 2024-09-25 | - | Rule -19 started at 9am, NDT completed and tomorrow nitrogen to be filled and commissioned.
CL5211 | 2024-09-26 | Kattupakkam | R | Outlet offline ups problem. | Breakdown | Suneel Sagar | 2024-09-25 | - | Offline ups problem resolved by replacing of 2 nos of new batteries.Working in good condition.
CL5212 | 2024-09-26 | Saravanampatty | C | Outlet stamping work | Certification | Gowtham | 2024-09-26 | - | Stamping completed and certificate will receive by tomorrow.
CL5213 | 2024-09-26 | Melur | D | Outlet dispensing solenoid valve and dispensing motor spider problem. | Breakdown | Kathiresan | 2024-09-26 | - | Dispensing solenoid valve set problem rectified by replaced due to plunger and dispensing motor spider to be replaced.
CL5214 | 2024-09-26 | Vadivelan nagar | C | Outlet tank 2 rule- 19 work. | Certification | Suneel Sagar | 2024-09-26 | - | Tank 2 rule- 19 work started and Tank-1 work completed and sales started.
CL5215 | 2024-09-27 | Kinathukadavu | G | General inspection | Preventive | Gowtham | 2024-09-27 | - | Inspected all the equipments and working in good condition
CL5216 | 2024-09-27 | Aravakuruchi | C | Stamping and Calibration work | Certification | Thirumalaisamy and Nivas | 2024-09-27 | - | Calibration report : 'A-nozzle=9.97 litters 'B-Nozzle=9.96 litters' K-Factor:- 'A-nozzle old k=10100 'A-nozzle new k=10050 B-Nozzle old k=10100 B-nozzle new k=10070 Testing:- A-Nozzle=451.69 B-nozzle=255.40
CL5217 | 2024-09-27 | Puliyur | C | Stamping and Calibration work | Certification | Thirumalaisamy and Nivas | 2024-09-27 | - | Calibration report : 'A-Nozzle=9.93 litters 'B-Nozzle=9.94 litters' K-Factor no change:- 'A-nozzle k=10050 B-nozzle k=10050 Testing:- A-Nozzle=133.26 B-nozzle=152.26
CL5218 | 2024-09-27 | Vadivelan nagar | C | Rule-19 and Rule -18 work | Certification | Suneel Sagar | 2024-09-27 | - | Both tanks Rule- 19 and Rule -18 work completed and all equipment performance satisfactory.
CL5219 | 2024-09-28 | Virudhachalam | D | Outlet "A" side Nozzle hammer and dispensing vapour line ROV leakage problem. | Breakdown | Pandidurai | 2024-09-28 | - | "A" side nozzle hammer problem rectified by changing of 4 no's of teeth and dispensing vapour line ROV leakage problem arrested by tigtening of nuts. Control panel Y- phase indication light 1 number changed. DP valve checked working in good condition. Total all leakage checked and PMR also completed.
CL5220 | 2024-09-28 | Dindugal | D | Outlet dispenser A side nozzle hose leakage. | Breakdown | Kamaraj | 2024-09-28 | - | Dispenser A side nozzle hose leakage arrested by changing of spare nozzle hose. Working in good condition. Testing litre : 1.84 lit.
CL5221 | 2024-09-28 | Avadi | C | Outlet Rule-18 work. | Certification | Suneel Sagar | 2024-09-28 | - | Rule-18 work completed and 4 nozzles Dp valve diaphram replaced by new one. Testing : A - 5 ltrs B - 5 ltrs C- 5ltrs D- 5 ltrs
CL5222 | 2024-09-28 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-09-28 | - | Redeem Litre- 12.26 L Amount Rs- 713.16 Total No's of Redeem vehicle - 1 Auto- 0 Car-1 - Completed
CL5223 | 2024-09-28 | Kattupakkam | C | Outlet Rule-18 work. | Certification | Suneel Sagar | 2024-09-28 | - | Rule-18 work completed & 4 nozzles Dp valve diaphram replaced by new one and VFD reconnected.
CL5224 | 2024-09-29 | Dharapuram | R | Outlet reading reverse problem. | Breakdown | Gowtham | 2024-09-29 | - | Outlet reading reverse problem due to power shutdown. (-94.17 ltr ). Now working normal.' Shift Cl/Op reading - 'A side - 240459.41 'B side - 227387.24
CL5225 | 2024-09-29 | Namakkal-1 | G | Outlet fire extinguisher service and renewal work. | Preventive | Nivas | 2024-09-29 | - | Fire extinguisher service and renewal completed.Fire ball 1 No's changed Training given to pump staff's
CL5226 | 2024-09-29 | Namakkal-3 | G | Outlet fire extinguisher service and renewal work. | Preventive | Nivas | 2024-09-29 | - | Fire extinguisher service and renewal completed.Fire ball 1 No's changed Training given to pump staff's
CL5227 | 2024-09-29 | Chengalpattu | C | Outlet Rule-18 work. | Certification | Suneel Sagar | 2024-09-29 | - | Rule-18 work completed and 2 nozzles Dp valve diaphram replaced by new one.
CL5228 | 2024-09-29 | Dharapuram | R | Outlet EB main line R phase problem. | Breakdown | Gowtham | 2024-09-29 | - | EB mainline R phase problem resolved by E.B technician and PMR completed.
CL5229 | 2024-09-30 | Tiruchengode | G | Fire extinguisher service,renewal and staff training | Preventive | Avinash | 2024-09-30 | - | Fire extinguisher service,renewal and staff training completed
CL5230 | 2024-09-30 | Nasiyanur | G | Fire extinguisher service,renewal and staff training | Preventive | Avinash | 2024-09-30 | - | Fire extinguisher service,renewal and staff training completed and one 9 kg ABC fire extinguisher replaced by spare. .
CL5231 | 2024-09-30 | Erode | G | Fire extinguisher service,renewal and staff training | Preventive | Avinash | 2024-09-30 | - | Fire extinguisher service,renewal and staff training completed and both 75 kg fire extinguisher powder replaced by new powder.
CL5232 | 2024-10-01 | Dharmapuri | G | Outlet general visit and unloading training. | Preventive | Prabu | 2024-10-01 | - | Verified the unloading ATG 85% cutoff and dispenser diaphragm checked.Unloading training given pump staff
CL5233 | 2024-10-01 | Theni | D | Outlet dispenser A side display problem. | Breakdown | Kamaraj and Nepolean | 2024-10-02 | - | Dispenser A side display problem is due to mother board and new mother board changed. Both side working condition normal.one day under observation. Old mother bord reading: A side : Opening - 331133.43 Closing - 331133.43 B side : Opening -296432.92 Closing - 296564.40 Testing - 0.620 New mother bord reading : A side : Opening - 708366.74 Closing- 708371.61 B side : Opening - 903091.53 Closing - 903101.21 Testing - 5.11.
CL5234 | 2024-10-01 | Vadivelan nagar | D | Outlet master solenoid coil and panel pressure problem. | Breakdown | Suneel Sagar | 2024-10-01 | - | Solenoid coil replaced by new one and panel pressure switch adjusted
CL5235 | 2024-10-02 | Tenkasi | R | Outlet stabilizer and dispensing motor sound and vibration problem. | Breakdown | Kathiresan | 2024-10-02 | - | Dispensing motor sound and vibration problem rectified by re alignment and now working in normal sound and vibration.Then on line UPS Battery backup problem resovlved but next time battery to be replaced.Dispensing "25 NB" vapour line LPG leakage arrested . PMR also done. DP valve diaphragm Checked. Working in good condition.
CL5236 | 2024-10-02 | T.V.Koil | D | Outlet dispenser 'C 'Nozzle hammer problem. | Breakdown | Vigneshwaran | 2024-10-02 | - | Dispenser 'C 'Nozzle problem resolved by changing of 4 nos of hammer.
CL5237 | 2024-10-03 | Kangeyam | G | Outlet compressor oil checking and PMR work. | Preventive | Gowtham | 2024-10-03 | - | Compressor oil changed and PMR completed
CL5238 | 2024-10-03 | Theni | D | Outlet dispenser mother board problem. | Breakdown | Nepolean | 2024-10-03 | - | Dispenser mother board problem resolved by changing of one new mother board. A side metering unit - Angle valve LPG leackage problem rectified.Working in good condition.
CL5239 | 2024-10-03 | Madurai-3(Pandikoil) | T | Outlet CP value drop down and CP reference failure. | Breakdown | Kathiresan | 2024-10-23 | - | Outlet CP Value is drop down rectified by installation of new CP reference C.P Value : R1 - C1 = -0.230 R1 -C2 = -0.37 R1- A1 = -1.140 R1 - A2 = -1.200 R1 -A3 =-1.248 R1 - A4 =-1.230 After looping : -0.67
CL5240 | 2024-10-03 | Manapparai | D | Outlet dispenser A side On/Off switch problem, | Breakdown | Nepolean | 2024-10-03 | - | Dispenser A side On/Off switch problem resolved by changing of one new switch and working in good condition.
CL5241 | 2024-10-04 | Madurai Ellis nagar | R | Outlet on line UPS temperature Error problem. | Breakdown | Kathiresan | 2024-10-04 | - | On line UPS temperature error due to not properly working of cooling fan and the problem resolved by changing of new fan.Working in good condion.
CL5242 | 2024-10-04 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-04 | - | Redeem Litre- 6.71 L Amount Rs- 400.00 Total No's of Redeem vehicle - 1 Auto- 0 Car-1 - Completed
CL5243 | 2024-10-05 | Mettupalayam | D | Outlet PMR work and CP value found below average problem. | Breakdown | Gowtham | 2024-10-05 | - | PMR completed. DP valve function checked and working in good condition. CP value found below average range. Dispenser vapour ROV and unloading liquid ROV leakage arrested. B side nozzle fitting replaced. Testing ltr.0.99 ltr. CP Reading : R1 C1 - -0.322 R C2 - -0.246 R A1 - -0.480 R A2 - -1.344 R A3 - -0.743 R A4 - -0.640 After Loop : -0.731
CL5244 | 2024-10-05 | Karur | T | Outlet unloading motor MCB problem. | Breakdown | Thirumalaisamy | 2024-10-05 | - | Unloading motor MCB new changed due to Y phase terminal damage.New 1kvA online UPS installed.Working in good condition and back up time near 40min..B side nozzle hammer new changed.
CL5245 | 2024-10-05 | Namakkal 3 | G | Outlet PMR work. | Preventive | Nivas | 2024-10-05 | - | PMR completed.
CL5246 | 2024-10-05 | Cantonment | D | Outlet pump nozzle hose sleeve damaged. | Breakdown | Chandrasekar | 2024-10-05 | - | Both pump nozzle hose 5 metre new one changed due to nozzle hose sleeve damage condition.Working in good condition. .D.Testing-0.85 litre D.Reading-4841447.85 B.Testing-1.09 litre B.Reading-9146527.68 D.pump on /off switch one no element changed.
CL5247 | 2024-10-05 | Mulanur | R | Outlet B phase issue in both EB and genset mode. | Breakdown | Thirumalaisamy | 2024-10-07 | 1.15 Hrs | B phase issues both EB and genset mode resolved by replacing with new change over.Working in good condition
CL5248 | 2024-10-05 | Avadi | D | Outlet D side dispensing hose damaged. | Breakdown | Suneel Sagar | 2024-10-05 | - | The damaged D side dispensing hose replaced by new one.
CL5249 | 2024-10-06 | Namakkal 2 | R | Outlet control panel voltage scanner damaged. | Breakdown | Nivas | 2024-10-08 | - | Outlet voltage scanner replaced by new one now loop removed and online UPS 12 V 7 Ah battery replaced by 3 New batteries backup 30 min.Working in ood condition.
CL5250 | 2024-10-07 | T.V.Koil | D | Outlet C and D both side DP value diaphragm problem. | Breakdown | Sureshkumar | 2024-10-07 | - | C and D both side DP value diaphragm problem rectified by changing of new one.Working in good condition.
CL5251 | 2024-10-07 | Pudukkottai | D | Outlet fire extinguisher service and renewal work and "A" side nozzle leakage problem. | Breakdown | Pandidurai | 2024-10-07 | - | Fire extinguisher service and renewal work completed.Training given to pump staff. "A" side nozzle leakage arrested by interchanging of 'O' ring. Unloading vapour line ROV air leakage arrested. Total all leakage checked and PMR also completed.
CL5252 | 2024-10-07 | Ramanathapuram | G | Outlet fire extinguisher renewal and service work. | Preventive | Kathiresan | 2024-10-07 | - | Fire extinguisher renewal and service done. "9 kg" fire extinguisher one number and fire ball one number replaced due to expired. Training given to pump staff.
CL5253 | 2024-10-08 | Kumbakonam | C | Outlet Rule - 18 work. | Certification | Pandidurai and Sureshkumar | 2024-10-08 | - | Rule - 18 work completed and Earth regenerated. Genset general service work done. "B" side DP valve diaphram one number newly changed. Total all leakage checked and PMR also completed.
CL5254 | 2024-10-08 | Thanjavur | D | Outlet "B" side DP valve diaphram problem and genset oil service work. | Breakdown | Pandidurai and Sureshkumar | 2024-10-08 | - | "B" side DP valve diaphram problem resolved by changing of new one. Genset oil service work completed.
CL5255 | 2024-10-08 | Palayam | R | Outlet EB mode not working. | Breakdown | Thirumalaisamy | 2024-10-08 | - | Outlet EB mode problem rectified by changing of new ELCP and PMR completed.
CL5256 | 2024-10-09 | Karaikudi | G | Outlet site marking work | New project | Prakash and Chandrasekar | 2024-10-08 | - | Outlet site marking work completed.
CL5257 | 2024-10-09 | Kinathukadau | G | Outlet N 2 testing work | New project | Prakash,Chandrasekar and Gowtham | 2024-10-09 | - | Outlet N 2 testing work completed.
CL5258 | 2024-10-10 | Perundurai | D | Outlet dispenser E 00 and E 10 Error. | Breakdown | Avinash | 2024-10-10 | 6 Hrs | Dispenser E 00 and E 10 Error rectified.Working in good condition after checking of all parameters and readings.
CL5259 | 2024-10-11 | Cantonment | D | Outlet C, D, E and F both yenen dispenser DP valve diaphragm problem. | Breakdown | Chandrasekar | 2024-10-11 | - | C, D, E and F both yenen dispenser DP valve diaphragm newly changed.Working in good condition. C.Testing.5.00 litre D.Testing.5.00 litre E.Testing.6.57 litre F.Testing.5.00 litre Total testing.21.57 litre
CL5260 | 2024-10-13 | Madurai Villapuram | G | Outlet Genset engine self motor wire damaged problem. | Breakdown | Kathiresan | 2024-10-22 | 25 Minutes | Now Genset engine self motor wire replaced..Working in good condition.Tomorrow new connector will be arranged.
CL5261 | 2024-10-13 | Kinathukadavu | G | Outlet fire extinguisher DCP loading. | Preventive | Gowtham | 2024-10-13 | - | Outlet fire extinguisher DCP loading completd
CL5262 | 2024-10-14 | Eral | C | Stamping and Rule-18 work | Certification | Sureshkumar and Kathiresan | 2024-10-14 | - | Calibration and stamping and Rule 18 work Completed.PMR also done. Earth regerated CP value = - 1.258 Earth Value = 3( v) Calibration Report : "A" Side - 10 = 9.96 "B" Side - 10 = 9.96 'K' Factor Report; "A" Side = 10050 "B" Side = 10050
CL5263 | 2024-10-14 | Thuraiyur | R | Outlet online UPS and A side nozzle problem. | Breakdown | Nivas | 2024-10-14 | - | Online UPS problem rectified by replacing of 2 new batteries with warranty and A side nozzle problem resolved by replacing of spare nozzle.Working in good condition. Testing - 0.78lit.
CL5264 | 2024-10-14 | Vadivelan nagar | R | Outlet stabilizer problem. | Breakdown | Suneel Sagar | 2024-10-14 | - | Stabilizer problem rctified by replacing of damaged mcb with new one.Working in good condition.
CL5265 | 2024-10-14 | Kodungaiyur | R | Outlet Automation cat6 cable and ATG signal cable damaged. | Breakdown | Suneel Sagar | 2024-11-22 | - | Automation and ATG probe new cables connected.Now sales is going on online.
CL5266 | 2024-10-14 | Ayothiyapattinam | T | Outlet tank and dispensing unloading air hose damaged. | Breakdown | Prabu | 2024-10-14 | - | The damaged tank and dispensing unloading air hose is replaced by new one and the burnt stabilizer Y phase line wire changed. Working in good condition. PMR also completed. CP value =1.01 Earth value = 2 (v)
CL5267 | 2024-10-15 | Velacherry | G | General inspection | Preventive | Suneel Sagar | 2024-10-15 | 30 Minutes | Sales stopped due to heavy rain and thunder storm.
CL5268 | 2024-10-15 | Kattupakkam | G | General inspection | Preventive | Suneel Sagar | 2024-10-15 | 30 Minutes | Sales stopped due to heavy rain and thunder storm.
CL5269 | 2024-10-15 | Vadivelan nagar | G | General inspection | Preventive | Suneel Sagar | 2024-10-15 | 30 Minutes | Sales stopped due to heavy rain and thunder storm.
CL5270 | 2024-10-15 | T.V.Koil | D | Outlet "C" side and D side nozzle leakage problem. | Breakdown | Pandidurai | 2024-10-15 | - | "C" side nozzle leakage arrested by servicing and one nozzle changed. "D" side nozzle the damaged front 'O' ring one number replaced.Working in good condition. .C side testing = 0.91 Ltr
CL5271 | 2024-10-16 | Madurai Ellis nagar | R | Outlet "NRV" and pressure relief valve problem. | Breakdown | Kathiresan | 2024-10-16 | - | "NRV" and pressure relief valve problem rectified by servicing the NRV and working in good condiotion.
CL5272 | 2024-10-17 | Perundurai | T | Outlet tank area dispensing line air hose damaged. | Breakdown | Avinash | 2024-10-17 | - | The damaged tank area dispensing line air hose replaced by new hose and Automation maintenance done. DP value checked. FRL unit to be replaced.PMR completed. Testing B side 0.24 Lts.
CL5273 | 2024-10-17 | Kinathukadavu | G | Outlet inuguration work | New project | Prakash and Krishna Balaji | 2024-10-17 | - | Outlet sales started all instruments working normal with online.
CL5274 | 2024-10-17 | Kinathukadavu | C | Stamping and Calibration work | Certification | Gowtham | 2024-10-17 |  | Calibration and Stamping completed. A side - 10.09/10.00 B side - 10.11/10.00 Reading A side opening - 294.65 B side opening - 277.60 Tank opening - 75% ATG - 7467.40 ltr A & B side K factor - 10000
CL5275 | 2024-10-17 | Rasipuram | T | Outlet tank area dispensing vapour line ROV air leak problem . | Breakdown | Nivas | 2024-10-17 | - | Tank area dispensing vapour line ROV air leak problem rectified by interchanging of unloading ROV.The damaged A side hose is recrimmed. DP valve checked. PMR completed. Testing=0.80 lit.
CL5276 | 2024-10-17 | Avadi | D | Outlet dispensing motor spider problem. | Breakdown | Suneel Sagar | 2024-10-17 | - | Dispensing motor spider problem resolved by replacing by new one.
CL5277 | 2024-10-17 | T.V.Koil | A | Loyalty program redeem | Development | Pandidurai | 2024-10-17 | - | Redeem Litre- 349.65 L Amount Rs- 20866.76 Total No's of Redeem vehicle - 67 Auto- 67 Car-0 - Completed
CL5278 | 2024-10-17 | Cantonment | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-17 | - | Redeem Litre- 795.41 L Amount Rs- 47476.54 Total No's of Redeem vehicle - 166 Auto- 164 Car-2 - Completed
CL5279 | 2024-10-17 | T.V.Koil | A | Loyalty program redeem | Development | Pandidurai | 2024-10-17 | - | Redeem program testing purpose "C" side = 4.77 litres.
CL5280 | 2024-10-17 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-17 | - | Redeem Litre- 182.94 L Amount Rs- 10907.00 Total No's of Redeem vehicle - 34 Auto- 30 Car-4 - Completed
CL5281 | 2024-10-17 | Cantonment | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-17 | - | Redeem program testing purpose "E" side testing =4.77 litres
CL5282 | 2024-10-18 | Ammapettai | T | Outlet unloading fill point vapour ROV open problem. | Breakdown | Avinas | 2024-10-18 | - | Uunloading fill point vapour ROV open problem resolved by servicing, leak checked, Automation maintenance done,DP value checked, cp value has dropped (- 0.695 v dc ) and PMR completed, Testing A side=0.15 Lts
CL5283 | 2024-10-18 | Dindugal | G | Outlet for fire extinguisher service work. | Preventive | Kamaraj | 2024-10-18 | - | Fire extinguisher 75 kg 2 Nos new DCP powder changed and for 10 kg fire extinguisher new DCP powder also changed.All fire extinguisher serviced and renewal done.
CL5284 | 2024-10-18 | Kattupakkam | D | Outlet B side keypad problem. | Breakdown | Suneel Sagar | 2024-10-18 | - | B side keypad problem rectified by replaced by new one.
CL5285 | 2024-10-18 | Madurai Ellis nagar | D | Outlet "A" and B side nozzles problem. | Breakdown | Kathiresan | 2024-10-18 | - | "A" side nozzle problem resolved by changining of 4 nos of hammer teeth and "B" Side nozzle problem rectified by changing of latch lock Set.Working in good condition.
CL5286 | 2024-10-18 | Salem 2 | D | Outlet dispensing liquid line pressure gauge problem. | Breakdown | Prabu | 2024-10-18 | - | Dispensing liquid line pressure gauge problem resolved by changing of oil drain and vent line pressure gauge interchanged.DP value checked.Working in good condition.
CL5287 | 2024-10-18 | T.V.Koil | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-18 | - | Redeem Litre- 964.29 L Amount Rs- 57555.25 Total No's of Redeem vehicle - 192 Auto- 188 Car-4 - Completed
CL5288 | 2024-10-18 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-18 | - | Redeem Litre- 484.63 L Amount Rs- 28898.30 Total No's of Redeem vehicle - 97 Auto- 91 Car-6 - Completed
CL5289 | 2024-10-18 | Cantonment | A | Loyalty program redeem | Development | Navaneetha krishnan | 2024-10-18 | - | Redeem Litre- 1096.08 L Amount Rs- 65424.95 Total No's of Redeem vehicle - 225 Auto- 224 Car-1 - Completed
CL5290 | 2024-10-19 | Mulanur | D | Outlet A side nozzle hammer and dispensing line pneumatic hose problem. | Breakdown | Thirumalaisamy | 2024-10-19 | - | A side nozzle problem rectified by changing of hammer teeths and tank area dispensing line pneumatic hose newly changed.PMR completed.Automation equipment maintenance completed.
CL5291 | 2024-10-19 | Neelambur | G | Outlet billing mobile and offline ups problem. | Breakdown | Gowtham | 2024-10-19 | - | Out of 2 billing mobile,one new mobile configured with our operation. Spare ups provided and faulty mobiles are given to service.
CL5292 | 2024-10-19 | T.V.Koil | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-19 | - | Redeem Litre- 930.87 L Amount Rs- 55558.84 Total No's of Redeem vehicle - 192 Auto- 181 Car-11- Completed
CL5293 | 2024-10-19 | Cantonment | A | Loyalty program redeem | Development | Navaneetha krishnan | 2024-10-19 | - | Redeem Litre- 1192.26 L Amount Rs- 71170.63 Total No's of Redeem vehicle - 262 Auto- 261 Car-1 - Completed
CL5294 | 2024-10-19 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-19 | - | Redeem Litre- 403.43 L Amount Rs- 24057.80 Total No's of Redeem vehicle - 86 Auto- 84 Car-2 - Completed
CL5295 | 2024-10-20 | Kinathukadau | G | Outlet general inspection. | Preventive | Gowtham | 2024-10-20 | - | After transaction, 2 minutes motor running program disabled. No leak found and basic training given to pump staff's.
CL5296 | 2024-10-21 | Tirunelveli | D | Outlet decanting motor and DOL starter problem. | Breakdown | Kathiresan | 2024-10-21 | - | Decanting motor problem rectified and DOL starter contactor problem resolved by rewiring and reset of contactor.Working in good condition. Then dispenser hose rope changed. 9 kg fire extinguisher 3 nos failure to be replaced. CP Reading ; Tank 1 = 1.140 Tank 2 = 1.125 Panel Earth value 1.8 (v).
CL5297 | 2024-10-21 | Kinathukadau | C | Outlet stamping certificate | Certification | Gowtham | 2024-10-21 | - | Outlet stamping certificate received
CL5298 | 2024-10-21 | Tharamangalam | D | Outlet dispenser A side nozzle and ROV air fitting leakage problem. | Breakdown | Prabu | 2024-10-21 | - | Dispenser A side nozzle leakage problem resolved by chaning of 4 nos of teeths and ROV air fitting leakage problem rectified. Dispenser DP values check done. CP reading . A1R1=1.379 A2R1=0.360 A3R1=0.413 A4R1=1.406 R1C1=0.518 R1C2=0.339 After looping=0.675
CL5299 | 2024-10-21 | T.V.Koil | D | Outlet A side nozzle service work | Preventive | Nepolean | 2024-10-21 | - | A side nozzle service and testing work completed A side testing : 1.13 lit.
CL5300 | 2024-10-21 | Cantonment | A | Loyalty program redeem | Development | Navaneetha krishnan | 2024-10-21 | - | Redeem Litre- 993.96 L Amount Rs- 59334.55 Total No's of Redeem vehicle - 223 Auto- 219 Car-24 - Completed
CL5301 | 2024-10-21 | T.V.Koil | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-21 | - | Redeem Litre- 733.10 L Amount Rs- 43758.21 Total No's of Redeem vehicle - 152 Auto- 137 Car-15 - Completed
CL5302 | 2024-10-22 | Madurai Villapuram | R | Outlet Online UPS" backup and error Problem. | Breakdown | Kathiresan | 2024-10-22 | - | Online UPS" backup and error problem rectified by replacing of new "On Line UPS 1 KVA". Working in good condition and backup timing more than 30 min. Old UPS hand over Jayavilas Office.
CL5303 | 2024-10-22 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-22 | - | Redeem Litre- 233.58 L Amount Rs- 13928.20 Total No's of Redeem vehicle - 54 Auto- 47 Car-7 - Completed
CL5304 | 2024-10-22 | T.V.Koil | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-22 | - | Redeem Litre- 514.05 L Amount Rs- 36685.32 Total No's of Redeem vehicle - 107 Auto- 94 Car-13 - Completed
CL5305 | 2024-10-22 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-22 | - | Redeem Litre- 709.32 L Amount Rs- 42338.82 Total No's of Redeem vehicle - 150 Auto- 147 Car-3 - Completed
CL5306 | 2024-10-23 | Thanjavur | C | Outlet calibration and stamping work | Certification | Pandidurai and Sureshkumar | 2024-10-23 | - | Calibration and stamping work completed and N2 compressor noise problem rectified. Calibration Report : "A" Side 10 ltrs = 9.95 "B" Side 10 ltrs = 9.97 "K" Factor Report : K factor no changes " A " Side K factor = 10000 " B " Side K factor = 10000 Testing Report : "A" Side = 124.13ltrs "B" Side = 153.77ltrs Total = 277.90ltrs
CL5307 | 2024-10-23 | Velacheery | T | Outlet unloding motor contactor amps problem. | Breakdown | Suneel Sagar | 2024-10-23 | - | Unloding motor contactor amps tripping problem rectified by adjusting from 5a to 7.5a.Working in good condition.
CL5308 | 2024-10-23 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-23 | - | Redeem Litre- 560.79 L Amount Rs- 33473.23 Total No's of Redeem vehicle - 117 Auto- 117 Car-10 - Completed
CL5309 | 2024-10-23 | Thuraiyur | C | Outlet Rule - 18 and Re-calibration work | Certification | Pandidurai and Sureshkumar | 2024-10-23 | - | Rule - 18 and Re-calibration work completed.General check up done and Total all leakage checked. Calibration Report : "A" Side 10 ltrs = 10.10 "B" Side 10 ltrs = 9.99 "K" Factor Report : K factor no changes " A " Side K factor = 100603 " B " Side K factor = 100623 Testing Report : "A" Side = 154.45ltrs "B" Side = 155.18ltrs Total = 309.63ltrs
CL5310 | 2024-10-23 | Madurai 3 | T | Outlet CP reference problem. | Breakdown | Kathiresan | 2024-10-23 | - | CP reference problem rectified by installation of new one. Working in good condition. Then dispensing line "40 NB ROV" steam LPG leakage arrested PMR also done. CP Reading : R1 C1 : 0.620 R1 C2 :0.630 R1 A1 : 1.560 R1 A2 : 1.620 R1 A3 :1.600 R1 A4 : 1.620
CL5311 | 2024-10-23 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-23 | - | Redeem Litre- 191.12 L Amount Rs- 11396.90 Total No's of Redeem vehicle - 42 Auto- 34 Car- 8 - Completed
CL5312 | 2024-10-24 | Uthamacholapuram | C | Outlet Stamping and Calibration work | Certification | Prabu and Sureshkumar | 2024-10-24 | - | Calibration and stamping work completed.General check up done. Calibration Report : "A" Side 10 ltrs = 10.01 "B" Side 10 ltrs = 9.99 "K" Factor Report : K factor no changes " A " Side K factor = 10010 " B " Side K factor = 10030 Testing Report : "A" Side = 133.03ltrs "B" Side = 142.91ltrs Total = 275.94ltrs.
CL5313 | 2024-10-24 | Kinathukadavu | G | Outlet staffs unloading training. | Preventive | Gowtham | 2024-10-24 | - | Outlet unloading training completed
CL5314 | 2024-10-24 | Uthamapalayam | D | Outlet dispenser bottom ROV air leakage problem. | Breakdown | Kamaraj | 2024-10-24 | - | Dispenser bottom ROV air leakage arrested. Air Compressor filter cleaned. general check up done.
CL5315 | 2024-10-24 | Virudhunagar | D | Outlet "A" side nozzle and "B" side"LPG hose damaged. | Breakdown | Kathiresan | 2024-10-24 | - | "A" side nozzle problem rectified by changing of new one and the damaged "B" side"LPG hose 0.50" mtrs new changed."B" side nozzle front "O" ring replaced.Working in good condition. Automation TP link access point out side installed .
CL5316 | 2024-10-24 | Ayiyamangalam | G | Outlet bore well motor pressure drop problem and D. G room switch board problem. | Breakdown | Nepolean | 2024-10-24 | - | Bore well motor pressure drop problem rectified by adjusting the pressure and working condition normal and D. G room new fan one no fixed . D. G room switch board problem resolved by changing of new 3 pin plug socket.
CL5317 | 2024-10-24 | Ayiyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-24 | - | Redeem Litre- 71.44 L Amount Rs- 4260.00 Total No's of Redeem vehicle - 17 Auto- 15 Car- 2 - Completed
CL5318 | 2024-10-24 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-24 | - | Redeem Litre- 362.80 L Amount Rs- 21660.15 Total No's of Redeem vehicle - 90 Auto- 88 Car- 2 - Completed
CL5319 | 2024-10-24 | Ayiyamangalam | D | Outlet A side nozzle service and testing work. | Preventive | Nepolean | 2024-10-24 | - | A side nozzle service and testing work worked Testing lit: 2.21 lit.
CL5320 | 2024-10-25 | Ayiyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-25 | - | Redeem Litre- 97.50 L Amount Rs- 5820.60 Total No's of Redeem vehicle - 20 Auto- 15 Car- 5 - Completed
CL5321 | 2024-10-25 | Ayiyamangalam | D | Outlet A side Ellis nagar nozzle service and testing work. | Preventive | Nepolean | 2024-10-25 | - | A side Ellis nagar nozzle service and testing work completed. Nozzle working condition normal. Two days observation. A side testing : 1.17 lit.
CL5322 | 2024-10-25 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-25 | - | Redeem Litre- 318.59 L Amount Rs- 19017.93 Total No's of Redeem vehicle - 66 Auto- 61 Car- 5 - Completed
CL5323 | 2024-10-25 | Kodungaiyur | C | Stamping work | Certification | Suneel Sagar | 2024-10-25 | - | Stamping work completed
CL5324 | 2024-10-25 | Cantonment | G | Fire extinguisher service work | Preventive | Chandrasekar | 2024-10-25 | - | Fire extinguisher service work completed.75 kg fire extinguisher pressure gauge 1 no's newly changed and all fire extinguisher condition is normal.
CL5325 | 2024-10-26 | Kodumudi | G | Outlet PMR and redeem points training | Preventive | Thirumalaisamy | 2024-10-26 | - | PMR completed and redeem points training given to pump staffs
CL5326 | 2024-10-26 | Udumalpet | G | Outlet PMR and redeem points training | Preventive | Gowtham | 2024-10-26 | - | PMR completed and redeem points training given to pump staffs
CL5327 | 2024-10-26 | Musiri | A | Outlet redeem point training work | Development | Nivas | 2024-10-26 | - | Outlet redeem point training work to pump staffs completed
CL5328 | 2024-10-26 | Thuraiyur | A | Outlet redeem point training work | Development | Nivas | 2024-10-26 | - | Outlet redeem point training work to pump staffs completed
CL5329 | 2024-10-26 | Ayiyamangalam | D | Outlet D side On/off switch problem.. | Breakdown | Nepolean | 2024-10-26 | - | D side On/off switch problem rectified by changing of new one.Working in good condition.
CL5330 | 2024-10-26 | Cantonment | G | Outlet N2 Air machine mouth(clip connector) problem. | Breakdown | Chandrasekar | 2024-10-26 | - | N2 Air machine mouth(clip connector) problem resolved by changing of new one.
CL5331 | 2024-10-26 | Cantonment | D | Outlet E.side two wheeler lpg tank cut off testing work. | Breakdown | Chandrasekar | 2024-10-26 | - | E.side two wheeler lpg tank cut off testing completed.E.side Testing.61.57 litre
CL5332 | 2024-10-26 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-26 | - | Redeem Litre- 66.73 L Amount Rs- 3980.00 Total No's of Redeem vehicle - 13 Auto- 8 Car- 5 - Completed
CL5333 | 2024-10-26 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-26 | - | Redeem Litre- 183.60 L Amount Rs- 10959.46 Total No's of Redeem vehicle - 41 Auto- 38 Car- 3 - Completed
CL5334 | 2024-10-26 | Nasiyanur | G | Outlet PMR and redeem points training | Preventive | Avinash | 2024-10-26 | - | PMR completed and redeem points training given to pump staffs
CL5335 | 2024-10-26 | Omalur | G | Outlet PMR and redeem points training | Preventive | Prabu | 2024-10-26 | - | PMR completed and redeem points training given to pump staffs
CL5336 | 2024-10-27 | Namakkal 1 | D | Dispenser A side keypad problem. | Breakdown | Nivas | 2024-10-27 | - | Dispenser A side keypad problem rectified by changing of new one.Working in good condition.
CL5337 | 2024-10-27 | T.V.Koil | D | Outlet Batchen dispenser A side nozzle problem. | Breakdown | Vigneshwaran | 2024-10-27 | - | Batchen dispenser A side nozzle prolem resolved by changing of o-ring.
CL5338 | 2024-10-27 | Erode | G | PMR Work | Preventive | Avinash | 2024-10-27 | - | PMR work completed.
CL5339 | 2024-10-28 | Avinashi | D | Outlet Batchen dispenser Error 20 problem, | Breakdown | Gowtham | 2024-10-30 | - | Loyalty program training provided to pump staff's. Batchen dispenser Error 20 problem resolved by installation of new IC.Working on good condition
CL5340 | 2024-10-28 | Ayothiyapattinam | A | Outlet loyalty program training. | Development | Prabu | 2024-10-28 | - | Loyalty program training given to pump staff's.
CL5341 | 2024-10-28 | Uthamacholapuram | A | Outlet loyalty program training. | Development | Prabu | 2024-10-28 | - | Loyalty program training given to pump staff's.
CL5342 | 2024-10-28 | Karur | D | outlet batchen dispenser main power fuse holder damaged. | Breakdown | Thirumalaisamy | 2024-10-28 | - | The damaged Batchen dispenser main power fuse holder newly changed.
CL5343 | 2024-10-28 | Melur | D | Outlet Dispensing motor vibration and noise problem. | Breakdown | Kathiresan | 2024-10-28 | - | Dispensing Motor vibration and noise problem resolved by replacing of damaged spider.Working in good condition. Loyalty program training given to pump staff.
CL5344 | 2024-10-28 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-28 | - | Redeem Litre- 80.81 L Amount Rs- 4848.90 Total No's of Redeem vehicle - 11 Auto- 6 Car- 5 - Completed
CL5345 | 2024-10-28 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-28 | - | Redeem Litre- 150.84 L Amount Rs- 9008.00 Total No's of Redeem vehicle - 43 Auto- 43 Car- 0 - Completed
CL5346 | 2024-10-28 | Cantonment | G | Outlet POS machine g-pay bill checking work. | Development | Sureshkumar | 2024-10-28 | - | Outlet POS machine g-pay bill checking work completed.. Testing littre:3.36
CL5347 | 2024-10-28 | T.V.Koil | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-28 | - | Redeem Litre- 167.12 L Amount Rs- 9977.03 Total No's of Redeem vehicle - 37 Auto- 30 Car- 07 - Completed
CL5348 | 2024-10-29 | Thuraiyur | A | Outlet loyalty training program | Development | Nivas | 2024-10-29 | - | Loyalty program training given to pump staff's
CL5349 | 2024-10-29 | Sangagiri | G | Outlet PMR work and DP value check. | Preventive | Avinash | 2024-10-29 | - | PMR completed and leak,DP value checked and reedem training given to pump staff.
CL5350 | 2024-10-29 | T.V.Koil | D | Outlet D side nozzle hose and A side hummer teeth problem. | Breakdown | Sureshkumar | 2024-10-29 | - | The damaged D side nozzle hose ( 5 meter) changed by new one and A side hummer teeth problem rectified by changing of 4 nos of new teeths.Working in good condition. D side reading: 2679711.12 Testing littre:0.94 litres
CL5351 | 2024-10-29 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-29 | - | Redeem Litre- 223.70 L Amount Rs- 13350.00 Total No's of Redeem vehicle - 42 Auto- 39 Car- 03 - Completed
CL5352 | 2024-10-29 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-29 | - | Redeem Litre- 37.07 L Amount Rs- 2210.00 Total No's of Redeem vehicle - 8 Auto- 6 Car- 02 - Completed
CL5353 | 2024-10-29 | Tharamangalam | A | Outlet loyalty training program | Development | Prabu | 2024-10-29 | - | Loyalty program training given to pump staff's
CL5354 | 2024-10-29 | Krishnagiri | A | Outlet loyalty training program | Development | Prabu | 2024-10-29 | - | Loyalty program training given to pump staff's
CL5355 | 2024-10-30 | Ammapettai | D | Outlet both nozzle teeths problem. | Breakdown | Avinash | 2024-10-30 | - | Outle both nozzle teeths problem rectified by changing by new one and reedem training given to pump staff.
CL5356 | 2024-10-30 | Bhavani | G | Outlet PMR and c side nozzle serviced. | Preventive | Avinash | 2024-10-30 | - | PMR completed and reedem training given to pump staff, leak checked and c side nozzle serviced.
CL5357 | 2024-10-30 | Neelambur | A | Outlet loyalty program training and PMR work. | Development | Gowtham | 2024-10-30 | - | Loyalty program training provided. PMR completed.
CL5358 | 2024-10-30 | T.V.Koil | A | Loyalty program redeem | Development | Sureshkumar | 2024-10-30 | - | Redeem Litre- 60.34 L Amount Rs- 3602.00 Total No's of Redeem vehicle - 11 Auto- 7 Car- 04 - Completed
CL5359 | 2024-10-30 | Avinashi | R | Outlet mother board IC replacement. | Breakdown | Gowtham | 2024-10-30 | - | Outlet mother board IC replacement completed.Working in good condition
CL5360 | 2024-10-30 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-10-30 | - | Redeem Litre- 169.80 L Amount Rs- 10134.25 No's of Redeem vehicle - 34 Auto- 28 Car- 06 - Completed
CL5361 | 2024-10-30 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-10-30 | - | Redeem Litre- 52.92 L Amount Rs- 3154.90 No's of Redeem vehicle - 9 Auto- 7 Car- 02 - Completed
CL5362 | 2024-10-31 | Neelambur | G | Outlet stabilizer working in EB and Genset power problem. | Breakdown | Gowtham | 2024-10-31 | - | Stabilizer working through EB and Genset power problem resolved by servicing and now working in good condition.
CL5363 | 2024-11-01 | Pudukkottai | A | Outlet Redeem point training programme. | Development | Nepolean | 2024-11-01 | - | Redeem point training given to pump staff.
CL5364 | 2024-11-01 | Madurai Ellis nagar | D | Outlet"C" side nozzle latch lock set and key pad problem. | Breakdown | Kathiresan | 2024-11-01 | - | The damaged "C" side nozzle latch lock set changed by new one and"C" side key pad to be Replaced.
CL5365 | 2024-11-01 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-01 | - | Redeem Litre- 13.66 L Amount Rs- 840.00 No's of Redeem vehicle - 4 Auto- 3 Car- 01 - Completed
CL5366 | 2024-11-01 | Devakottai | A | Loyalty program redeem | Development | Nepolean | 2024-11-01 | - | Redeem Litre- 65.92 L Amount Rs- 4059.00 No's of Redeem vehicle - 17 Auto- 17 Car- 0 - Completed
CL5367 | 2024-11-01 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-01 | - | Redeem Litre- 70.57 L Amount Rs- 4344.00 No's of Redeem vehicle - 14 Auto- 13 Car- 01 - Completed
CL5368 | 2024-11-02 | Perundurai | R | Outlet sales going in Offline. | Breakdown | Aninash | 2024-11-02 | - | Outlet sales back in online after changing of damaged RS 485 board.Working in good condition.
CL5369 | 2024-11-02 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-02 | - | Redeem Litre- 37.08 L Amount Rs- 2283.00 No's of Redeem vehicle - 9 Auto- 8 Car- 01 - Completed
CL5370 | 2024-11-04 | Musiri | C | Outlet Rule-18 work | Certification | Sureshkumar and Nivas | 2024-11-04 | - | Outlet Rule-18 work completed and both side DP diaphragm changed. Earth re-genreted.PMR also completed.Testing litre -10.63
CL5371 | 2024-11-04 | Trichengode | G | Outlet PMR work and checking of DP value. | Preventive | Avinash | 2024-11-04 | - | PMR completed,leak DP value checked , all camera checked working fine, Automation maintenance done.
CL5372 | 2024-11-04 | Pudukkottai | R | Outlet CPU problem. | Breakdown | Nepolean | 2024-11-04 | - | CPU problem rectified by replacing of new one and power cable one no changed. CPU working condition normal.
CL5373 | 2024-11-04 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-04 | - | Redeem Litre- 45.52 L Amount Rs- 2800.00 No's of Redeem vehicle -10 Auto- 8 Car- 02 - Completed
CL5374 | 2024-11-04 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-04 | - | Redeem Litre- 66.37 L Amount Rs- 4085.00 No's of Redeem vehicle -13 Auto- 12 Car- 01 - Completed
CL5375 | 2024-11-04 | Thuraiyur | C | Outlet Rule-18 work | Certification | Sureshkumar and Nivas | 2024-11-04 | - | Rule-18 work completed. Earth re-genreted .PMR also completed .
CL5376 | 2024-11-05 | Avinashi | A | Outlet redeem training program. | Development | Gowtham | 2024-11-05 | - | Redeem training given to pump staffs once again.
CL5377 | 2024-11-05 | Rasipuram | C | Outlet Rule-18 work | Certification | Sureshkumar and Nivas | 2024-11-05 | - | Rule-18 work completed. DP value diaphragm both side changed.Earth re-genreted
CL5378 | 2024-11-05 | Rasipuram | C | Outlet calibration and stamping work. | Certification | Nivas | 2024-11-05 | - | Calibration and stamping work completed. Calibration Report : "A" Side 10 ltrs = 10.07 "B" Side 10 ltrs = 9.97 "K" Factor Report : K factor no changes " A " Side K factor = 10150 " B " Side K factor = 10000 Testing Report : "A" Side = 143.35ltrs "B" Side = 132.50ltrs DP value testing ltrs.: 14.00 Total = 289.85ltrs
CL5379 | 2024-11-05 | Namakkal-1 | C | Outlet calibration and stamping work. | Certification | Nivas | 2024-11-05 | - | Calibration and stamping work completed. Calibration Report : "A" Side 10 ltrs = 10.03 "B" Side 10 ltrs = 10.02 "K" Factor Report : K factor no changes " A " Side K factor = 10150 " B " Side K factor = 10150
CL5380 | 2024-11-05 | Vadivelan nagar | G | Fire Extinguisher service work | Preventive | Suneel Sagar | 2024-11-05 | - | Fire Extinguisher service work completed and certificate received
CL5381 | 2024-11-05 | Karur | D | Outlet tank and dispensing area pneumatic hose damaged. | Breakdown | Thirumalaisamy | 2024-11-05 | - | The damaged tank and dispensing area pneumatic hose changed.
CL5382 | 2024-11-05 | Chengalpattu | G | Fire Extinguisher service work | Preventive | Suneel Sagar | 2024-11-05 | - | Fire Extinguisher service work completed and certificate received
CL5383 | 2024-11-05 | Cantonment | A | Loyalty program redeem | Development | Chandraselkar | 2024-11-05 | - | Redeem Litre- 91.02 L Amount Rs- 5603.79 No's of Redeem vehicle -21 Auto- 128 Car- 03 - Completed
CL5384 | 2024-11-05 | Namakkal-2 | C | Outlet Rule-18 work | Certification | Sureshkumar and Nivas | 2024-11-05 | - | Rule-18 work completed.both side DP diaphragm changed. Earth re-genreted. Testing lit -49.00 ltrs
CL5385 | 2024-11-05 | Namakkal-3 | C | Outlet Rule-18 work | Certification | Sureshkumar and Nivas | 2024-11-05 | - | Rule-18 work completed. Earth re-genreted . Testing lit:10.00 ltrs
CL5386 | 2024-11-06 | Attur | C | Outlet Rule-18 work | Certification | Sureshkumar,Nivas and Pandidurai | 2024-11-06 | - | Rule -18 work completed. Earth re-generate.Decanting and Dispensing liquid line ROV leakage arrested.Total all leakage checked.
CL5387 | 2024-11-06 | Ariyamangalam | D | Outlet B side nozzle LPG leakage problem. | Breakdown | Nepolean | 2024-11-06 | - | B side nozzle LPG leakage problem rectified by changing of 4 nos of new teeths and and nozzle o ring one number newly changed.Working in good condition.
CL5388 | 2024-11-06 | T.V.Koil | G | Outlet oil machine gun and tyre inflator machine clip connector problem. | Breakdown | Vigneshwaran | 2024-11-06 | - | Oil machine gun has been and the tyre inflator machine clip connector changed.
CL5389 | 2024-11-06 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-06 | - | Redeem Litre- 8.13 L Amount Rs- 500.00 No's of Redeem vehicle -2 Auto- 1 Car- 01 - Completed
CL5390 | 2024-11-06 | Devakottai | A | Loyalty program redeem | Development | Nepolean | 2024-11-06 | - | Redeem Litre- 69.71 L Amount Rs- 4294.00 No's of Redeem vehicle -22 Auto- 21 Car- 01 - Completed
CL5391 | 2024-11-06 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-06 | - | Redeem Litre- 73.16 L Amount Rs- 4503.00 No's of Redeem vehicle -17 Auto- 15 Car- 02 - Completed
CL5392 | 2024-11-07 | Ayothiyapattinam | D | Outlet unloading hose agmi adapter leakage and unloading liquid line ROV inside air leakage problem. | Breakdown | Prabu | 2024-11-07 | - | Unloading hose agmi adapter leakage problem rectified by reconnecting the hose and adapter. Unloading liquid line ROV inside air leakage problem and ball valve tightly working. Now manual working condition.
CL5393 | 2024-11-07 | Vadivelan nagar | R | Outlet online ups backup issue, | Breakdown | Suneel Sagar | 2024-11-07 | - | Online ups serviced as ups backup issue and now it is under observation.
CL5394 | 2024-11-07 | Velacherry | G | Outlet unloading spare motor service. | Preventive | Suneel Sagar | 2024-11-07 | - | Unloading spare motor serviced , tested and found satisfactory.
CL5395 | 2024-11-07 | Ariyamangalam | D | Outlet A side LPG hose leakage problem. | Breakdown | Nepolean | 2024-11-07 | - | A side LPG hose leakage problem rectified by changing of new 5 metre.Working in good condition. A side testing: 1.04 lit.
CL5396 | 2024-11-07 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-07 | - | Redeem Litre- 37.42 L Amount Rs- 2300.00 No's of Redeem vehicle -12 Auto- 10 Car- 02 - Completed
CL5397 | 2024-11-07 | Devakottai | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-07 | - | Redeem Litre- 62.43 L Amount Rs- 3845.00 No's of Redeem vehicle -18 Auto- 16 Car- 02 - Completed
CL5398 | 2024-11-07 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-07 | - | Redeem Litre- 76.49 L Amount Rs- 4708.00 No's of Redeem vehicle -18 Auto- 16 Car- 02 - Completed
CL5399 | 2024-11-08 | Devakottai | A | Loyalty program redeem | Development | Nepolean | 2024-11-08 | - | Redeem Litre- 56.37 L Amount Rs- 3470.00 No's of Redeem vehicle -14 Auto- 13 Car- 01 - Completed
CL5400 | 2024-11-08 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-08 | - | Redeem Litre- 43.90 L Amount Rs- 2700.00 No's of Redeem vehicle -08 Auto- 05 Car- 03 - Completed
CL5401 | 2024-11-08 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-08 | - | Redeem Litre- 74.49 L Amount Rs- 4584.28 No's of Redeem vehicle -15 Auto- 14 Car- 01 - Completed
CL5402 | 2024-11-09 | Kinathukadavu | R | Outlet EB low power fluctuation problem | Breakdown | Gowtham | 2024-11-09 | - | EB low power fluctuation problem controlled by stabilizer input and output parameter change. Genset frequency to be change. Now over load found while dispensing motor starting time, but stabilizer under cut off problem during output power supply. Working normal and outlet in under observation. Outlet low voltage found - 200, 205, 203 High voltage - 270, 256,249 Stabilizer high voltage cut off set to - 285 V.
CL5403 | 2024-11-09 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-09 | - | Redeem Litre- 26.57 L Amount Rs- 1636.00 No's of Redeem vehicle -5 Auto- 03 Car- 02 - Completed
CL5404 | 2024-11-10 | Tharamangalam | D | Outlet Dispenser A side nozzle leakage problem. | Breakdown | Prabu | 2024-11-10 | - | Dispenser A side nozzle leakage problem rectified by changing of 4 teeths and unloading liquid hose venting pipe line checked.
CL5405 | 2024-11-11 | Pudukkottai | C | Outlet Rule-18 work | Certification | Sureshkumar and Nepolean | 2024-11-11 | - | Ruel-18 work completed
CL5406 | 2024-11-11 | Pudukkottai | C | Outlet Stamping and Calibration work | Certification | Sureshkumar and Nepolean | 2024-11-11 | - | Stamping work completed Calibration report: A side testing lit.- 169.08 B side testing lit : 141.02 K factory no changes Both side : 10190 A side 10lit : 10.04 B side 10 lit : 10.03 Total testing: 310.10 lit
CL5407 | 2024-11-11 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-11 | - | Redeem Litre- 67.77 L Amount Rs- 4173.00 No's of Redeem vehicle -18 Auto- 16 Car- 02 - Completed
CL5408 | 2024-11-12 | Namakkal-1 | G | Outlet unloading training program. | Preventive | Nivas | 2024-11-12 | - | Unloading training completed.
CL5409 | 2024-11-12 | Madurai Villapuram | D | Outlet dispenser motor spider problem. | Breakdown | Kathiresan | 2024-11-12 | - | Dispensing motor spider problem rectified by changing of new one and compressor NRV serviced. Working good in good condition
CL5410 | 2024-11-12 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-12 | - | Redeem Litre- 30.94 L Amount Rs- 1906.00 No's of Redeem vehicle -10 Auto- 09 Car- 01 - Completed
CL5411 | 2024-11-12 | Kodumudi | C | Outlet Calibration work | Certification | Sureshkumar,Avinash and Thirumalaisamy | 2024-11-12 | - | Calibration completed. K- Factor Testing. A. 10300 152.62 B. 10300 153.42
CL5412 | 2024-11-12 | Perundurai | C | Outlet Calibration work | Certification | Sureshkumar,Avinash and Thirumalaisamy | 2024-11-12 | - | Calibration completed. K- Factor. Testing. 10L= A. 10200 151.50 10.00 B. 10200 144.55 09.96
CL5413 | 2024-11-12 | Nasiyanur | C | Outlet Calibration work | Certification | Sureshkumar,Avinash and Thirumalaisamy | 2024-11-12 | - | Calibration completed. K- Factor Testing. 10L= A. 10000 153.29 09.95 B. 10000 152.48 09.98
CL5414 | 2024-11-12 | Bhavani | C | Outlet Calibration work | Certification | Sureshkumar,Avinash and Thirumalaisamy | 2024-11-12 | - | Calibration completed. K- Factor Testing. 10L= A. 10050 152.52 09.97 B. 10050 152.75 10.00 C. 10000 151.17 10.01 D. 10000 151.49 10.00
CL5415 | 2024-11-12 | Ammapettai | C | Outlet Calibration work | Certification | Sureshkumar,Avinash and Thirumalaisamy | 2024-11-12 | - | Calibration completed. K- Factor Testing. 10L= A. 10000 151.87 10.00 B. 10000 101.95 09.99
CL5416 | 2024-11-12 | Erode | C | Outlet Calibration work | Certification | Sureshkumar,Avinash and Thirumalaisamy | 2024-11-12 | - | Calibration completed. K- Factor Testing. 10L= A. 10100 111.10 09.97 B. 10100 151.56 10.04
CL5417 | 2024-11-13 | Vedasandur | D | Outlet dispenser B-side display hanging problem. | Breakdown | Kamaraj | 2024-11-13 | - | Outlet dispenser B-side display hanging problem rectified by re inserting of display cable and keypad cable.Working in good condition.
CL5418 | 2024-11-13 | Perundurai | C | Outlet Stamping work | Certification | Avinash and Sureshkumar | 2024-11-13 | - | Stamping has been completed and certificates will be issued by once the portal is opened.
CL5419 | 2024-11-13 | Nasiyanur | C | Outlet Stamping work | Certification | Avinash and Sureshkumar | 2024-11-13 | - | Stamping has been completed and certificates will be issued by once the portal is opened.
CL5420 | 2024-11-13 | Bhavani | C | Outlet Stamping work | Certification | Avinash and Sureshkumar | 2024-11-13 | - | Stamping has been completed and certificates will be issued by once the portal is opened.
CL5421 | 2024-11-13 | Ammapettai | C | Outlet Stamping work | Certification | Avinash and Sureshkumar | 2024-11-13 | - | Stamping has been completed and certificates will be issued by once the portal is opened.
CL5422 | 2024-11-13 | Erode | C | Outlet Stamping work | Certification | Avinash and Sureshkumar | 2024-11-13 | - | Stamping has been completed and certificates will be issued by once the portal is opened.
CL5423 | 2024-11-13 | Cantonment | D | Outlet C side nozzle leakage problem. | Breakdown | Chandrasekar | 2024-11-13 | - | C side nozzle leakage problem resolved by changing of 4 nos of new hammer set. Closing.reading.5224652.78
CL5424 | 2024-11-13 | Ariyalur | G | Outlet fire extinguisher service and renewal work. | Preventive | Pandi durai | 2024-11-13 | - | Fire extinguisher service and renewal work completed.Training given to pump staffs.
CL5425 | 2024-11-13 | Perambalur | G | Outlet fire extinguisher service and renewal work. | Preventive | Pandi durai | 2024-11-13 | - | Fire extinguisher service and renewal work completed.Training given to pump staffs.
CL5426 | 2024-11-13 | Viruthachalam | G | Outlet fire extinguisher service and renewal work. | Preventive | Pandi durai | 2024-11-13 | - | Fire extinguisher service and renewal work completed.Training given to pump staffs.
CL5427 | 2024-11-13 | Perambalur | G | Outlet operator switch problem. | Breakdown | Pandi durai | 2024-11-13 | - | Operator switch 1 no changed.
CL5428 | 2024-11-13 | Viruthachalam | G | Outlet CO2 75 kg hose and new unloading solenoid coil problem. | Breakdown | Pandi durai | 2024-11-13 | - | The damaged CO2 75 kg hose newly replaced and unloading solenoid coil changed.
CL5429 | 2024-11-13 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-13 | - | Redeem Litre- 36.28 L Amount Rs- 2233.00 No's of Redeem vehicle -9 Auto- 8 Car- 01 - Completed
CL5430 | 2024-11-13 | Vadivelan nagar | A | Outlet Redeem program training. | Development | Suneel Sagar | 2024-11-13 | - | Redeem program training completed.
CL5431 | 2024-11-13 | Velacherry | A | Outlet Redeem program training. | Development | Suneel Sagar | 2024-11-13 | - | Redeem program training completed.
CL5432 | 2024-11-14 | Kattupakkam | A | Outlet Redeem program training. | Development | Suneel Sagar | 2024-11-14 | - | Redeem program training completed.
CL5433 | 2024-11-14 | Avadi | A | Outlet Redeem program training. | Development | Suneel Sagar | 2024-11-14 | - | Redeem program training completed.
CL5434 | 2024-11-14 | Ariyamangalam | A | Loyalty program redeem | Development | Pandi durai | 2024-11-14 | - | Redeem Litre- 32.52 L Amount Rs- 2000.00 No's of Redeem vehicle - 7 Auto- 4 Car- 03 - Completed
CL5435 | 2024-11-14 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-14 | - | Redeem Litre- 48.94 L Amount Rs- 3014.00 No's of Redeem vehicle -13 Auto- 12 Car- 01 - Completed
CL5436 | 2024-11-15 | Chinnasalem | R | Outlet Online ups problem. | Breakdown | Pandidurai | 2024-11-15 | - | Online ups problem rectified by changing of UPS 1 KVA, 12V 42AH external battery and changing of one "R" phase surge 1. Total all leakage checked and PMR also completed.
CL5437 | 2024-11-15 | Mettupalayam | R | Outlet Offline ups battery backup and unloading liquid ROV problem. | Breakdown | Gowtham | 2024-11-15 | - | Offline ups battery backup and unloading liquid ROV (2") problem resolved. ATG configured with new memory card and reprogramming, but ATG show current inventory only. cut off function not working due to tank threshold input access issue.
CL5438 | 2024-11-15 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-15 | - | Redeem Litre- 27.58 L Amount Rs- 1698.00 No's of Redeem vehicle -8 Auto- 7 Car- 01 - Completed
CL5439 | 2024-11-15 | Ariyamangalam | D | Outlet B side on/off switch problem. | Breakdown | Nepolean | 2024-11-15 | - | B side on/off switch problem rectified by changing of new one and working in good condition.
CL5440 | 2024-11-15 | T.V.Koil | T | Outlet unloading side D.O.L stater MNX contractor problem, | Breakdown | Nepolean | 2024-11-15 | - | Unloading side D.O.L stater MNX contractor problem resolved by changing with new contractor and unloading condition normal.
CL5441 | 2024-11-15 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-15 | - | Redeem Litre- 38.71 L Amount Rs- 2380.00 No's of Redeem vehicle -8 Auto- 3 Car- 05 - Completed
CL5442 | 2024-11-16 | Velacherry,Vadivelan nagar,Avadi,Kattupakkam and Chengalpattu | G | Outlets Redeem program training and Safety Audit | Preventive | Navaneetha krishnan | 2024-11-16 | - | Outlets Redeem program training and Safety Audit completed
CL5443 | 2024-11-16 | Bhavani | R | Outlet control panel tripping problem. | Breakdown | Avinash | 2024-11-16 | - | Control panel tripping problem rectified by changing of new solenoid coil and B side the damaged keypad replaced by new one.Working in good condition.
CL5444 | 2024-11-16 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-16 | - | Redeem Litre- 19.88 L Amount Rs- 1224.00 No's of Redeem vehicle -5 Auto- 4 Car- 01 - Completed
CL5445 | 2024-11-16 | Madurai-3(Pandikoil) | A | Loyalty program redeem | Development | Kathiresan | 2024-11-16 | - | Redeem Litre- 5.39 L Amount Rs- 332.00 No's of Redeem vehicle -1 Auto- 1 Car- 0 - Completed
CL5446 | 2024-11-16 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-16 | - | Redeem Litre- 1.63 L Amount Rs- 100.00 No's of Redeem vehicle -1 Auto- 1 Car- 0 - Completed
CL5447 | 2024-11-16 | Pudukkottai | A | Loyalty program redeem | Development | Nepolean | 2024-11-16 | - | Redeem Litre- 18.35 L Amount Rs- 1130.00 No's of Redeem vehicle -6 Auto- 6 Car- 0 - Completed
CL5448 | 2024-11-16 | Ariyamangalam | D | Outlet LPG hose problem. | Breakdown | Nepolean | 2024-11-16 | - | A side LPG 5m hose new one changed .A side testing: 1.10 lit
CL5449 | 2024-11-18 | Madurai Ellis nagar | D | Outlet "D" side nozzle and oil dispenser leakage problem . | Breakdown | Kathiresan | 2024-11-18 | - | "D" side nozzle problem resolved by replacing of front O ring and oil dispenser oil leakage arrested by changing of new nozzle.Working in good condition. Oil dispenser testing =0.50 ltrs
CL5450 | 2024-11-18 | Ramanathapuram | R | Outlet Automation working problem. | Breakdown | Kathiresan | 2024-11-18 | - | Automation now working without mobile due to mobile display problem and another mobile touch damaged . Problem solved in evening 5 clock
CL5451 | 2024-11-18 | Kodumudi | R | Outlet control pannel booting issue. | Breakdown | Thirumalaisamy | 2024-11-18 | 45 Minutes | Control panel booting issue solved by changing of damaged 24 volt outlet transformer.SaleS stopped 45min(5.15 to 6.00PM).
CL5452 | 2024-11-18 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-18 | - | Redeem Litre- 5.37 L Amount Rs- 330.00 No's of Redeem vehicle -2 Auto- 2 Car- 0 - Completed
CL5453 | 2024-11-18 | Madurai-3(Pandikoil) | A | Loyalty program redeem | Development | Kathiresan | 2024-11-18 | - | Redeem Litre- 5.66 L Amount Rs- 349.00 No's of Redeem vehicle -2 Auto- 1 Car- 1 - Completed
CL5454 | 2024-11-18 | Cantonment | A | Loyalty program redeem | Development | Chandrasekar | 2024-11-18 | - | Redeem Litre- 21.29 L Amount Rs- 1311.00 No's of Redeem vehicle -5 Auto- 5 Car- 0 - Completed
CL5455 | 2024-11-19 | Rasipuram | D | Outlet surge arrester failure. | Breakdown | Nivas | 2024-11-19 | - | Surge arrester failure resolved by replacing of 2 new surge.
CL5456 | 2024-11-19 | Uthamapalayam | R | Outlet automation network problem. | Breakdown | Kamaraj | 2024-11-19 | - | Automation network problem rectified by changing of damaged network cable.Working in good condition.
CL5457 | 2024-11-19 | Ariyamangalam | D | Outlet A side LPG 5m hose (criming) testing work. | Breakdown | Nepolean | 2024-11-19 | - | A side LPG 5m hose one no (criming) one side testing work completed.. A side testing: 2.22 lit.
CL5458 | 2024-11-19 | Ayothiyapattinam | D | Outlet spare nozzle and office room side camera cable problem. | Breakdown | Prabu | 2024-11-19 | - | Spare nozzle 1 no's serviced and office room side camera cable and camera 1 no's changed.Working in good condition.
CL5459 | 2024-11-20 | Madurai Villapuram | R | Outlet Automation firewall power adaptor failure | Breakdown | Kathiresan | 2024-11-20 | - | Automation firewall power adaptor problem rectified by changing of new one.
CL5460 | 2024-11-20 | Madurai Ellis nagar | D | Outlet "A" side nozzle latch lock set damaged | Breakdown | Kathiresan | 2024-11-20 | - | The damaged "A" side nozzle latch lock set changed by new one.
CL5461 | 2024-11-20 | Dindugal | C | Outlet Rule-18 work | Certification | Kamaraj and Chandrasekar | 2024-11-20 | - | Rule-18 work completed.Earth Re-generate.DP valve diaphragm checked and all leakage tested.
CL5462 | 2024-11-20 | Batlagundu | C | Outlet Rule-18 work | Certification | Kamaraj and Chandrasekar | 2024-11-20 | - | Rule-18 work completed.Earth Re-generate.DP valve diaphragm checked and all leakage tested.
CL5463 | 2024-11-20 | Mulanur | D | Outlet dispensing motor spider problem and unloading training. | Breakdown | Thirumalaisamy | 2024-11-20 | - | The damaged dispensing motor spider newly changed and unloading training given to pump person
CL5464 | 2024-11-20 | Saravanampatty | G | Outlet STP motor MOL problem in genset power. | Breakdown | Gowtham | 2024-11-20 | 2 Hrs | Outlet STP motor MOL problem in genset power problem automatically solved and till not receive MOL in both power supply. Now pump working normal and kept under in observation.
CL5465 | 2024-11-20 | Ariyamangalam | A | Loyalty program redeem | Development | Nepolean | 2024-11-20 | - | Redeem Litre- 4.55 L Amount Rs- 280.00 No's of Redeem vehicle -2 Auto- 1 Car- 1- Completed
CL5466 | 2024-11-20 | Ariyamangalam | G | Outlet N2 air M/c mouth problem. | Breakdown | Nepolean | 2024-11-20 | - | Outlet N2 air M/c mouth problem resolved by changing of new one.working in good condition.
CL5467 | 2024-11-21 | Theni | C | Outlet Rule-18 work | Certification | Chandrasekar and Kamaraj | 2024-11-21 | - | Rule-18 work completed.Earth Re-generate.DP valve diaphragm checked and all leakage tested.
CL5468 | 2024-11-21 | Bodi | C | Outlet Rule-18 work | Certification | Chandrasekar and Kamaraj | 2024-11-21 | - | Rule-18 work completed.Earth Re-generate.DP valve diaphragm checked and all leakage tested.
CL5469 | 2024-11-21 | Uthamapalayam | C | Outlet Rule-18 work | Certification | Chandrasekar and Kamaraj | 2024-11-21 | - | Rule-18 work completed.Earth Re-generate.DP valve diaphragm checked and all leakage tested.
CL5470 | 2024-11-22 | Tharamangalam | R | Outlet stabilizer not working. | Breakdown | Prabu | 2024-11-26 | - | Stabilizer new contactor and voltage display board 1 no's changed.Working condition.
CL5471 | 2024-11-22 | Madurai-Villapuram | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-22 | - | Rule - 18 work Completed and Earth regenerated, all equipment are working in good condition. PMR also done. DP valve diaphragm checked Working fine. CP value = 0.885 . Earth value = 3.6 (v)
CL5472 | 2024-11-22 | Madurai Ellis nagar | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-22 | - | Rule - 18 Work Completed and Earth Regenerated, all equipment are working in good condition. PMR also done. DP valve diaphragm checked Working in good condition. CP value ; Tank 1 = - 1.100 Tank 2 = - 1.114 Earth value = 1.8 (v)
CL5473 | 2024-11-22 | Salem-2 | C | Outlet DG 1 service and Dispenser DP valve checking work. | Certification | Prabu | 2024-11-22 | - | DG 1 service work and Dispenser DP valve checking completed. Total testing: 0.99lit
CL5474 | 2024-11-23 | Virudhunagar | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-23 | - | Rule - 18 Work Completed and Earth regenerated and all equipments worrking in good condition.Automation power "R" phase to "Y" phase changed. PMR also done. DP valve diaphragm Checked. Working in good condition. CP value = 0.853 Earth value = 2.1 (v)
CL5475 | 2024-11-23 | Tenkasi | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-23 | - | Rule - 18 work wompleted and Earth regenerated all equipment working in good condition. PMR also done. DP valve diaphragm checked. Working in good condition. 9 kg fire extinguisher one number failure to be replaced. CP value = 0.885 Earth value = 1.8 (v)
CL5476 | 2024-11-23 | Tirunelveli | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-23 | - | Rule - 18 work completed and Earth regenerated, all equipments working in good condition.. PMR also done. DP valve diaphragm checked Working in good condition."9 kg fire extinguisher 3 nos failure to be replaced. CP value ; Tank 1 = - 1.110 Tank 2 = - 1.109 Earth value = 1.8 (v)
CL5477 | 2024-11-24 | Kodumudi | C | Outlet stamping work. | Certification | Avinash | 2024-11-24 | - | Stamping work completed.
CL5478 | 2024-11-24 | Namakkal-3 | D | Outlet dispenser A side nozzle leakage problem. | Breakdown | Nivas | 2024-11-24 | - | Dispenser A side nozzle leakage problem rectified by servicing the nozzle.Working in good condition. Testing -0.86 lit.
CL5479 | 2024-11-24 | Madurai-3(Pandikoil) | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-24 | - | Rule - 18 work completed . PMR also done. DP valve diaphragm checked. Working in good condition. CP value = - 1.114 Earth value = 1.2 (v)
CL5480 | 2024-11-24 | Melur | C | Outlet Rule-18 work | Certification | Kathiresan and Chandrasekar | 2024-11-24 | - | Rule - 18 work completed and Earth regenerated. All equipment working in good condition.. PMR also done. DP valve diaphragm checked. Working fine. Control panel LED indicators to be replaced. CP value = - 1.040 Earth value = 1(v)
CL5481 | 2024-11-24 | T.V.Koil | D | Outlet batchen dispenser "A"&"B" side nozzle leakage problem. | Breakdown | Pandidurai | 2024-11-24 | - | Dispenser "A"&"B" side nozzle leakage problem resolved by changing of 8 nos of new hammer teeths.Working in good condition.
CL5482 | 2024-11-24 | Dharmapurai | G | Fire Extinguisher service and renewal work | Preventive | Prabu | 2024-11-24 | - | Fire Extinguisher service and renewal work completed and 75 kg 2 nos DCP Powder to be Changed
CL5483 | 2024-11-24 | Tharamangalam | G | Fire Extinguisher service and renewal work | Preventive | Prabu | 2024-11-24 | - | Fire Extinguisher service and renewal work completed and training given to pump staffs.
CL5484 | 2024-11-24 | Uthamacholapuram | G | Fire Extinguisher service and renewal work | Preventive | Prabu | 2024-11-24 | - | Fire Extinguisher service and renewal work completed and training given to pump staffs.
CL5485 | 2024-11-26 | Bhavani | C | Outlet stamping work | Certification | Avinash | 2024-11-26 | - | Outlet stamping certificate received
CL5486 | 2024-11-26 | Erode | C | Outlet stamping work | Certification | Avinash | 2024-11-26 | - | Outlet stamping certificate received
CL5487 | 2024-11-26 | Kodumudi | C | Outlet stamping work | Certification | Avinash | 2024-11-26 | - | Outlet stamping certificate received
CL5488 | 2024-11-26 | Perundurai | C | Outlet stamping work | Certification | Avinash | 2024-11-26 | - | Outlet stamping certificate received
CL5489 | 2024-11-26 | Nasiyanur | C | Outlet stamping work | Certification | Avinash | 2024-11-26 | - | Outlet stamping certificate received
CL5490 | 2024-11-26 | Ammapettai | C | Outlet stamping work | Certification | Avinash | 2024-11-26 | - | Outlet stamping certificate received
CL5491 | 2024-11-26 | Madurai Ellis nagar | D | Outlet dispenser "Off line UPS battery backup timing problem. | Breakdown | Kathiresan | 2024-12-17 | - | Outlet Off line UPS battery changed battery including warranty period. backup timing 8 min more.
CL5492 | 2024-11-28 | Bhavani | C | Outlet stamping work | Certification | Avinash | 2024-11-28 | - | Rule 18 work completed and DP value Earth regenerated.All leak has been checked.
CL5493 | 2024-11-28 | Nasiyanur | C | Outlet stamping work | Certification | Avinash | 2024-11-28 | - | Rule 18 work completed and DP value Earth regenerated.All leak has been checked.
CL5494 | 2024-11-28 | Ammapettai | C | Outlet stamping work | Certification | Avinash | 2024-11-28 | - | Rule 18 work completed and DP value Earth regenerated.All leak has been checked.
CL5495 | 2024-11-28 | Madurai-Villapuram | D | Outlet"D" side nozzle hammer teeth problem. | Breakdown | Kathiresan | 2024-11-28 | - | "D" side nozzle problem rectified by changing of 4 nos of hammer teeths due to the reading crossed by more than one lac. Testing = 0.64 ltrs
CL5496 | 2024-11-28 | Ariyamangalam | D | Outlet B side nozzle lock problem. | Breakdown | Nepolean | 2024-11-28 | - | B side nozzle lock problem resoved by changing of new one.Working in good condition.
CL5497 | 2024-11-29 | Thiruvaiyaru | G | Outlet canopy light problem. | Breakdown | Nivas | 2024-11-29 | - | Canopy light problem resolved by replacing by 2 nos of new lights,
CL5498 | 2024-11-29 | Virudhunagar | R | Outlet dispenser Automation communication "485 Board" problem. | Breakdown | Kathiresan | 2024-11-29 | - | Dispenser Automation communication "485 Board" problem rectified by changing of new one.Working in good condition and kept under observation foe one week.
CL5499 | 2024-11-29 | Omalur | C | Outlet Stamping and Calibration work | Certification | Sureshkumar and Prabu | 2024-11-29 | - | Dispenser stamping and calibration completed. Testing litre A side-122.53 B side-163.20 Total -285.73 K-factor A side 10000 B side 10000 A side- 10=10.01 B side- 10=10.02
CL5500 | 2024-11-29 | Omalur | C | Outlet Rule-18 work | Certification | Sureshkumar and Prabu | 2024-11-29 | - | Rule 18 work completed and DP valve, Earth regenerated and all leak tested.Working in good condition.
CL5501 | 2024-11-29 | Tharamangalam | C | Outlet Rule-18 work | Certification | Sureshkumar and Prabu | 2024-11-29 | - | Rule 18 work completed and DP valve, Earth regenerated and all leak tested.Working in good condition.
CL5502 | 2024-11-30 | Kinathukadavu | R | Outlet panel shutoff problem while fueling. | Breakdown | Gowtham | 2024-11-30 | - | Panel shutoff problem while fueling is due to low voltage(206,207,189). Now stabilizer CT function disabled. Progress in observation and stabilizer wheel 2 nos replaced by new one.
CL5503 | 2024-11-30 | Ayothiyapattinam | C | Outlet Rule-18 work | Certification | Sureshkumar and Prabu | 2024-11-30 | - | Rule 18 work completed and DP valve, Earth regenerated and all leak tested.Working in good condition.
CL5504 | 2024-11-30 | Uthamacholapuram | C | Outlet Rule-18 work | Certification | Sureshkumar and Prabu | 2024-11-30 | - | Rule 18 work completed and DP valve, Earth regenerated and all leak tested.Working in good condition.
CL5505 | 2024-12-01 | Avadi | R | Outlet is offline due to CPU issue. | Breakdown | Suneel Sagar | In process | - | Due to CPU issue the rate changed manually.Now avadi is online and D side keypad is not working, will be resolved till the spares received from H.O.Trichy.
CL5506 | 2024-12-01 | Salem-2 | C | Outlet Rule-18 work | Certification | Sureshkumar and Prabu | 2024-12-01 | - | Rule 18 work completed and DP valve, Earth regenerated and all leak tested.Working in good condition.
CL5507 | 2024-12-01 | Ayothiyapattinam | T | Outlet unloading liquid line ROV service work. | Breakdown | Prabu | 2024-12-01 | - | Unloading liquid line ROV serviced and working in good condition.
CL5508 | 2024-12-02 | Namakkal-2 | G | PMR Work | Preventive | Nivas | 2024-12-02 | - | PMR completed
CL5509 | 2024-12-04 | Tirunelveli | C | Outlet Stamping and Calibration work | Certification | Chandrasekar and Kathiresan | 2024-12-04 | - | Calibration and stamping Completed. The unloading Tank 1 and Tank 2 select switch changed. "A" Side key pad changed and "C" side nozzle front O ring Replaced.Working in good condition. Calibration report's ; "A" Side - 10 = 10.02 "B" Side - 10 = 10.01 "C" Side - 10 = 9.97 "D" Side - 10 = 9.96 "K" Factor Report ; "A" Side = 10000 "B" Side = 10000 "C" Side = 10341 "D" Side = 10330
CL5510 | 2024-12-04 | Avadi | G | Outlet compressor problem | Breakdown | Suneel Sagar | 2024-12-04 | - | Outlet compressor problem resolved and PMR completed
CL5511 | 2024-12-05 | Namakkal-1 | G | Outlet PMR work. | Preventive | Nivas | 2024-12-05 | - | PMR work completed.
CL5512 | 2024-12-05 | Dharmapuri | T | Outlet leakage problem. | Breakdown | Prabu | 2024-12-05 | - | Outlet leakage problem resolved and.unloading completed.
CL5513 | 2024-12-05 | Karur | A | Outlet Automation work. | Development | Madhavan,Vigneshwaran and Thirumalaisamy | 2024-12-05 | - | Automation work completed and both dispenser are online.
CL5514 | 2024-12-05 | Theni | C | Outlet Stamping and Calibration work | Certification | Kamaraj and Chandrasekar | 2024-12-05 | - | Outlet calibration and atamping completed. Calibration details. Testing litres A side- 155.95 B side- 157.23 Total - 313.17 litres. K-factor A side- 103250 B side- 104990 A side -10=9.96 B side - 10=9.94
CL5515 | 2024-12-05 | Bodi | C | Outlet Stamping and Calibration work | Certification | Kamaraj and Chandrasekar | 2024-12-05 | - | Outlet calibration and atamping completed. Calibration details. Testing litres A side- 155.41 B side- 152.32 Total - 307.73 litres K-factor A side- 10000 B side- 10000 A side -10=10.01 B side - 10=10.01
CL5516 | 2024-12-05 | Uthamapalayam | C | Outlet Stamping and Calibration work | Certification | Kamaraj and Chandrasekar | 2024-12-05 | - | Outlet calibration and atamping completed. Calibration details. Testing litres A side- 155.62 B side- 152.29 Total - 307.91 litres K-factor A side- 10000 B side- 10100 A side -10=10.02 B side - 10= 9.94
CL5517 | 2024-12-06 | Ayothiyapattinam | G | Outlet compressor continuously running and dispenser bottom liquid line ROV leakage problem | Breakdown | Prabu | 2024-12-06 | - | Compressor continuously running problem rectified by adjusting the compressor pressure switch.Dispenser bottom liquid line ROV leakage problem rectified by interchanging of unloading ROV one number interchanged.Working in good condition.
CL5518 | 2024-12-07 | Madurai Villapuram | D | Outlet dispenser "1/4 FRL" unit set leakage problem. | Breakdown | Kathiresan | 2024-12-07 | - | Dispenser "1/4 FRL" unit set leakage problem arrested by replacing by new unit and air hose also changed.Working in good condition.
CL5519 | 2024-12-07 | Perundurai | C | Outlet Rule 19 material requirement data collection work. | Certification | Avinash | 2024-12-07 | - | Outlet Rule 19 work material requirement data collected.
CL5520 | 2024-12-07 | Ammapettai | T | Outlet ATG not functioning. | Breakdown | Avinash | 2024-12-07 | - | The Ammapettai ATG removed and taken to Erode station for checking purpose .
CL5521 | 2024-12-09 | Perundurai | C | Outlet Rule-19 work | Certification | Avinash,Thirumalaisamy and Chandrasekar | 2024-12-11 | 40 Hrs and 30 Minutes | Rule-19 work started and sales have been stopped by 4.30 PM(09-12-2024).Sales started by 9.00 AM(11-12-2024)
CL5522 | 2024-12-09 | Cantonment | D | Outlet "A" side nozzle leakage problem. | Breakdown | Sureshkumar | 2024-12-09 | - | "A" side nozzle leakage problem arrested by replacing of NRV O ring and pump working in good condition. Testing litters: 1.18 lits
CL5523 | 2024-12-10 | Vadivelan nagar | D | Outlet dispenser c side dispensing hose problem. | Breakdown | Suneel Sagar | 2024-12-10 | - | Dispenser c side dispensing hose problem rectified by replaced by new one and old one sent for recrimpling.
CL5524 | 2024-12-10 | Uthamasolapuram | A | Outlet dispenser online problem. | Development | Prabu | 2024-12-10 | - | Dispenser back to on-line and system CPU connected.
CL5525 | 2024-12-10 | Perambalur | C | Stamping and Calibration work | Certification | Pandidurai and Sureshkumar | 2024-12-10 | - | Stamping & calibration work completed. Calibration Report : "A" Side 10 ltrs = 10.03 "B" Side 10 ltrs = 10.02 "K" Factor Report : K factor no changes " A " Side K factor = 09900 " B " Side K factor = 09900 Testing Report : "A" Side = 156.22 ltrs "B" Side = 153.25 ltrs Total = 309.47ltrs
CL5526 | 2024-12-10 | Perambalur | C | Rule-18 work | Certification | Pandidurai and Sureshkumar | 2024-12-10 | - | Rule 18 work completed and DP valve checked. Earth regenerated work done.Total all leakage checked.PMR also completed.
CL5527 | 2024-12-10 | Ariyalur | C | Stamping and Calibration work | Certification | Pandidurai and Sureshkumar | 2024-12-10 | - | Stamping & calibration work completed. Calibration Report : "A" Side 10 ltrs = 9.97 "B" Side 10 ltrs = 9.97 "K" Factor Report : K factor no changes " A " Side K factor = 10000 " B " Side K factor = 10000 Testing Report : "A" Side = 157.99 ltrs "B" Side = 163.05 ltrs Total = 321.04 ltrs
CL5528 | 2024-12-10 | Ariyalur | C | Outlet Rule-18 work | Certification | Pandidurai and Sureshkumar | 2024-12-10 | - | Rule 18 work completed and DP valve checked. Earth regenerated work done.Total all leakage checked.PMR also completed.
CL5529 | 2024-12-10 | Madurai-3(Pandikoil) | G | Outlet Fire Extinguisher service and renewal work | Preventive | Kathiresan | 2024-12-10 | - | Fire extinguisher service and renewal work completed.and training given to pump staff
CL5530 | 2024-12-10 | Eral | G | Outlet Fire Extinguisher service and renewal work | Preventive | Kathiresan | 2024-12-10 | - | Fire extinguisher service and renewal completed and the damaged "75 kg" fire extinguisher hose 2 nos newly changed. and training given to pump staff
CL5531 | 2024-12-10 | Thirunelveli | G | Outlet Fire Extinguisher service and renewal work | Preventive | Kathiresan | 2024-12-10 | - | Fire extinguisher service and renewal work completed "9 kg Fire extinguisher 3 nos replaced due to pressure drop and "Fire Ball 1 no" changed.and training given to pump staff
CL5532 | 2024-12-11 | Perundurai | C | Rule-18 work | Certification | Avinash,Thirumalaisamy and Chandrasekar | 2024-12-11 | - | Rule 18 work completed all equipments leak checked. Dispenser both side diaphragm changed.Working in good condition.Testing: 32.51 Lts
CL5533 | 2024-12-11 | Virudhachalam | C | Stamping and Calibration work | Certification | Pandidurai and Sureshkumar | 2024-12-11 | - | Station stamping & calibration work completed.Calibration Report : "A" Side 10 ltrs = 9.96 "B" Side 10 ltrs = 9.96 "K" Factor Report : K factor Changed to "B" Side " A " Side K factor = 10100 " B " Side Old K factor = 10200 "B" Side New K factor = 10100 Testing Report : "A" Side = 151.95 ltrs "B" Side = 242.50 ltrs Total = 394.45 ltrs
CL5534 | 2024-12-11 | Virudhachalam | C | Outlet Rule-18 work | Certification | Pandidurai and Sureshkumar | 2024-12-11 | - | Rule 18 work completed and DP valve checked. Earth regenerated work done.Unloading vent line problem rectified and Dispensing vapour line ROV leakage arrested. Total all leakage checked.PMR also completed.
CL5535 | 2024-12-11 | Chinnasalem | C | Outlet Rule-18 work | Certification | Pandidurai and Sureshkumar | 2024-12-11 | - | Rule 18 work completed and DP valve checked. Earth regenerated work done.Total all leakage checked.
CL5536 | 2024-12-12 | Tenkasi | T | Outlet "OPW ATG 3v battery problem. | Breakdown | Kathiresan | 2024-12-12 | - | "OPW ATG 3v battery replaced and working in good condition.
CL5537 | 2024-12-12 | Tenkasi | G | Outlet Fire Extinguisher service and renewal work | Preventive | Kathiresan | 2024-12-12 | - | Fire Extinguisher service and renewal work completed."9 kgFire extinguisher 1 no replaced due to pressure drop and Fire extinguisher Working and training given to pump staff .
CL5538 | 2024-12-12 | Virudhunagar | G | Outlet Fire Extinguisher service and renewal work | Preventive | Kathiresan | 2024-12-12 | - | Fire extinguisher service and renewal work completed.The expired "Fire Ball 1 no" changed Fire extinguisher working in good condition and training given to pump staff
CL5539 | 2024-12-12 | Perundurai | G | General inspection | Preventive | Avinash | 2024-12-12 | - | Outlet all equipments leak checked, all equipment working in good condition.
CL5540 | 2024-12-12 | Dindugal | C | Stamping and Calibration work | Certification | Kamaraj | 2024-12-12 | - | Outlet calibration and stamping work completed. Testing litres A side- 149.85 B side- 113.04 Total - 262.89 litres. K-factor A side- 09600 B side- 09600 A side -10=10.03 B side - 10=9.97
CL5541 | 2024-12-13 | Vadivelan nagar | G | Outlet PMR work | Preventive | Suneel Sagar | 2024-12-13 | - | Outlet PMR work completed
CL5542 | 2024-12-13 | T.V.Koil | G | Outlet PMR work | Preventive | Nepolean | 2024-12-13 | - | Outlet PMR work completed
CL5543 | 2024-12-14 | Kattupakkam | G | Outlet PMR work | Preventive | Suneel Sagar | 2024-12-14 | - | Outlet PMR work completed
CL5544 | 2024-12-14 | Ariyamangalam | G | Outlet Rest Room E.B Power supply problem. | Breakdown | Nepolean | 2024-12-14 | - | Rest Room E.B Power supply problem rectified by Mr.Bala attending cable short circuit in office room back side.Working in good condition.
CL5545 | 2024-12-14 | Eral | G | Outlet General information | Preventive | Kathiresan | 2024-12-14 | - | Tamiraparani river flood has reached the town and all the vehicles are parked at our station due to heavy rain and instruction given to pump staffs to be alert and stay in safe zone and station diesel genset and Diesel fill are under monitoring
CL5546 | 2024-12-14 | Uthamasolapuram | R | Outlet dispenser UPS battery and control panel indicator light problem. | Breakdown | Prabu | 2024-12-14 | - | Dispenser UPS battery 1 number and control panel indicator light changed.Working in good condition.
CL5547 | 2024-12-14 | Tharamangalam | R | Outlet control panel voltage scanner problem | Breakdown | Prabu | 2024-12-14 | - | Control panel voltage scanner problem rectified by changing of new one.Working in good condition.
CL5548 | 2024-12-16 | Kodumudi | C | Outlet Rule-19 work | Certification | Chandrasekar and Thirumalaisamy | 2024-12-17 | 17 Hrs | Rule-19 work started and sales stopped by 4.45PM.outlet sales started at 9.30PM.
CL5549 | 2024-12-17 | Manapparai | G | Outlet PMR work. | Preventive | Nepolean | 2024-12-17 | - | PMR work completed. C.P voltage one Anode problem (-0.10 Dcv)
CL5550 | 2024-12-17 | Ariyamangalam | D | Outlet A side nozzle leakage problem. | Breakdown | Nepolean | 2024-12-17 | - | A side nozzle leakage problem rectified by servicing and changing of one new nozzle and working in good condition. A side testing: 1.17 lit
CL5551 | 2024-12-17 | Velacherry | G | Outlet PMR work. | Preventive | Suneel Sagar | 2024-12-17 | - | PMR work completed.
CL5552 | 2024-12-18 | Vedasandur | D | Outlet dispenser B-side nozzle hose leakage and control panel voltage scanner problem. | Breakdown | Kamaraj | 2024-12-18 | - | Dispenser B-side nozzle hose LPG leakage problem rectified by changing with spare hose.Control panel voltage scanner new one replaced due to short circuit. Both compressor oil changed.and PMR completed.
CL5553 | 2024-12-18 | Kodumudi | C | Rule-18 and Rule-19 work | Certification | Thirumalaisamy | 2024-12-18 | - | Outlet rule 19 and 18 work completed,tank and dispenser area leak checked and all equipment working condition good. Dispenser both side DP valve diaphragm checked. Testing: 23.05litters
CL5554 | 2024-12-18 | Namakkal-1 | R | Outlet Automation RS485 converter board and 1 kva online UPS mother board short circuit problem. | Breakdown | Nivas | 2024-12-18 | - | Automation RS485 converter board problem resolved by changing of new board.1 kva online UPS mother board short circuit problem rectified by changing of new UPS.Working in good condition.
CL5555 | 2024-12-19 | Dharapuram | C | Rule-18 work | Certification | Gowtham and Sureshkumar | 2024-12-19 | - | Rule-18 work completed
CL5556 | 2024-12-19 | Madurai-3(Pandikoil) | R | Outlet office emergency switch "NC Element problem. | Breakdown | Kathiresan | 2024-12-19 | - | Office emergency switch "NC Element problem rectified by replacing and now working in good condition.
CL5557 | 2024-12-20 | Namakkal-1 | D | Outlet E05 error problem. | Breakdown | Nivas | 2024-12-20 | 1.30 hrs | E05 error problem rectified interchanging and reconfiguration of display and working in good condition.Now pump under observation. Testing - 33.41.
CL5558 | 2024-12-20 | Dharapuram | C | Outlet Stamping and Calibration work | Certification | Gowtham | 2024-12-20 | - | Calibration and calibration work completed PMR completed. Earth regenerate and DP valve checking done. Calibration details:- Testing litres A side- 140.94 B side- 167.80 Total - 308.74 litres K-factor A side- 10000 B side- 10000 A side -10=10.06 B side - 10=10.06
CL5559 | 2024-12-20 | Udumalpet | C | Outlet Stamping and Calibration work | Certification | Gowtham | 2024-12-20 | - | Calibration and stamping completed. Testing litres A side- 420.98 B side- 306.21 C side - 323.39 D side - 426.50 Total - 1477.08 litres Old K-factor A side - 101500 B side - 101100 C side - 10300 D side - 10350 New K factor A side - 102000 B side - 101800 C side - 10200 D side - 10200 A side - 10= 09.92 B side - 10= 09.92 C side - 10= 09.95 D side - 10= 09.93
CL5560 | 2024-12-21 | Udumelpet | C | Outlet Rule-18 work | Certification | Gowtham | 2024-12-21 | - | Rule 18 work completed. Earth regenerated and DP valve checking is done. C side testing - 0.5 ltr.
CL5561 | 2024-12-21 | Avinashi | C | Outlet Rule-18 work | Certification | Gowtham | 2024-12-21 | - | Rule 18 work completed. Earth regenerated and DP valve checking is done.Outlet earth failure,new earth to be install. Tank 2 CP anode 1 nos. to be replaced.
CL5562 | 2024-12-22 | Mettupalayam | C | Outlet Rule-18 work | Certification | Gowtham | 2024-12-22 | - | Rule 18 work completed. Earth regenerated and DP valve checking is done.
CL5563 | 2024-12-22 | Saravanampatty | C | Outlet Rule-18 work | Certification | Gowtham | 2024-12-22 | - | Rule 18 work completed. Earth regenerated and DP valve checking is done.Outlet CP failure.
CL5564 | 2024-12-23 | Ramanathapuram | C | Outlet Rule-18 work | Certification | Kathiresan and Vigneshwaran | 2024-12-23 | - | Rule 18 work completed.
CL5565 | 2024-12-24 | Ramanathapuram | C | Outlet Stamping and Calibration work | Certification | Kathiresan and Vigneshwaran | 2024-12-24 | - | Calibration and stamping Completed. "9 kg" Fire extinguisher one number failure."40 NB ROV to be serviced. Calibration report "A" side 10 = 9.94 "B" Side 10 = 9.93 "K" Factor Report "A" side = 10030 "B" Side = 10030 Testing report Day A = 208.53 B = 196.81 Night A = 36.58 B= 114.12
CL5566 | 2024-12-24 | Pudukkottai | C | Outlet Rule-18 work | Certification | Kathiresan and Vigneshwaran | 2024-12-24 | - | Rule 18 work completed. Earth regenerated and total leakage tested. Dispensing motor realignment working fine. Both Nozzle hammer teeth Changed."50 NB ROV to be serviced. DP Valve diaphragm checked.Working in good condition. Testing = 0.42 lit
CL5567 | 2024-12-24 | Ramanathapuram | R | Outlet control panel problem. | Breakdown | Kathiresan | 2024-12-31 | - | Stabilizer PCB serviced and new nutral surge installed and changeover panel input line "25 sq mm Leg" changed.Stabilizer Servo mode working in good condition.VSR (voltage scanner Relay) not working.
CL5568 | 2024-12-25 | Kodumudi | G | Outlet general visit | Preventive | Thirumalaisamy | 2024-12-25 | - | Outlet all equipments working normal
CL5569 | 2024-12-25 | Madurai Villapuram | D | Outlet "C" side nozzle LPG hose starting to damage. | Breakdown | Kathiresan | 2024-12-25 | - | "C" side nozzle LPG hose 5 mtrs replaced by new one. Working in good condition.Testing 1.77 ltrs.
CL5570 | 2024-12-25 | Mettupalayam | C | Outlet Stamping and Calibration work | Certification | Gowtham | 2024-12-25 | - | Stamping and Calibration work completed.
CL5571 | 2024-12-25 | Avinashi | T | Outlet Electrical and Non Electrical earth work. | Breakdown | Gowtham | 2024-12-25 | - | Electrical and Non electrical earth newly installed and found satisfactory in field Earth line operation.
CL5572 | 2024-12-25 | Palladam-1 | T | Outlet Electrical and Non Electrical earth work. | Breakdown | Gowtham | 2024-12-25 | - | Electrical and Non electrical earth newly installed and found satisfactory in field Earth line operation.
CL5573 | 2024-12-26 | Thanjavur | T | Outlet decanting liquid line problem. | Breakdown | Pandidurai | 2024-12-26 | - | Decanting liquid line problem rectified by servicing the ROV and fitted.Working in good condition.Air machine keypad wiring reconnected and Bill printer machine interchanged to office room. PMR also completed.
CL5574 | 2024-12-26 | Uthamapalayam | G | Outlet fire Extinguisher service and Renewal work. | Preventive | Kamaraj | 2024-12-26 | - | Fire Extinguisher service and Renewal work completed and certificate also received.New fire ball changed due to date expired.
CL5575 | 2024-12-26 | Bodi | G | Outlet fire Extinguisher service and Renewal work. | Preventive | Kamaraj | 2024-12-26 | - | Fire Extinguisher service and Renewal work completed and certificate also received.New fire ball changed due to date expired.
CL5576 | 2024-12-26 | Theni | G | Outlet fire Extinguisher service and Renewal work. | Preventive | Kamaraj | 2024-12-26 | - | Fire Extinguisher service and Renewal work completed and certificate also received.Training given to all pump staffs.
CL5577 | 2024-12-27 | Cantonment | D | Outlet Dispenser nozzle daphram changing work | Preventive | Chandrasekar | 2024-12-27 | - | Dispenser -C,D,E,F, 4- Nozzle new diaphram changed.(Newly purchased diaphram changed for testing purpose) C -Testing.5.00 D-Testing.5.96 E-Testing.5.00 F-Testing.5.00 Total Testing.20.96 litre
CL5578 | 2024-12-28 | Karur Puliyur | C | Outlet Rule-18 work | Certification | Sureshkumar and Thirumalaisamy | 2024-12-28 | - | Rule 18 work completed.
CL5579 | 2024-12-28 | Maurai Ellis nagar | D | Outlet Dispenser "A" "B" "C" "D" side new diaphragm changing work for testing purpose | Preventive | Kathiresan | 2024-12-28 | - | Dispenser "A" "B" "C" "D" side new diaphragm changed by newly purchsed one. Testing Totalizers "A" = 1300191.220 "B" = 1432982.250 "C" = 896170.360 "D" = 1167436.240
CL5580 | 2024-12-28 | T.V.Koil | D | Outlet Dispenser "C" "D" side new diaphragm changing work for testing purpose | Preventive | Nepolean | 2024-12-28 | - | Dispenser "C" "D" side new diaphragm changed by newly purchsed one. Testing Totalizers C" = 2881820.88 "D" = 2762624.49 Testing liter: C side : 5.89 D side : 6.01 Total : 11.90 lit
CL5581 | 2024-12-28 | Cantonment | D | Outlet Dispenser "C" "D" E" F" side new diaphragm changing work for testing purpose | Preventive | Chnadrasekar | 2024-12-28 | - | Dispenser "C" "D" E" F" side new diaphragm changed by newly purchsed one. Testing Totalizers C.side reading -5324970.04 D.side reading -5013377.30 E.side reading -1169274.80 F.side reading -1060680.70
CL5582 | 2024-12-28 | Hosur | G | Outlet PMR work. | Preventive | Prabu | 2024-12-28 | - | PMR work completed.
CL5583 | 2024-12-28 | Dharmapuri | G | Outlet PMR work. | Preventive | Prabu | 2024-12-28 | - | PMR work completed.
CL5584 | 2024-12-28 | Krishnagiri | G | Outlet PMR work. | Preventive | Prabu | 2024-12-28 | - | PMR work completed and Dispenser display B side board number visible problem.
CL5585 | 2024-12-30 | Tirunchengode | R | Outlet 1 kva online UPS battery problem. | Breakdown | Nivas | 2024-12-30 | - | Outlet 1 kva online UPS battery problem rectified by changing of new battery.Working in good condition.
CL5586 | 2024-12-30 | Kangeyam | C | Outlet Rule 18 and PMR work | Certification | Gowtham | 2024-12-30 | - | Rule 18 work PMR completed. Earth regenerated and DP valve checking done.
CL5587 | 2024-12-30 | Palladam-1 | C | Outlet Rule 18 and PMR work | Certification | Gowtham | 2024-12-30 | - | Rule 18 work PMR completed. Earth regenerated and DP valve checking done.
CL5588 | 2024-12-30 | Palladam-2 | C | Outlet Rule 18 and PMR work | Certification | Gowtham | 2024-12-30 | - | Rule 18 work PMR completed. Earth regenerated and DP valve checking done.
CL5589 | 2024-12-30 | Palladam-1 | C | Outlet Rule-18 work | Certification | Gowtham | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5590 | 2024-12-30 | Karur Puliyur | C | Outlet Rule-18 work | Certification | Thirumalaisamy | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5591 | 2024-12-30 | Paramathy Velur | C | Outlet Rule-18 work | Certification | Thirumalaisamy | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5592 | 2024-12-30 | Karur | C | Outlet Rule-18 work | Certification | Thirumalaisamy | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5593 | 2024-12-30 | Palayam | C | Outlet Rule-18 work | Certification | Thirumalaisamy | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5594 | 2024-12-30 | Mulanur | C | Outlet Rule-18 work | Certification | Thirumalaisamy | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5595 | 2024-12-30 | Vellakoil | C | Outlet Rule-18 work | Certification | Thirumalaisamy | 2024-12-30 | - | Rule 18 work completed, Earth regenerated and DP valve checked.
CL5596 | 2024-12-30 | Kodumudi | A | Outlet Automation rack dressing work. | Development | Thirumalaisamy | 2024-12-30 | - | Outlet Automation rack dressing work completed.